## ITP Cover Page
Retaining Wall 04 - Waste water Inspection and Test Plan
Project: Tauriko Enabling Project
Number and Revision: DN1210-SP2 - ITP 010-003-001 - Rev 1
SECTION 1 – GENERAL DETAILS
Project Name: |  |  | Tauriko Enabling Project |  |  |  |  | ITP Number: |  |  | ITP 010-003-001
Project Number: |  |  | DN1210-SP2 |  |  |  |  | ITP Status: |  |  | Approved
ITP Description: |  |  | Retaining Wall 4 Wastewater Installation |  |  |  |  | Revision: | 1000 |  | 1
Contract Number: |  |  | 8287 |  |  |  |  | Drawing Sets: |  |  | 232735.02-WSP-DR-WST
Customer: |  |  | Waka Kotahi |  |  |  |  | Specification: |  |  | Section 22.1 to Section 22.13
Quality Specified: |  |  | ISO 9001:2015
Review / Update History | [9 empty] | Verification Activity
Rev: | Status: | Date: |  | Reviewed By: |  | Revision Details: |  |  |  | Activity Key |  |  | Responsibilities Key
0 | Draft for Approval |  |  | Cordelia Girdler-Brown & Nick Adams | [5 empty] | A | Action |  | ENG | Engineer / Engineer's Rep
[10 empty] | B | Report by Breach |  | CR | Customer Rep
[10 empty] | C | Check |  | PD | Project Director
[10 empty] | D | Dimension Inspection |  | PM | Project Manager
[10 empty] | E | Examine |  | OP | Operations Manager
[10 empty] | HP | Hold Point (Engineer) (Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point) |  | HSE | HSE Manager / Rep
1 | Approved |  |  | Cordelia Girdler-Brown & Nick Adams | [5 empty] | H | Hold Point (Internal) (Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point) |  | PE/SE | QA Manager / Rep
[10 empty] | I | Inspection (Formal inspection activity to be undertaken and recorded) |  | PE | Project Engineer
[10 empty] | M | Monitor on Random Basis |  | SE | Site Engineer
[10 empty] | O | Operation |  | QE | Quality Engineer
[10 empty] | R | Review |  | SUP | Superintendent / Supervisor
[10 empty] | S | Subcontractor |  | SV | Surveyor
[10 empty] | V | Visual Verification |  | ITP | Third Party Inspector
[10 empty] | W | Witness Point (Review of text reports/records or other evidence of compliance) |  | SPEC | Specialist
SECTION 2A – ITP Approval | [7 empty] | SECTION 2B – ITP CLOSEOUT
Position |  | Name: |  |  | Signature: |  | Date: | Position |  | Name: |  | Signature: |  |  | Date:
Downer PM |  | NICK ADAMS |  |  | #VALUE! |  | 30/04/2025 | Downer PM |  | NICK ADAMS
Downer QM |  | CORDELIA GIRDLER-BROWN |  |  |  |  | 30/04/2025 | Downer QM |  | CORDELIA GIRDLER-BROWN
Client (If Applicable) | [7 empty] | Client (If Applicable)

## ITP Master Body
Northern Access Road & Carpark Wastewater
Tauriko Enabling Works
DN1210 - SP2- ITP010-003-001 - REV 0
Item No. | Inspection and Test Point | Detail / Activity | Acceptance / Conformance Criteria | Standard / Specification | Verifying Document | Testing Quantity Required (based from schedule qtys) | Verification Activity |  | Downer Conformance of Compliance Signoff
[7 empty] | Activity | By | ConQA Signature | Date | Comments / Closeout Details | ENGINEERS COMMENTS - Date: | DOWNER RESPONSE - Date:
SECTION 3 – PRE-CONSTRUCTION - MATERIAL , PERSONNEL & THIRD PARTY APPROVLS (P&G / ESTABLISHMENT)
3.1 | GENERAL - Pipe Laying | Method statement | As Per Specification and IFC Drawings | PS- 22.3 Appendix V | Wastewater Construction Work Pack Sign off | Prior to Construction | HP Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | ENG
3.2 | GENERAL - Pipeline Pressure Testing | Method statement | As Per Specification and IFC Drawings | PS- 22.3 Appendix V | Wastewater Pipeline Pressure Testing Work Pack Sign off | Prior to Construction | HP Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | ENG
3.3 | GENERAL - Extent of Line Setout | Ensure line and level of Wastewater has been marked out and agreed with Engineer in accordance with Waste water drawings. Identify any clashes before construction. LOT- markup | As Per Drawings & Markup drawing | Design Drawings | ITP Sign Off / Mark-up | Prior to Construction & Every Revision of IFC Drawings/Data. | HP Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | ENG
3.4 | MATERIAL TESTING- AP65 Material grading: Materials (Gap65/AP65) | NZS4407:2015, Test 3.8.1 - Particle Size Distribution | No Particles >200mm Maximum fines 10% passing 75micron sieve | PS 22.13.1 Appendix XVIII PS 16.5.5 Appendix V | Lab Test Report NZS 4407.3.8.1 | Stockpile Size (m3): 0-400 - 2 tests 400-1,500 - 3 tests 1,500-4,000 - 4 tests >4,000 - 1 test for each additional 1,000m3 Results to Engineer 2 wks before importing | HP Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | ENG
3.5 | MATERIAL TESTING- AP65 Weathering index: Materials (Gap65/AP65) | NZS4407:2015, Test 3.11 - The Weathering Quality Index of Coarse Aggregate | AA, AB, AC, BA, BB, or CA | Appendix XVIII PS 16.5.5 Appendix V | IANZ Accredited Report | 2 Tests Per Material, Per Source Results to Engineer 2 wks before importing | HP Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | ENG
3.6 | MATERIAL TESTING- AP65 Crushing Resistance: Materials (Gap65/AP65) | NZS4407:2015, Test 3.10 - The Crushing Resistance of Coarse Aggregate Under a Specified Load | >100KN | Appendix XVIII Appendix V | IANZ Accredited Report | 2 Tests Per Material, Per Source Results to Engineer 2 wks before importing | HP Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | ENG
3.7 | MATERIAL TESTING- AP65 Maximum Dry Density and Optimum Water Content | NZS4402:1986, Test 4.1.2 - Heavy Compaction Test | Report Value Only | Appendix XVIII Appendix V | IANZ Accredited Report | 1 Test Per Material, Per Source Results to Engineer 2 wks before importing | HP Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | ENG
3.8 | MATERIAL TESTING- Pumice Sand Material grading: Materials (Sand) | Bedding/Side Zone/ Overlay Zone/Embedment Zone | Sieve Size % Passing 19.0mm 85-100% passing 9.5mm 25-55% passing 4.75mm 0-10% passing 2.36mm 0-5% passing 0.075mm 0-2% passing | AS/NZS 2566.2 PS 22.4.5 | Lab Test Report NZS 4407.2015 Test3.8.1 | 0-400m3 2 Test 400-1500m3 3 Test 1500-4000m3 4 Test >4000 1 Test Additional 1000m3 | HP Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | ENG
3.9 | MATERIAL TESTING- Pipes Pipes (PE/ PVC) | Manufacturer's record and location of extrusion plants. Name of the proposed PE resin, the manufacturer, production information on the properties of resin. Full Traceability information and certification of analysis for the resin batch. | Full Traceability information and certification of Material and resin. PE/PCV Pipes in accordance with the IDC Approved Material List AM-6 Wastewater AS/NZS 1477 AS/NZS 4130 | PS-22.4.1 (d) | Full Traceability information and certification of Material and resin. Delivery Dockets | Prior to construction | HP Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | ENG
3.1 | MATERIAL TESTING- Pipes Green Dome Odour Filter | A Green Dome Odour Filter (Model GDOF36) complete with DN150 ducting. | IFC Drawing 0324-1 | Model GDOF30 | Delivery Dockets | Prior to construction | HP Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | ENG
3.11 | MATERIAL TESTING- Pipes Valves, Adaptors, Flanges and Fittings | Have a pressure rating no less than the designed pressure. Mechanically, chemically and electrically compatible with the class and material of the pipe. Current Water Services Association of Australia (WSAA) appraisal certificate or approved independent proof of fitness-for-purpose. | Engineer approval AS/NZS 4129 | PS-22.4.2 | Delivery Dockets | Prior to construction | HP Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | ENG
3.12 | MATERIAL DELIVERY Pipe and fittings. (PE100- DN180 PN16, PE100- DN90 PN12.5 & DN150 PVCu SN16) | Confirm diameter, class & jointing type as shown on the drawings, and that the pipes are correct and in good condition. | Confirm diameter, class & jointing type as shown on the drawings, and that the pipes are correct and in good condition. | Design Drawings | Delivery Dockets / Inspection Checksheet (DG-QA-TP019) | Each Delivery to site | H Hold Point (Internal) (Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point) | PE/SE
3.13 | MATERIAL DELIVERY Valves, Adaptors, Flanges and Fittings | Confirm class and type as shown on the drawings, and that the fittings are correct and in good condition. | Confirm class and type as shown on the drawings, and that the fittings are correct and in good condition. | PS-22.4.2 | Delivery Dockets / Inspection Checksheet(DG-QA-TP019) | Each Delivery to site | H Hold Point (Internal) (Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point) | PE/SE
3.14 | MATERIAL DELIVERY Granular Material (Imported Pumice sand, GAP65/AP65) | Confirm Specification and material in good condition. | Confirm Specification and material in good condition. | PS-22.4.1 | Delivery Dockets / Inspection Checksheet(DG-QA-TP019) | Each Delivery to site | H Hold Point (Internal) (Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point) | PE/SE
3.15 | MATERIAL DELIVERY Bidim/Geogrid | BIDIM A29 Durogrid 30/30 or similar. | Site Engineer Approval | PS-22.4.1 | Delivery Dockets / Inspection Checksheet(DG-QA-TP019) | Each Delivery to site | H Hold Point (Internal) (Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point) | PE/SE
3.16 | MATERIAL DELIVERY Manhole WWMH 24 | Confirm the class and type as shown in the drawings, and fittings required for MH is same | Confirm the class and type as shown in the drawings, and fittings required for MH is same | Design Drawings | Delivery Dockets / Inspection Checksheet(DG-QA-TP019) | Each Delivery to site | H Hold Point (Internal) (Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point) | PE/SE
3.17 | MATERIAL DELIVERY Manhole WWMH 11 | Confirm the class and type as shown in the drawings, and fittings required for MH is same | Confirm the class and type as shown in the drawings, and fittings required for MH is same | Design Drawings | Delivery Dockets / Inspection Checksheet(DG-QA-TP019) | Each Delivery to site | H Hold Point (Internal) (Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point) | PE/SE
3.18 | MATERIAL DELIVERY Bedding material | Free of larger sharp particles conforming sand | Free of larger sharp particles conforming to sand | PS 25.13.2 (g) & (h) | Delivery Dockets/Material Certification | Each Delivery to site | H | SE
SECTION 4 | CONSTRUCTION ACTIVITY - WASTEWATER PIPELINE- Excavation and Laying
4.1 | WASTEWATER PIPELINE- Excavation and Laying Foundation Compliance | On Granular or Cohesive Material | Granular Material: Scala 3 blows/100mm (Or) Cohesive Material: Vane Shear Strength min50kpa, ave>60kpa | Appendix V Table 21:11 | Scala/Shear test result | One test per 10m evenly spaced intervals along pipelines with a minimum of 1 test between each pit/manhole. | W Review of text reports/records or other evidence of compliance | SE
4.2 | WASTEWATER PIPELINE- Excavation and Laying Undercut approval | Trench Foundation | 300mm Max cut IFC Drawing Sheet 320 (Or) Engineers approval | IFC Drawing WST 0320. AS/NZS 2566.2/2002 | Lab Test Report / Wastewater line record | If Undercut required | H Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | SE
4.3 | WASTEWATER PIPELINE- Excavation and Laying Undercut Backfill Compliance (GAP65) | On Granular Material / On each layer as per specification / on the trench foundation. | Visiual Inspection | IFC Drawing WST 0320 | Lab Test Report / Wastewater line record | Every Undercut | H Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | SE
4.4 | WASTEWATER PIPELINE- Excavation and Laying Bedding Zone Compaction Testing | On Granular Material / On each layer as per specification (Imported Sand/GAP20/19mm chip) | Bedding Zone: 100mm minimum thickness (compacted) over the bottom of the trench. Minimum Compaction- 85%MDD | IFC Drawing 0320-1 AS/NZS 2566.2/2002 | Lab Test Report | As per SW Specification. One test per 10m evenly spaced intervals. | H Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | SE
4.5 | WASTEWATER PIPELINE- Excavation and Laying Laying of Pipes | Lay in straight lines, beginning at the lower end of the line. Lay all pipe with manufacturing codes and class markings facing upwards. | As Per Drawings. (232735.02-WSP-DR-WST 0208) AS/NZS 2566.2 | PS22.7.1 C AS/NZS 2566.2 | Visual Inspection / Wastewater line record | Every Line | H Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | SE
4.6 | WASTEWATER PIPELINE- Excavation and Laying Pipe Installation on Curved Alignments | All Industry Guideline PVC, PP AND PE PIPE INSTALLATION ON CURVED ALIGNMENTS (POP202) | AS Per POP 202 | PS 22.7.1 D | Visual Inspection / Wastewater line record | Every Line | M Monitor on Random Basis | SE
4.7 | WASTEWATER PIPELINE- Joint and Connection: Flanges | Manufacturer specifies their own bolt tightening torque and sequence, it should override the project specification. | Flanges to AS/NZS 4087 | PS 22.7.5 | Visual Inspection | First flanged joint | HP Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | ENG
4.8 | WASTEWATER PIPELINE- Joint and Connection Bends | PE 100 butt fusion welded segmented bends only where specifically indicated on the Drawings. Fitting must meets the same PN rating as the adjacent PE 100. Fittings must be suitable for producing the joints shown on the Drawings. | PIPA POP 006 and AS/NZS 4129 | PS 22.4.2 | Visual Inspection | As per the IFC drawing | H Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | SE
4.9 | WASTEWATER PIPELINE- Butt-Fusion Welding Butt-Fusion pre construction weld test | One weld on the most common size of pipes used for the project. One weld on the thickest wall (highest PN) pipe | ISO 13953 for tensile strength and failure mode. WMS Report DVS2207-1 | PS 22.9.6 (a) | Visual Inspection | Two test welds per operative(Welder) | HP Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | ENG
4.1 | WASTEWATER PIPELINE- Butt-Fusion Welding Butt-Fusion Welding | Use only semi-automatic or automatic welding machines. Maintain a site record for all butt-fusion welds. The lead welder or supervisor must verify on the site record form that all welds have been made in accordance with the WMS and that the information on the record form is correct. | Site Butt Fusion Welding record to be filled out. (Refer to CWP) WMS Report | Appendix 22. PS 22.9.4 C | Visual Inspection / Butt Fusion welding records checklist. WMS Report | Every Welding Point | HP Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | ENG
4.11 | WASTEWATER PIPELINE- Butt-Fusion Welding Butt-Fusion Construction weld test | Test at least two welds from the first 50 welds. One of the welds to be selected by the Engineer for satisfactory result. | Tensile testing and ductility of welds. | PS- 22.9.6 (a) (iv) | Test report | Two welds for the first 50 welds | HP Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | ENG
4.12 | WASTEWATER PIPELINE- Butt-Fusion Welding Survey | Inspection of Pipeline Inverts | Vertical design Setout: Pipes ≤ 1% grade: +/- 10mm variance Pipes > 1% grade: +/- 20mm variance Horizontal design Setout: +/-30mm variance | PS- 21.7.6 Table 21.15 | Survey Data / As-built record | Pipeline invert to be surveyed at chainages as indicated in the drawings. | H Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | SE
4.13 | WASTEWATER PIPELINE- Backfill Emebment Zone - (Side Haunch Overlay ) | Granular Sand backfill Compacted in 200mm Layers. NDM/CleggTesting to be completed on maximum 200mm lifts of overlays . NDM BS to be Carried Out | in 200mm layers. More than 85% of MDD. | IFC Drawing 0320-1 | Lab Report / Wastewater line record | One test per 10m evenly spaced intervals. 200mm lift | H Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | SE
4.14 | WASTEWATER PIPELINE- Backfill Pipe Markers | Lay a conductive signal strip or tracer wire along the full length of all non-metallic pressure pipelines as shown on the Drawings. Mark fire hydrant positions in accordance with SNZ PAS 4509 | AS Per Drawings. | PS 22.7.3 a | Visual Inspection / Wastewater line record | Every Line | H Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | SE
4.15 | WASTEWATER PIPELINE- Backfill Backfill Compaction Testing | GAP65/AP65 Backfill Compacted in 200mm Layers. NDM Testing to be completed on maximum 200mm lifts of backfill. | GAP65/AP65or site won material Backfill Compacted in 200mm layers. Testing to be completed on maximum 200mm lifts of backfill. 95% NDM on Shared and Carriageway. OR 28% CIV For site won min >60kpa Ave > 80kpa | PS- 22.13.5 NDM Standerd 25832 NZS 4402 Test 4.1.3 IFC Drawing 0320-1 | Lab Report / Wastewater line record | As per SW Specification. One test per 10m evenly spaced intervals. | H Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | SE
4.16 | WASTEWATER PIPELINE- Inspection Pipe Inspection | Inspection of Drainage line | Inspect pipes prior to backfilling to ensure they have been installed correctly and the joints are in place. Check for gaps and/or defects and check pipe alignment for straightness | Internal | Wastewater line record | Continious 1 per Line | I Formal inspection activity to be undertaken and recorded. | SE
4.17 | WASTEWATER PIPELINE - Testing Pressure Acceptance Testing | Backfill/cover with embedment before testing End caps in place, provision for filling the pipeline and bleeding air. | Wastewater Rising Main Pipelines – 800kPa Ensure the STP is not more than 25% above the rated pressure of any pipeline component. | PS 22.7.12(d) PS 22.7.13(b) | Test Report Pressure Log in.csv or .xlsx format | All Pipeline All valves | HP Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | ENG
4.18 | WASTEWATER - Manhole installation Foundation Compliance | On Granular or Cohesive Material | Granular Material: Scala 3 blows/100mm Cohesive Material: Vane Shear Strength min50kpa, ave>60kpa | Appendix V Table 21:11 | Shear vane or Scala test result | 1 Test/Manhole | W | SE
4.19 | WASTEWATER - Manhole installation Undercut approval | On Subgrade | Subgrade CBR between 3.5% <5%: Undercut 150mm and Replace with Compacted AP65 or Approved Granular material. Subgrade CBR between 2% <3.5%: Undercut 300mm and Replace with Compacted AP65 or Approved Granular material. Subgrade CBR between <2%: Engineer to advise or Undercut 450mm and Replace with Compacted AP65 or Approved Granular material. | Table 21.5 | Lab Test Report | If Undercut required | HP Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | ENG
4.2 | WASTEWATER - Manhole installation Undercut Backfill Compliance AP65 | On Granular Material | Average 95% MDD, min >92% OR Clegg 25% CIV | PS- 16.5.12 | Lab Test Report | 1 Test per Undercut | H Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | SE
4.21 | WASTEWATER - Manhole installation Bedding Compaction Testing AP65 | On Granular Material | Average 95% MDD, min >92% OR Clegg 25% CIV | PS- 16.5.12 PS- 21.6.11 | Lab Test Report | 1 Test/Manhole | H Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | SE
4.22 | WASTEWATER - Manhole installation Survey | Inspection of Structure | Horizontal Alignment: The permissible deviation of the horizontal alignment between manholes or structures shall be ± 30mm. | PS- 21.7.6 | Survey Data | 1 Test/Manhole | H Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | SV
4.23 | WASTEWATER - Manhole installation Sidefill Compaction Testing | From the bedding layer to the overlay layer of pipe. | AP20/GAP20 Testing to be completed on maximum 200mm lifts of backfill - 85% MDD AP20/19mm chip | PS- Table 21.12 | Lab Test Report | 4 Density test per layer at Quarter Points around the Structure. | H Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | SE
4.24 | WASTEWATER - Manhole installation Backfill Compaction Testing | From Overlay layer to the subgrade layer | AP65 Testing to be completed on maximum 200mm lifts of backfill - 92% (Average 95%) of MDD on metal. AP65-Clegg28%CIV | PS- 16.5.12 | Lab Test Report | 4 Density test per layer at Quarter Points around the Structure. | H Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | SE
4.25 | WASTEWATER - Manhole installation MH joints inspection | Inspection of joints | Right joint type used, no visual leak or breakage | PS 22.7.10 | Visual inspection | 1 Test/Manhole | HP Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | ENG
4.26 | WASTEWATER - Manhole installation Inspection | Inspection of Structure | Inspection of Structure prior to backfilling to ensure correct installation and that the joints are sealed. No damages caused to the Structure. | PS- 21.6.11 | Manhole/Catchpit Record | 1 Checksheet per manhole/catchpit | I | SE
4.27 | WASTEWATER - Manhole installation Plumb | The maximum permitted installed out of plumb is 25 mm of horizontal deviation in 1 m of vertical rise. | The maximum permitted installed out of plumb is 25 mm of horizontal deviation in 1 m of vertical rise. | PS-22.7.10 | Survey Data | 1 Test/Manhole | H Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | SV
4.28 | WASTEWATER - Manhole installation Step Rungs | Step rungs evenly spaced at nominal 300mm vertical intervals | Lowest rung more than 450mm above floor highest rung not more than 600mm below the top surface of MH cover | PS-22.7.11 | Visual inspection | 1 Test/Manhole | H Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | SE
4.29 | WASTEWATER - Manhole installation Manhole frame and covers | Make up the height between the manhole roof slab or precast lid and the finished surface level using concrete riser rings. Set the manhole frame and cover in concrete so it finishes flush with the finished ground or roadway level. Finish the concrete in a way that allows the final surface to be brought close to the cover frame. | Make up the height between the manhole roof slab or precast lid and the finished surface level using concrete riser rings. Set the manhole frame and cover in concrete so it finishes flush with the finished ground or roadway level. Finish the concrete in a way that allows the final surface to be brought close to the cover frame. | PS-22.7.12 | Visual inspection | 1 Test/Manhole | H Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | SE
4.3 | WASTEWATER - Communication Duct Installation Foundation Compliance | It shall be de-watered prior to installation of bedding material. If the bottom of the trench is naturally occurring rock, or has stones, gravel or other sharp material in occurrence | 50mm granular layer shall be laid and compacted before the bedding layer is laid. | PS 25.13.2 c) and g) | Checklist | Each Cable | M | SE
4.31 | WASTEWATER - Communication Duct Installation Bedding | The floor of the trench shall be clear of any obstacles and shall be as flat as possible. | Clean Imported Sand or SAP 7 to be placed 50mm minimum thickness (compacted) over the bottom of the trench. | PS 25.13.2 g) | Checklist | Each Cable | M | SE
4.32 | WASTEWATER - Communication Duct Installation Installation of Ducts | If more than 2 ducts are being placed. | Must have 50 mm bedding material between the two ducts. | PS 25.13.7 b) iii | Checklist | Each Cable | M | SE
4.33 | WASTEWATER - Communication Duct Installation Draw Wires | A draw wire shall be intalled in all ducts and within all sub-ducts to facilitate the hauling-in of cable after the completion of the ducting. | Pigmented, stranded polypropylene or equivalent rot-proof material draw wire of 5kN breaking load. ≥20 years design life. The ends of draw wires shall be made fast within the pits and be secured to the duct plugs. Blue colour wire | PS 25.13.7 e) ii to iv | Checklist | Each Cable | M | SE
4.34 | WASTEWATER - Communication Duct Installation Caps | All duct ends shall be capped | Capped ducts | PS 25.13.7 e) v | Checklist | Each Cable | M | SE
4.35 | WASTEWATER - Communication Duct Installation Warning Tape | Warning tape to be placed above services. | Warning Tape to be placed no more than 300mm above the topmost duct | PS 25.13.7 b) iii & f) | Checklist | Each Cable | M | SE
4.36 | WASTEWATER - Communication Duct Installation Overlay | 150 mm minimum sand placed on top of duct. No mechanical compaction will caarry out till 300mm drom top of duct. | 100 mm minimum sand placed on top of duct. | PS 25.13.7 b) ii | Checklist | Each Cable | M | SE
4.37 | WASTEWATER - Communication Pit Location | Locations shall be avoided where running water can flow over the lid or where mud and debris can fall or be washed onto the lid . | Pit lid and concrete apron shall be flush with ground level in grass, concrete or asphalt areas. When pit is located on a slope of 10 to 30 degrees, the lid shall be flush with ground on the upper side. When slope is greater than 30 degrees, the lid shall be up to 100mm above the ground level on the upper side. | PS 25.13.8 a) i and ii | Checklist | Each Pit Location | H Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | SE
4.38 | WASTEWATER - Communication Pit Bedding | Bedding with 150mm compacted GAP20 hard-fill coverd with 20mm compacted sand. Pits shall be carefully lifted into place and lined up with the ducts to penetrate the chamber. | 150mm compacted GAP20 hard-fill covered with 20mm of compacted sand | PS 25.13.8 d) | Checklist | Each Pit Location | H Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | SE
4.39 | WASTEWATER - Communication Pit Sidefill concrete | Plactic pits shall be cast into the ground with 150mm concrete surround | Plactic pits shall be cast into the ground with 150mm concrete surround | PS 25.13.8 d) | Checklist | Each Pit Location | H Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | SE
4.4 | WASTEWATER - Communication Pit Backfilling | Backfill and compact the ground around concrete pits. Extra care to be taken to avoid damaging the ducts in 200mm layers of GAP 65. | Min 92% compaction rate and Average of 95%. | PS 25.13.10 a) modified | Checklist | Each Pit Location | H Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | SE
4.41 | WASTEWATER - Communication Pit Concrete | Top 300mm of pit shall be concreted around with a with of 150mm with a 20MpA concrete. | 20 mPa | PS 25.13.8 d) iv. | Concrete Dockets | Each Pit Location | H Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | SE
4.42 | WASTEWATER - Communication Pit Clean up | Clean out all pit after completion of the work | Pit are free of dirty, mud,water and foreign materials | PS 25.13.8 e) | Checklist | Each Pit Location | M | SE
4.43 | WASTEWATER - Communication Pit Survey As Built | As Built every ducts joint before backfill | Completed as per drawings | Standard Practise | Survey | On going | H Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | PE
SECTION 5 – POST CONSTRUCTION (FINAL INSPECTION AND HANDOVER)
5.1 | Survey As-Builts | Quality Check on Nee pipeline and structure based on the tolerances in RITS | Meets spec as per drawings and capture any NCR or change to design. | Project Specifications | Red pen markup only | Post works completion of a lot | H Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | SE