## res
type | name | values | prefix | postfix | usage count | user addable | template name | Resource Id
checklist | DN1210-SP2-010-003-001 ITP Retaining wall 4 Wastewater | itp |  |  |  |  | DN1210-SP2-010-003-001 ITP Retaining wall 4 Wastewater Rev 1
section | SECTION 3 – PRE-CONSTRUCTION - MATERIAL , PERSONNEL & THIRD PARTY APPROVLS (P&G / ESTABLISHMENT)
checkpoint | 3.1 - GENERAL - Pipe Laying
label | Detail / Activity - Method statement
label | Acceptance / Conformance Criteria - As Per Specification and IFC Drawings
label | Standard / Specification - PS- 22.3 Appendix V
label | Verifying Document - Wastewater Construction Work Pack Sign off
label | Testing Quantity Required (based from schedule qtys) - Prior to Construction
label | Verification Activity: Activity - HP
label | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 3.2 - GENERAL - Pipeline Pressure Testing
label | Detail / Activity - Method statement
label | Acceptance / Conformance Criteria - As Per Specification and IFC Drawings
label | Standard / Specification - PS- 22.3 Appendix V
label | Verifying Document - Wastewater Pipeline Pressure Testing Work Pack Sign off
label | Testing Quantity Required (based from schedule qtys) - Prior to Construction
label | Verification Activity: Activity - HP
label | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 3.3 - GENERAL - Extent of Line Setout
label | Detail / Activity - Ensure line and level of Wastewater has been marked out and agreed with Engineer in accordance with Waste water drawings.
label | ○ Identify any clashes before construction.
label | ○ LOT- markup
label | Acceptance / Conformance Criteria - As Per Drawings & Markup drawing
label | Standard / Specification - Design Drawings
label | Verifying Document - ITP Sign Off / Mark-up
label | Testing Quantity Required (based from schedule qtys) - Prior to Construction & Every Revision of IFC Drawings/Data.
label | Verification Activity: Activity - HP
label | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 3.4 - MATERIAL TESTING - AP65 Material grading: Materials (Gap65/AP65)
label | Detail / Activity - NZS4407:2015, Test 3.8.1 - Particle Size Distribution
label | Acceptance / Conformance Criteria - No Particles >200mm
label | ○ Maximum fines 10% passing 75micron sieve
label | Standard / Specification - PS 22.13.1 Appendix XVIII, PS 16.5.5 Appendix V
label | Verifying Document - Lab Test Report NZS 4407.3.8.1
label | Testing Quantity Required (based from schedule qtys) - Stockpile Size (m3):
label | ○ 0-400 - 2 tests
label | ○ 400-1,500 - 3 tests
label | ○ 1,500-4,000 - 4 tests
label | ○ >4,000 - 1 test for each additional 1,000m3
label | — Results to Engineer 2 wks before importing
label | Verification Activity: Activity - HP
label | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 3.5 - MATERIAL TESTING - AP65 Weathering index: Materials (Gap65/AP65)
label | Detail / Activity - NZS4407:2015, Test 3.11 - The Weathering Quality Index of Coarse Aggregate
label | Acceptance / Conformance Criteria - AA, AB, AC, BA, BB, or CA
label | Standard / Specification - Appendix XVIII, PS 16.5.5 Appendix V
label | Verifying Document - IANZ Accredited Report
label | Testing Quantity Required (based from schedule qtys) - 2 Tests Per Material, Per Source
label | ○ Results to Engineer 2 wks before importing
label | Verification Activity: Activity - HP
label | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 3.6 - MATERIAL TESTING - AP65 Crushing Resistance: Materials (Gap65/AP65)
label | Detail / Activity - NZS4407:2015, Test 3.10 - The Crushing Resistance of Coarse Aggregate Under a Specified Load
label | Acceptance / Conformance Criteria - >100KN
label | Standard / Specification - Appendix XVIII, Appendix V
label | Verifying Document - IANZ Accredited Report
label | Testing Quantity Required (based from schedule qtys) - 2 Tests Per Material, Per Source
label | ○ Results to Engineer 2 wks before importing
label | Verification Activity: Activity - HP
label | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 3.7 - MATERIAL TESTING - AP65 Maximum Dry Density and Optimum Water Content
label | Detail / Activity - NZS4402:1986, Test 4.1.2 - Heavy Compaction Test
label | Acceptance / Conformance Criteria - Report Value Only
label | Standard / Specification - Appendix XVIII, Appendix V
label | Verifying Document - IANZ Accredited Report
label | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source
label | ○ Results to Engineer 2 wks before importing
label | Verification Activity: Activity - HP
label | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 3.8 - MATERIAL TESTING - Pumice Sand Material grading: Materials (Sand)
label | Detail / Activity - Bedding/Side Zone/ Overlay Zone/Embedment Zone
label | Acceptance / Conformance Criteria - Sieve Size ¦¦ % Passing
label | 19.0mm ¦¦ 85-100% passing
label | 9.5mm ¦¦ 25-55% passing
label | 4.75mm ¦¦ 0-10% passing
label | 2.36mm ¦¦ 0-5% passing
label | 0.075mm ¦¦ 0-2% passing
label | Standard / Specification - AS/NZS 2566.2, PS 22.4.5
label | Verifying Document - Lab Test Report NZS 4407.2015 Test3.8.1
label | Testing Quantity Required (based from schedule qtys) - 0-400m3 ¦¦ 2 Test
label | ○ 400-1500m3 ¦¦ 3 Test
label | ○ 1500-4000m3 ¦¦ 4 Test
label | ○ >4000 ¦¦ 1 Test Additional 1000m3
label | Verification Activity: Activity - HP
label | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 3.9 - MATERIAL TESTING - Pipes (PE/ PVC)
label | Detail / Activity - Manufacturer's record and location of extrusion plants.
label | ○ Name of the proposed PE resin, the manufacturer, production information on the properties of resin.
label | ○ Full Traceability information and certification of analysis for the resin batch.
label | Acceptance / Conformance Criteria - Full Traceability information and certification of Material and resin.
label | ○ PE/PCV Pipes in accordance with the IDC Approved Material List AM-6 Wastewater AS/NZS 1477, AS/NZS 4130
label | Standard / Specification - PS-22.4.1 (d)
label | Verifying Document - Full Traceability information and certification of Material and resin. Delivery Dockets
label | Testing Quantity Required (based from schedule qtys) - Prior to construction
label | Verification Activity: Activity - HP
label | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 3.10 - MATERIAL TESTING - Pipes Green Dome Odour Filter
label | Detail / Activity - A Green Dome Odour Filter (Model GDOF36) complete with DN150 ducting.
label | Acceptance / Conformance Criteria - IFC Drawing 0324-1
label | Standard / Specification - Model GDOF30
label | Verifying Document - Delivery Dockets
label | Testing Quantity Required (based from schedule qtys) - Prior to construction
label | Verification Activity: Activity - HP
label | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 3.11 - MATERIAL TESTING - Pipes Valves, Adaptors, Flanges and Fittings
label | Detail / Activity - Have a pressure rating no less than the designed pressure.
label | ○ Mechanically, chemically and electrically compatible with the class and material of the pipe.
label | ○ Current Water Services Association of Australia (WSAA) appraisal certificate or approved independent proof of fitness-for-purpose.
label | Acceptance / Conformance Criteria - Engineer approval AS/NZS 4129
label | Standard / Specification - PS-22.4.2
label | Verifying Document - Delivery Dockets
label | Testing Quantity Required (based from schedule qtys) - Prior to construction
label | Verification Activity: Activity - HP
label | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 3.12 - MATERIAL DELIVERY - Pipe and fittings. (PE100- DN180 PN16, PE100- DN90 PN12.5 & DN150 PVCu SN16)
label | Detail / Activity - Confirm diameter, class & jointing type as shown on the drawings, and that the pipes are correct and in good condition.
label | Acceptance / Conformance Criteria - Confirm diameter, class & jointing type as shown on the drawings, and that the pipes are correct and in good condition.
label | Standard / Specification - Design Drawings
label | Verifying Document - Delivery Dockets / Inspection Checksheet (DG-QA-TP019)
label | Testing Quantity Required (based from schedule qtys) - Each Delivery to site
label | Verification Activity: Activity - H
label | ○ Hold Point (Internal)
label | ○ (Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point)
label | Verification Activity: By - PE/SE
checkpoint | 3.13 - MATERIAL DELIVERY - Valves, Adaptors, Flanges and Fittings
label | Detail / Activity - Confirm class and type as shown on the drawings, and that the fittings are correct and in good condition.
label | Acceptance / Conformance Criteria - Confirm class and type as shown on the drawings, and that the fittings are correct and in good condition.
label | Standard / Specification - PS-22.4.2
label | Verifying Document - Delivery Dockets / Inspection Checksheet(DG-QA-TP019)
label | Testing Quantity Required (based from schedule qtys) - Each Delivery to site
label | Verification Activity: Activity - H
label | ○ Hold Point (Internal)
label | ○ (Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point)
label | Verification Activity: By - PE/SE
checkpoint | 3.14 - MATERIAL DELIVERY - Granular Material (Imported Pumice sand, GAP65/AP65)
label | Detail / Activity - Confirm Specification and material in good condition.
label | Acceptance / Conformance Criteria - Confirm Specification and material in good condition.
label | Standard / Specification - PS-22.4.1
label | Verifying Document - Delivery Dockets / Inspection Checksheet(DG-QA-TP019)
label | Testing Quantity Required (based from schedule qtys) - Each Delivery to site
label | Verification Activity: Activity - H
label | ○ Hold Point (Internal)
label | ○ (Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point)
label | Verification Activity: By - PE/SE
checkpoint | 3.15 - MATERIAL DELIVERY - Bidim/Geogrid
label | Detail / Activity - BIDIM A29 Durogrid 30/30 or similar.
label | Acceptance / Conformance Criteria - Site Engineer Approval
label | Standard / Specification - PS-22.4.1
label | Verifying Document - Delivery Dockets / Inspection Checksheet(DG-QA-TP019)
label | Testing Quantity Required (based from schedule qtys) - Each Delivery to site
label | Verification Activity: Activity - H
label | ○ Hold Point (Internal)
label | ○ (Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point)
label | Verification Activity: By - PE/SE
checkpoint | 3.16 - MATERIAL DELIVERY - Manhole WWMH 24
label | Detail / Activity - Confirm the class and type as shown in the drawings, and fittings required for MH is same
label | Acceptance / Conformance Criteria - Confirm the class and type as shown in the drawings, and fittings required for MH is same
label | Standard / Specification - Design Drawings
label | Verifying Document - Delivery Dockets / Inspection Checksheet(DG-QA-TP019)
label | Testing Quantity Required (based from schedule qtys) - Each Delivery to site
label | Verification Activity: Activity - H
label | ○ Hold Point (Internal)
label | ○ (Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point)
label | Verification Activity: By - PE/SE
checkpoint | 3.17 - MATERIAL DELIVERY - Manhole WWMH 11
label | Detail / Activity - Confirm the class and type as shown in the drawings, and fittings required for MH is same
label | Acceptance / Conformance Criteria - Confirm the class and type as shown in the drawings, and fittings required for MH is same
label | Standard / Specification - Design Drawings
label | Verifying Document - Delivery Dockets / Inspection Checksheet(DG-QA-TP019)
label | Testing Quantity Required (based from schedule qtys) - Each Delivery to site
label | Verification Activity: Activity - H
label | ○ Hold Point (Internal)
label | ○ (Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point)
label | Verification Activity: By - PE/SE
checkpoint | 3.18 - MATERIAL DELIVERY - Bedding material
label | Detail / Activity - Free of larger sharp particles conforming sand
label | Acceptance / Conformance Criteria - Free of larger sharp particles conforming to sand
label | Standard / Specification - PS 25.13.2 (g) & (h)
label | Verifying Document - Delivery Dockets/Material Certification
label | Testing Quantity Required (based from schedule qtys) - Each Delivery to site
label | Verification Activity: Activity - H
label | Verification Activity: By - SE
section | SECTION 4 – CONSTRUCTION ACTIVITY - WASTEWATER PIPELINE- Excavation and Laying
checkpoint | 4.1 - WASTEWATER PIPELINE - Excavation and Laying - Foundation Compliance
label | Detail / Activity - On Granular or Cohesive Material
label | Acceptance / Conformance Criteria - Granular Material: Scala 3 blows/100mm
label | (Or)
label | ○ Cohesive Material: Vane Shear Strength min50kpa, ave>60kpa
label | Standard / Specification - Appendix V Table 21:11
label | Verifying Document - Scala/Shear test result
label | Testing Quantity Required (based from schedule qtys) - One test per 10m evenly spaced intervals along pipelines with a minimum of 1 test between each pit/manhole.
label | Verification Activity: Activity - W
label | ○ Review of text reports/records or other evidence of compliance
label | Verification Activity: By - SE
checkpoint | 4.2 - WASTEWATER PIPELINE - Excavation and Laying - Undercut approval
label | Detail / Activity - Trench Foundation
label | Acceptance / Conformance Criteria - 300mm Max cut
label | ○ IFC Drawing Sheet 320
label | (Or)
label | ○ Engineers approval
label | Standard / Specification - IFC Drawing WST 0320. AS/NZS 2566.2/2002
label | Verifying Document - Lab Test Report / Wastewater line record
label | Testing Quantity Required (based from schedule qtys) - If Undercut required
label | Verification Activity: Activity - H
label | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - SE
checkpoint | 4.3 - WASTEWATER PIPELINE - Excavation and Laying - Undercut Backfill Compliance (GAP65)
label | Detail / Activity - On Granular Material / On each layer as per specification / on the trench foundation.
label | Acceptance / Conformance Criteria - Visiual Inspection
label | Standard / Specification - IFC Drawing WST 0320
label | Verifying Document - Lab Test Report / Wastewater line record
label | Testing Quantity Required (based from schedule qtys) - Every Undercut
label | Verification Activity: Activity - H
label | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - SE
checkpoint | 4.4 - WASTEWATER PIPELINE - Excavation and Laying - Bedding Zone Compaction Testing
label | Detail / Activity - On Granular Material / On each layer as per specification (Imported Sand/GAP20/19mm chip)
label | Acceptance / Conformance Criteria - Bedding Zone:
label | ○ 100mm minimum thickness (compacted) over the bottom of the trench.
label | ○ Minimum Compaction- 85%MDD
label | Standard / Specification - IFC Drawing 0320-1 AS/NZS 2566.2/2002
label | Verifying Document - Lab Test Report
label | Testing Quantity Required (based from schedule qtys) - As per SW Specification. One test per 10m evenly spaced intervals.
label | Verification Activity: Activity - H
label | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - SE
checkpoint | 4.5 - WASTEWATER PIPELINE - Excavation and Laying - Laying of Pipes
label | Detail / Activity - Lay in straight lines, beginning at the lower end of the line.
label | ○ Lay all pipe with manufacturing codes and class markings facing upwards.
label | Acceptance / Conformance Criteria - As Per Drawings (232735.02-WSP-DR-WST 0208), AS/NZS 2566.2
label | Standard / Specification - PS22.7.1 C, AS/NZS 2566.2
label | Verifying Document - Visual Inspection / Wastewater line record
label | Testing Quantity Required (based from schedule qtys) - Every Line
label | Verification Activity: Activity - H
label | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - SE
checkpoint | 4.6 - WASTEWATER PIPELINE - Excavation and Laying - Pipe Installation on Curved Alignments
label | Detail / Activity - All Industry Guideline PVC, PP AND PE PIPE INSTALLATION ON CURVED ALIGNMENTS (POP202)
label | Acceptance / Conformance Criteria - AS Per POP 202
label | Standard / Specification - PS 22.7.1 D
label | Verifying Document - Visual Inspection / Wastewater line record
label | Testing Quantity Required (based from schedule qtys) - Every Line
label | Verification Activity: Activity - M
label | ○ Monitor on Random Basis
label | Verification Activity: By - SE
checkpoint | 4.7 - WASTEWATER PIPELINE - Joint and Connection: Flanges
label | Detail / Activity - Manufacturer specifies their own bolt tightening torque and sequence, it should override the project specification.
label | Acceptance / Conformance Criteria - Flanges to AS/NZS 4087
label | Standard / Specification - PS 22.7.5
label | Verifying Document - Visual Inspection
label | Testing Quantity Required (based from schedule qtys) - First flanged joint
label | Verification Activity: Activity - HP
label | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 4.8 - WASTEWATER PIPELINE - Joint and Connection: Bends
label | Detail / Activity - PE 100 butt fusion welded segmented bends only where specifically indicated on the Drawings.
label | ○ Fitting must meets the same PN rating as the adjacent PE 100.
label | ○ Fittings must be suitable for producing the joints shown on the Drawings.
label | Acceptance / Conformance Criteria - PIPA POP 006 and AS/NZS 4129
label | Standard / Specification - PS 22.4.2
label | Verifying Document - Visual Inspection
label | Testing Quantity Required (based from schedule qtys) - As per the IFC drawing
label | Verification Activity: Activity - H
label | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - SE
checkpoint | 4.9 - WASTEWATER PIPELINE - Butt-Fusion Welding - Butt-Fusion pre construction weld test
label | Detail / Activity - One weld on the most common size of pipes used for the project.
label | ○ One weld on the thickest wall (highest PN) pipe
label | Acceptance / Conformance Criteria - ISO 13953 for tensile strength and failure mode.
label | ○ WMS Report DVS2207-1
label | Standard / Specification - PS 22.9.6 (a)
label | Verifying Document - Visual Inspection
label | Testing Quantity Required (based from schedule qtys) - Two test welds per operative(Welder)
label | Verification Activity: Activity - HP
label | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 4.10 - WASTEWATER PIPELINE - Butt-Fusion Welding - Butt-Fusion Welding
label | Detail / Activity - Use only semi-automatic or automatic welding machines.
label | ○ Maintain a site record for all butt-fusion welds.
label | ○ The lead welder or supervisor must verify on the site record form that all welds have been made in accordance with the WMS and that the information on the record form is correct.
label | Acceptance / Conformance Criteria - Site Butt Fusion Welding record to be filled out. (Refer to CWP)
label | ○ WMS Report
label | Standard / Specification - Appendix 22. PS 22.9.4 C
label | Verifying Document - Visual Inspection / Butt Fusion welding records checklist. WMS Report
label | Testing Quantity Required (based from schedule qtys) - Every Welding Point
label | Verification Activity: Activity - HP
label | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 4.11 - WASTEWATER PIPELINE - Butt-Fusion Welding - Butt-Fusion Construction weld test
label | Detail / Activity - Test at least two welds from the first 50 welds.
label | ○ One of the welds to be selected by the Engineer for satisfactory result.
label | Acceptance / Conformance Criteria - Tensile testing and ductility of welds.
label | Standard / Specification - PS- 22.9.6 (a) (iv)
label | Verifying Document - Test report
label | Testing Quantity Required (based from schedule qtys) - Two welds for the first 50 welds
label | Verification Activity: Activity - HP
label | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 4.12 - WASTEWATER PIPELINE - Butt-Fusion Welding - Survey
label | Detail / Activity - Inspection of Pipeline Inverts
label | Acceptance / Conformance Criteria - Vertical design Setout:
label | ○ Pipes ≤ 1% grade: +/- 10mm variance
label | ○ Pipes > 1% grade: +/- 20mm variance
label | Horizontal design Setout:
label | ○ +/-30mm variance
label | Standard / Specification - PS- 21.7.6, Table 21.15
label | Verifying Document - Survey Data / As-built record
label | Testing Quantity Required (based from schedule qtys) - Pipeline invert to be surveyed at chainages as indicated in the drawings.
label | Verification Activity: Activity - H
label | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - SE
checkpoint | 4.13 - WASTEWATER PIPELINE - Backfill - Emebment Zone - (Side Haunch Overlay)
label | Detail / Activity - Granular Sand backfill Compacted in 200mm Layers.
label | ○ NDM/CleggTesting to be completed on maximum 200mm lifts of overlays
label | ○ NDM BS to be Carried Out
label | Acceptance / Conformance Criteria - in 200mm layers.
label | ○ More than 85% of MDD.
label | Standard / Specification - IFC Drawing 0320-1
label | Verifying Document - Lab Report / Wastewater line record
label | Testing Quantity Required (based from schedule qtys) - One test per 10m evenly spaced intervals. 200mm lift
label | Verification Activity: Activity - H
label | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - SE
checkpoint | 4.14 - WASTEWATER PIPELINE - Backfill - Pipe Markers
label | Detail / Activity - Lay a conductive signal strip or tracer wire along the full length of all non-metallic pressure pipelines as shown on the Drawings.
label | ○ Mark fire hydrant positions in accordance with SNZ PAS 4509
label | Acceptance / Conformance Criteria - AS Per Drawings.
label | Standard / Specification - PS 22.7.3 a
label | Verifying Document - Visual Inspection / Wastewater line record
label | Testing Quantity Required (based from schedule qtys) - Every Line
label | Verification Activity: Activity - H
label | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - SE
checkpoint | 4.15 - WASTEWATER PIPELINE - Backfill - Backfill Compaction Testing
label | Detail / Activity - GAP65/AP65 Backfill Compacted in 200mm Layers.
label | ○ NDM Testing to be completed on maximum 200mm lifts of backfill.
label | Acceptance / Conformance Criteria - GAP65/AP65or site won material Backfill Compacted in 200mm layers.
label | ○ Testing to be completed on maximum 200mm lifts of backfill.
label | ○ 95% NDM on Shared and Carriageway.
label | OR
label | ○ 28% CIV
label | ○ For site won min >60kpa
label | ○ Ave > 80kpa
label | Standard / Specification - PS- 22.13.5 NDM Standerd 25832, NZS 4402 Test 4.1.3, IFC Drawing 0320-1
label | Verifying Document - Lab Report / Wastewater line record
label | Testing Quantity Required (based from schedule qtys) - As per SW Specification. One test per 10m evenly spaced intervals.
label | Verification Activity: Activity - H
label | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - SE
checkpoint | 4.16 - WASTEWATER PIPELINE - Inspection - Pipe Inspection
label | Detail / Activity - Inspection of Drainage line
label | Acceptance / Conformance Criteria - Inspect pipes prior to backfilling to ensure they have been installed correctly and the joints are in place. Check for gaps and/or defects and check pipe alignment for straightness
label | Standard / Specification - Internal
label | Verifying Document - Wastewater line record
label | Testing Quantity Required (based from schedule qtys) - Continious 1 per Line
label | Verification Activity: Activity - I
label | ○ Formal inspection activity to be undertaken and recorded.
label | Verification Activity: By - SE
checkpoint | 4.17 - WASTEWATER PIPELINE - Testing - Pressure Acceptance Testing
label | Detail / Activity - Backfill/cover with embedment before testing
label | ○ End caps in place, provision for filling the pipeline and bleeding air.
label | Acceptance / Conformance Criteria - Wastewater Rising Main Pipelines – 800kPa
label | ○ Ensure the STP is not more than 25% above the rated pressure of any pipeline component.
label | Standard / Specification - PS 22.7.12(d), PS 22.7.13(b)
label | Verifying Document - Test Report, Pressure Log in.csv or .xlsx format
label | Testing Quantity Required (based from schedule qtys) - All Pipeline, All valves
label | Verification Activity: Activity - HP
label | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 4.18 - WASTEWATER - Manhole installation - Foundation Compliance
label | Detail / Activity - On Granular or Cohesive Material
label | Acceptance / Conformance Criteria - Granular Material: Scala 3 blows/100mm
label | ○ Cohesive Material: Vane Shear Strength min50kpa, ave>60kpa
label | Standard / Specification - Appendix V Table 21:11
label | Verifying Document - Shear vane or Scala test result
label | Testing Quantity Required (based from schedule qtys) - 1 Test/Manhole
label | Verification Activity: Activity - W
label | Verification Activity: By - SE
checkpoint | 4.19 - WASTEWATER - Manhole installation - Undercut approval
label | Detail / Activity - On Subgrade
label | Acceptance / Conformance Criteria - Subgrade CBR between 3.5% <5%: Undercut 150mm and Replace with Compacted AP65 or Approved Granular material.
label | ○ Subgrade CBR between 2% <3.5%: Undercut 300mm and Replace with Compacted AP65 or Approved Granular material.
label | ○ Subgrade CBR between <2%: Engineer to advise or Undercut 450mm and Replace with Compacted AP65 or Approved Granular material.
label | Standard / Specification - Table 21.5
label | Verifying Document - Lab Test Report
label | Testing Quantity Required (based from schedule qtys) - If Undercut required
label | Verification Activity: Activity - HP
label | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 4.20 - WASTEWATER - Manhole installation - Undercut Backfill Compliance AP65
label | Detail / Activity - On Granular Material
label | Acceptance / Conformance Criteria - Average 95% MDD, min >92%
label | OR
label | ○ Clegg 25% CIV
label | Standard / Specification - PS- 16.5.12
label | Verifying Document - Lab Test Report
label | Testing Quantity Required (based from schedule qtys) - 1 Test per Undercut
label | Verification Activity: Activity - H
label | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - SE
checkpoint | 4.21 - WASTEWATER - Manhole installation - Bedding Compaction Testing AP65
label | Detail / Activity - On Granular Material
label | Acceptance / Conformance Criteria - Average 95% MDD, min >92%
label | OR
label | ○ Clegg 25% CIV
label | Standard / Specification - PS- 16.5.12, PS- 21.6.11
label | Verifying Document - Lab Test Report
label | Testing Quantity Required (based from schedule qtys) - 1 Test/Manhole
label | Verification Activity: Activity - H
label | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - SE
checkpoint | 4.22 - WASTEWATER - Manhole installation - Survey
label | Detail / Activity - Inspection of Structure
label | Acceptance / Conformance Criteria - Horizontal Alignment: The permissible deviation of the horizontal alignment between manholes or structures shall be ± 30mm.
label | Standard / Specification - PS- 21.7.6
label | Verifying Document - Survey Data
label | Testing Quantity Required (based from schedule qtys) - 1 Test/Manhole
label | Verification Activity: Activity - H
label | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - SV
checkpoint | 4.23 - WASTEWATER - Manhole installation - Sidefill Compaction Testing
label | Detail / Activity - From the bedding layer to the overlay layer of pipe.
label | Acceptance / Conformance Criteria - AP20/GAP20
label | ○ Testing to be completed on maximum 200mm lifts of backfill - 85% MDD
label | ○ AP20/19mm chip
label | Standard / Specification - PS- Table 21.12
label | Verifying Document - Lab Test Report
label | Testing Quantity Required (based from schedule qtys) - 4 Density test per layer at Quarter Points around the Structure.
label | Verification Activity: Activity - H
label | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - SE
checkpoint | 4.24 - WASTEWATER - Manhole installation - Backfill Compaction Testing
label | Detail / Activity - From Overlay layer to the subgrade layer
label | Acceptance / Conformance Criteria - AP65
label | ○ Testing to be completed on maximum 200mm lifts of backfill - 92% (Average 95%) of MDD on metal.
label | ○ AP65-Clegg28%CIV
label | Standard / Specification - PS- 16.5.12
label | Verifying Document - Lab Test Report
label | Testing Quantity Required (based from schedule qtys) - 4 Density test per layer at Quarter Points around the Structure.
label | Verification Activity: Activity - H
label | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - SE
checkpoint | 4.25 - WASTEWATER - Manhole installation - MH joints inspection
label | Detail / Activity - Inspection of joints
label | Acceptance / Conformance Criteria - Right joint type used, no visual leak or breakage
label | Standard / Specification - PS 22.7.10
label | Verifying Document - Visual inspection
label | Testing Quantity Required (based from schedule qtys) - 1 Test/Manhole
label | Verification Activity: Activity - HP
label | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 4.26 - WASTEWATER - Manhole installation - Inspection
label | Detail / Activity - Inspection of Structure
label | Acceptance / Conformance Criteria - Inspection of Structure prior to backfilling to ensure correct installation and that the joints are sealed. No damages caused to the Structure.
label | Standard / Specification - PS- 21.6.11
label | Verifying Document - Manhole/Catchpit Record
label | Testing Quantity Required (based from schedule qtys) - 1 Checksheet per manhole/catchpit
label | Verification Activity: Activity - I
label | Verification Activity: By - SE
checkpoint | 4.27 - WASTEWATER - Manhole installation - Plumb
label | Detail / Activity - The maximum permitted installed out of plumb is 25 mm of horizontal deviation in 1 m of vertical rise.
label | Acceptance / Conformance Criteria - The maximum permitted installed out of plumb is 25 mm of horizontal deviation in 1 m of vertical rise.
label | Standard / Specification - PS-22.7.10
label | Verifying Document - Survey Data
label | Testing Quantity Required (based from schedule qtys) - 1 Test/Manhole
label | Verification Activity: Activity - H
label | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - SV
checkpoint | 4.28 - WASTEWATER - Manhole installation - Step Rungs
label | Detail / Activity - Step rungs evenly spaced at nominal 300mm vertical intervals
label | Acceptance / Conformance Criteria - Lowest rung more than 450mm above floor highest rung not more than 600mm below the top surface of MH cover
label | Standard / Specification - PS-22.7.11
label | Verifying Document - Visual inspection
label | Testing Quantity Required (based from schedule qtys) - 1 Test/Manhole
label | Verification Activity: Activity - H
label | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - SE
checkpoint | 4.29 - WASTEWATER - Manhole installation - Manhole frame and covers
label | Detail / Activity - Make up the height between the manhole roof slab or precast lid and the finished surface level using concrete riser rings. Set the manhole frame and cover in concrete so it finishes flush with the finished ground or roadway level. Finish the concrete in a way that allows the final surface to be brought close to the cover frame.
label | Acceptance / Conformance Criteria - Make up the height between the manhole roof slab or precast lid and the finished surface level using concrete riser rings. Set the manhole frame and cover in concrete so it finishes flush with the finished ground or roadway level. Finish the concrete in a way that allows the final surface to be brought close to the cover frame.
label | Standard / Specification - PS-22.7.12
label | Verifying Document - Visual inspection
label | Testing Quantity Required (based from schedule qtys) - 1 Test/Manhole
label | Verification Activity: Activity - H
label | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - SE
checkpoint | 4.30 - WASTEWATER - Communication Duct Installation - Foundation Compliance
label | Detail / Activity - It shall be de-watered prior to installation of bedding material.
label | ○ If the bottom of the trench is naturally occurring rock, or has stones, gravel or other sharp material in occurrence
label | Acceptance / Conformance Criteria - 50mm granular layer shall be laid and compacted before the bedding layer is laid.
label | Standard / Specification - PS 25.13.2 c) and g)
label | Verifying Document - Checklist
label | Testing Quantity Required (based from schedule qtys) - Each Cable
label | Verification Activity: Activity - M
label | Verification Activity: By - SE
checkpoint | 4.31 - WASTEWATER - Communication Duct Installation - Bedding
label | Detail / Activity - The floor of the trench shall be clear of any obstacles and shall be as flat as possible.
label | Acceptance / Conformance Criteria - Clean Imported Sand or SAP 7 to be placed 50mm minimum thickness (compacted) over the bottom of the trench.
label | Standard / Specification - PS 25.13.2 g)
label | Verifying Document - Checklist
label | Testing Quantity Required (based from schedule qtys) - Each Cable
label | Verification Activity: Activity - M
label | Verification Activity: By - SE
checkpoint | 4.32 - WASTEWATER - Communication Duct Installation - Installation of Ducts
label | Detail / Activity - If more than 2 ducts are being placed.
label | Acceptance / Conformance Criteria - Must have 50 mm bedding material between the two ducts.
label | Standard / Specification - PS 25.13.7 b) iii
label | Verifying Document - Checklist
label | Testing Quantity Required (based from schedule qtys) - Each Cable
label | Verification Activity: Activity - M
label | Verification Activity: By - SE
checkpoint | 4.33 - WASTEWATER - Communication Duct Installation - Draw Wires
label | Detail / Activity - A draw wire shall be intalled in all ducts and within all sub-ducts to facilitate the hauling-in of cable after the completion of the ducting.
label | Acceptance / Conformance Criteria - Pigmented, stranded polypropylene or equivalent rot-proof material draw wire of 5kN breaking load.
label | ○ ≥20 years design life.
label | ○ The ends of draw wires shall be made fast within the pits and be secured to the duct plugs.
label | ○ Blue colour wire
label | Standard / Specification - PS 25.13.7 e) ii to iv
label | Verifying Document - Checklist
label | Testing Quantity Required (based from schedule qtys) - Each Cable
label | Verification Activity: Activity - M
label | Verification Activity: By - SE
checkpoint | 4.34 - WASTEWATER - Communication Duct Installation - Caps
label | Detail / Activity - All duct ends shall be capped
label | Acceptance / Conformance Criteria - Capped ducts
label | Standard / Specification - PS 25.13.7 e) v
label | Verifying Document - Checklist
label | Testing Quantity Required (based from schedule qtys) - Each Cable
label | Verification Activity: Activity - M
label | Verification Activity: By - SE
checkpoint | 4.35 - WASTEWATER - Communication Duct Installation - Warning Tape
label | Detail / Activity - Warning tape to be placed above services.
label | Acceptance / Conformance Criteria - Warning Tape to be placed no more than 300mm above the topmost duct
label | Standard / Specification - PS 25.13.7 b) iii & f)
label | Verifying Document - Checklist
label | Testing Quantity Required (based from schedule qtys) - Each Cable
label | Verification Activity: Activity - M
label | Verification Activity: By - SE
checkpoint | 4.36 - WASTEWATER - Communication Duct Installation - Overlay
label | Detail / Activity - 150 mm minimum sand placed on top of duct.
label | ○ No mechanical compaction will caarry out till 300mm drom top of duct.
label | Acceptance / Conformance Criteria - 100 mm minimum sand placed on top of duct.
label | Standard / Specification - PS 25.13.7 b) ii
label | Verifying Document - Checklist
label | Testing Quantity Required (based from schedule qtys) - Each Cable
label | Verification Activity: Activity - M
label | Verification Activity: By - SE
checkpoint | 4.37 - WASTEWATER - Communication Pit - Location
label | Detail / Activity - Locations shall be avoided where running water can flow over the lid or where mud and debris can fall or be washed onto the lid .
label | Acceptance / Conformance Criteria - Pit lid and concrete apron shall be flush with ground level in grass, concrete or asphalt areas.
label | ○ When pit is located on a slope of 10 to 30 degrees, the lid shall be flush with ground on the upper side.
label | ○ When slope is greater than 30 degrees, the lid shall be up to 100mm above the ground level on the upper side.
label | Standard / Specification - PS 25.13.8 a) i and ii
label | Verifying Document - Checklist
label | Testing Quantity Required (based from schedule qtys) - Each Pit Location
label | Verification Activity: Activity - H
label | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - SE
checkpoint | 4.38 - WASTEWATER - Communication Pit - Bedding
label | Detail / Activity - Bedding with 150mm compacted GAP20 hard-fill coverd with 20mm compacted sand. Pits shall be carefully lifted into place and lined up with the ducts to penetrate the chamber.
label | Acceptance / Conformance Criteria - 150mm compacted GAP20 hard-fill covered with 20mm of compacted sand
label | Standard / Specification - PS 25.13.8 d)
label | Verifying Document - Checklist
label | Testing Quantity Required (based from schedule qtys) - Each Pit Location
label | Verification Activity: Activity - H
label | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - SE
checkpoint | 4.39 - WASTEWATER - Communication Pit - Sidefill concrete
label | Detail / Activity - Plactic pits shall be cast into the ground with 150mm concrete surround
label | Acceptance / Conformance Criteria - Plactic pits shall be cast into the ground with 150mm concrete surround
label | Standard / Specification - PS 25.13.8 d)
label | Verifying Document - Checklist
label | Testing Quantity Required (based from schedule qtys) - Each Pit Location
label | Verification Activity: Activity - H
label | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - SE
checkpoint | 4.40 - WASTEWATER - Communication Pit - Backfilling
label | Detail / Activity - Backfill and compact the ground around concrete pits. Extra care to be taken to avoid damaging the ducts in 200mm layers of GAP 65.
label | Acceptance / Conformance Criteria - Min 92% compaction rate and Average of 95%.
label | Standard / Specification - PS 25.13.10 a) modified
label | Verifying Document - Checklist
label | Testing Quantity Required (based from schedule qtys) - Each Pit Location
label | Verification Activity: Activity - H
label | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - SE
checkpoint | 4.41 - WASTEWATER - Communication Pit - Concrete
label | Detail / Activity - Top 300mm of pit shall be concreted around with a width of 150mm with a 20MpA concrete.
label | Acceptance / Conformance Criteria - 20 mPa
label | Standard / Specification - PS 25.13.8 d) iv.
label | Verifying Document - Concrete Dockets
label | Testing Quantity Required (based from schedule qtys) - Each Pit Location
label | Verification Activity: Activity - H
label | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - SE
checkpoint | 4.42 - WASTEWATER - Communication Pit - Clean up
label | Detail / Activity - Clean out all pit after completion of the work
label | Acceptance / Conformance Criteria - Pit are free of dirty, mud,water and foreign materials
label | Standard / Specification - PS 25.13.8 e)
label | Verifying Document - Checklist
label | Testing Quantity Required (based from schedule qtys) - Each Pit Location
label | Verification Activity: Activity - M
label | Verification Activity: By - SE
checkpoint | 4.43 - WASTEWATER - Communication Pit - Survey As Built
label | Detail / Activity - As Built every ducts joint before backfill
label | Acceptance / Conformance Criteria - Completed as per drawings
label | Standard / Specification - Standard Practise
label | Verifying Document - Survey
label | Testing Quantity Required (based from schedule qtys) - On going
label | Verification Activity: Activity - H
label | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - PE
section | SECTION 5 – POST CONSTRUCTION (FINAL INSPECTION AND HANDOVER)
checkpoint | 5.1 - Survey As-Builts
label | Detail / Activity - Quality Check on Nee pipeline and structure based on the tolerances in RITS
label | Acceptance / Conformance Criteria - Meets spec as per drawings and capture any NCR or change to design.
label | Standard / Specification - Project Specifications
label | Verifying Document - Red pen markup only
label | Testing Quantity Required (based from schedule qtys) - Post works completion of a lot
label | Verification Activity: Activity - H
label | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - SE
checkpoint | Client Final Inspection - the signature below verifies that this ITP has been completed in accordance with the Specifications and verifies lot compliance.
textbox | Contractor's Rep Name:
textbox | Engineer's Rep. Name:
date | Date:
signoff | Add Signature