## Master List Templates
Id | Type | Name | Values | Prompting Name
98f3e20c-7459-44a1-acf3-d606bbabcc8c | checklist | Add Heyday On-site Penetration Register |  | Heyday On-site Penetration Register
59c53197-7f17-4c08-bf34-cbdecd6a2185 | checkpoint-no-value | Fire Stopping System No.
672e6ca0-d27f-5ade-be47-cadc764e3fd6 | dropdown | Select System No. | FAS190329 - Conduits within concrete,27912900 - Conduit through FRL
e82129a9-505d-4e71-b755-ee0177a1c10c | checkpoint-no-value | Penetration Type
cc41d543-a0b2-5338-bccb-350edabe3c42 | dropdown | Select Type | Floor,Wall,Ceiling
131473b5-4685-4902-9704-23cc5b0c0dad | checkpoint-no-value | Location
faf0f92a-b611-5142-9cc5-1997de933838 | textbox | Location:
0c4e0a22-6611-460c-a28a-e063b47bc23b | checkpoint-no-value | FRL
ff51926a-ed3a-538f-be24-62136736cc0a | dropdown | Select FRL | ~ / 120 / 120
9f625aa4-64a1-4726-aa04-9e338bb01d63 | checkpoint-no-value | Service Description
964bec46-4098-5d46-8d97-65a3ffddbac9 | dropdown | Select Description | Conduits within concrete,Concrete through FR compartment
3ce1e2b8-4527-4c0f-8dfd-51303366e887 | checkpoint | Photo of Fire Sealing & Label
fdca44a3-a610-4a4a-a0ea-7da07a734c72 | checklist | Communications - Cabinet |  | Cabinet
a6b5c039-9104-4d59-ab1d-6bfb5762edd5 | checkpoint | Confirm rack has been earthed
83c98af0-89bb-42b3-871e-fe93cc9cd729 | checkpoint | Confirm cabinet has seismic fixings and bayed together.
0a237f42-78de-4a32-b6a8-8d1d0024fc3d | checkpoint | Confirm cable management installed
c1084f6e-3980-4a5c-8269-2e82fcc13c33 | checkpoint | Confirm cabinet has asset managed label on front and rear
cc59b323-0b74-425c-8606-50e8f1820b7c | checkpoint | Confirm Cabinet is correct orientation
7ea45823-f0f0-4797-a3d6-e4ef97ffaa13 | checkpoint | Confirm PDU-A and PDU-B are on correct side and plugged into correct power supply
2ff22c34-eb26-4df6-afa8-2ad76c2cc4a7 | signoff | Checked By (Heyday/MDE):
b1832b7a-a98e-4f92-936f-06626789fef8 | checklist | Communications - Copper |  | Copper
76c3fe8f-3ddc-4a5e-a05c-ba977ab9a969 | checkpoint | Cabling is not susceptible to mechanical damage.
e18f9918-2b47-40e2-91f9-5482c3f7b9ec | checkpoint | Cable is dressed on the cable pathways with velcro.
eee317b7-8f5b-4eb2-883e-61d2e1a00f59 | checkpoint | Apply a plastic wrap printed label to each end of the cable.
2f3a1f84-388b-47df-90de-dde96ff660f7 | checkpoint | Cable is terminated into a faceplate or surface mount block.
78caadc4-7dd4-4b82-a55a-b5670488ad92 | checkpoint | Cable is terminated into the correct patch panel reflected in the communication cabinet elevations.
fe7c9542-22b6-49bb-8910-c5e9721757f7 | checkpoint | The patch panel, faceplate/surface mount block are labelled correctly with a traffolyte.
dfbecaf3-200a-4be9-8412-b04a17a436d1 | signoff | Checked By (Heyday/MDE):
d80c0715-f329-4661-9a44-68e4b5a51855 | checklist | Communications - Fibre |  | Fibre
e2737053-d94a-48c5-b40d-ea6cb9f0e5d8 | checkpoint | Cabling is not susceptible to mechanical damage.
c283b042-76d5-463a-8cca-eae28e34775a | checkpoint | Cable is dressed on the cable pathways with velcro.
0f151bed-084f-43d3-bbb6-d3158693983c | checkpoint | Apply a plastic traffolyte label to each end of the cable.
434d0ada-b213-43de-a343-48e2bdb3bafb | checkpoint | Fibre optic reticulates into cabinet correctly and is terminated into fobot.
361e5676-c9be-450d-b966-9efe3d620a60 | checkpoint | Fobots is labelled correctly with traffolyte.
716f9a14-a9e5-4c50-ad9f-89cc55535c35 | signoff | Checked By (Heyday/MDE):
6074ec10-56f3-4474-abae-aef805bb6293 | checklist | ITP |  | ITP
652e967d-7a17-434c-bf03-94f23854ac39 | checkpoint | Please attach copy of ITP
df71fccc-889f-4250-bc86-4df129d6a8ae | checklist | LOT BREAK UP |  | LOT BREAK UP
dcdf5328-e886-4cde-95f0-59dde8dc5444 | checkpoint | Attached Mark up of Lot Breakup
0768c84e-b3bd-4c6a-aa09-13255ac65d50 | checklist | Quality - Busduct |  | Quality - Busduct
b5e3fe26-c783-40f9-bcd4-eaf2b88586e1 | checkpoint | Receipt of busduct/ busway & take off box's delivery to site
a3ff3953-176a-4f1f-aa7e-1986d652eda6 | checkpoint | Set out - Ensure correct size, type and spare capacity
d6a046bc-7068-4c9b-9b6c-f8328e22b064 | checkpoint | Accessories to be factory made items
65db417e-1f27-4f5e-819c-78b92e4a29e3 | checkpoint | Hangers installed as per the drawings
299dea92-5f16-4433-a952-cfa942e266da | checkpoint | IR Test of Busduct - Separate - Test Result Above 1M Ω
8454a122-48a5-4d58-aebe-c3d8bdefcfe4 | checkpoint | Busduct Piece are installed safely
c87d056a-92e3-4209-8b5a-28c6bf6d1ea5 | checkpoint | Busduct Torqued to 95Nm
29e3b00e-cad7-45d1-917f-5c5cf497b715 | checkpoint | IR Test of Busduct - Joined - Test Result Above 1M Ω
ac33c530-7829-4181-9de4-04f2f3f3f53c | checkpoint | Photos attached of installed piece
1d378708-99dd-41cd-983b-c8c2d8a87dfb | checklist | Quality - Cable tray/Ladder |  | Quality - Cable tray/Ladder
f7304667-4e24-48f5-86d3-64ffdb1e21d2 | checkpoint | Receipt of Cable Tray delivery to site & storage
2bd9f9cf-263c-476d-95d4-0a08b088bef3 | checkpoint | Set out to be confirmed with latest AFC Drawings
e64772dd-b6dd-4bf5-8a12-dc36b7263180 | checkpoint | Accessories to be factory made items
fc0f799c-8b1b-4379-bc47-2f292f97907c | checkpoint | Correct Levelling & Alignment
b080b835-d7b7-432f-a0c0-8ab4fe9b2f95 | checkpoint | correct bracket and safe fixing
4a33f2d3-208c-4b01-be48-6274464e9497 | checkpoint | Correct Bends used (Cable Ladder)
3928498c-2649-4de9-8894-ce6451f89040 | checkpoint | Cable Tray Checked For Sharp Edges
818b9572-aaf8-4143-80ad-91e2dbb47f32 | checkpoint | Containment Earthing - As Per the Standards
ec96a558-76fa-48dd-91b2-bf90d58d063c | signoff | Signoff Required from Heyday & Multiplex
2d94ecbf-4577-48d4-8ae1-f2e0f5ca54ef | checkpoint | Photos attached.
f5d4527b-a4f5-4f85-a73d-8bb4269b0fe5 | checklist | Quality - Distribution boards |  | Quality - Distribution boards
d6119b14-f47e-46ad-9c3d-1dfc2d7431d3 | checkpoint | Receipt of switchboard delivery to site
bce8f233-f43b-4bb6-a305-e9445debc197 | checkpoint | set out to be confirmed with latest Switchboards Shop drawings
3fed3a41-f5ad-4054-adc2-0c781a13ca4d | checkpoint | Correct alignment to set out drawings
d3ccabc7-63ba-425b-ba90-8961928abe68 | signoff | Signoff Required from Heyday & Multiplex
0b755a50-7baf-4f0c-8830-94a475ae7592 | checkpoint | Correct bracket and safe fixing
aa1624e4-fda7-4b38-9962-42d72de05b34 | checkpoint | Photos of boards attached
942ddc73-90e7-4113-b188-d0d2bd40f2b6 | checklist | Quality - Earthing & Lightning protection |  | Quality - Earthing & Lightning protection
1479e842-cca4-487c-ab4e-fbc4bbd640de | checkpoint | Receipt of Cable & test point delivery to site
39de632f-40ed-467a-b184-4cb1d361cc72 | checkpoint | Correct cable size and Cable type installed per the shop drawing
949d0a9c-6e76-4913-a8b1-243717cdd555 | checkpoint | Installed and Terminated to final locations
6d5b64a1-3d75-444a-b7b6-bd7a5fc618ad | signoff | Signoff Required from Heyday & Multiplex
232b8310-ad90-42ac-8360-ffb23fe6a001 | checkpoint | Photos of test piont and bonds attached
649a71d7-064d-465e-ba05-320512b949a3 | checklist | Quality - Electrical Equipment/Accessory Installation |  | Quality - Electrical Equipment/Accessory Installation
d18315df-1b72-43cc-9143-5c9bc3430f85 | section | Quality - Electrical Equipment/Accessory Installation
585c5f70-3264-4601-aca9-9f6dc7a514ed | checkpoint | Installed Correct Type/Colour of Equipment or Accessory
cac01609-7c33-4cab-af93-fbd489f9fe06 | checkpoint | Installed to the correct location as per drawings
912552dd-470f-4970-90de-7ef32e3bc3fa | checkpoint | Installed with correct fixings and made safe
3c9b09ea-59d1-4090-b937-0a7ad38b7c63 | checkpoint | Installed to the correct Circuit & DB Destination
47fca860-7d93-449d-8125-dc0d57e93b9d | checkpoint | Installed correct labelling
03dffa92-dc6d-46f4-a357-8a4226f1f897 | checkpoint | Final Check and No Damage to item
8cad35c9-294a-40ec-9219-3986eeb6d95b | signoff | Signoff Required from Heyday
befeb558-5dff-408c-be76-d2ce72f1844a | checklist | Quality - In Ground conduit install - HV ONLY |  | Quality - In Ground conduit install.
73a71ac9-bed4-4633-9d29-21efd7bbd825 | checkpoint | Receipt of conduit delivery to site & storage. (ITP Reference Item 1)
2622f687-370d-4ad8-902e-5f73f0b589b6 | checkpoint | Set out. (ITP Reference Item 2)
6259a244-bbfe-42b5-b5fd-9ed8c0ad949c | checkpoint | Excavation - Correct trenching alignment & depth. (ITP Reference Item 3)
90fc07f1-12f8-4be1-896f-b45f3eac4701 | signoff | Signoff Required from Heyday & Multiplex
dd02b98f-0593-48ef-95db-8b6cc4b7ab98 | checkpoint | Conduit Installation. (ITP Reference Item 4)
c0e3dd45-3837-42c7-bee2-80fed1e7f336 | checkpoint | Spacer Frame Installation. (ITP Reference Item 5)
5761ad7f-9073-4e10-8201-47d52ca32c93 | checkpoint | Change of direction/bend Installation, correct bending radius used as per drawing. (ITP Reference Item 6)
d08685d6-ed34-483b-89b9-269076cad5c8 | checkpoint | Bellmouths installed within Insitu Pits. (ITP Reference Item 7)
b3c19a1d-81eb-4263-999c-3a3a7b5c1c09 | checkpoint | Glue Conduits together. (ITP Reference Item 8)
67b70002-92b4-4565-bbe6-d9c23f5fe188 | checkpoint | TSB Installation around & above conduits. (ITP Reference Item 9)
367f0d61-a448-4b6f-9362-f1c6a51d7b09 | signoff | Signoff Required from Heyday & Multiplex
5aba8eea-2b46-4f4a-96b5-2272371c28af | checkpoint | 150mm cover of backfill above TSB. (ITP Reference Item 10)
cd6b3534-56e2-435e-b73b-aa9fcc6bee01 | checkpoint | Warning tape installation above 150mm cover. (ITP Reference Item 11)
f70d4a64-90e6-489b-9c09-8c9e5f9b1ce5 | checkpoint | Back fill & compact. (ITP Reference Item 12)
8162eec1-3d56-4a82-bde2-8d1f7d768500 | checkpoint | Rope & pathway test. (ITP Reference Item 13)
54eb1e84-db3e-4c93-95e4-fbc4fb10d586 | checkpoint | Sealing of conduits. (ITP Reference Item 14) HOLD POINT
53bfa6af-a21d-4791-91fd-86ad581731fa | signoff | Signoff Required from Heyday & Multiplex
acb2f3e9-3777-4399-b35b-cd82a51e0bc9 | checklist | Quality - Inground LV & Communication Conduits |  | Quality - Inground LV & Communication Conduits
9b2fffc9-270e-40a7-8705-dc47b2e2fc93 | checkpoint | Receipt of conduit delivery to site & storage. (ITP Reference Item 1)
70b2b64d-0827-4bee-80ee-6c7a6b30714b | checkpoint | Set out. (ITP Reference Item 2)
0a679e76-8055-432b-9110-4815fb67c9bc | checkpoint | Excavation - Correct trenching alignment & depth. (ITP Reference Item 3) HOLD POINT
59074d54-8fd4-43b0-a5b8-4cdfea916d9c | signoff | Signoff Required from Heyday & Multiplex
357831f8-c75f-46be-9596-87d215933f06 | checkpoint | Conduit Installation. (ITP Reference Item 4)
9e6699ed-e0b0-4dd0-b3a0-700451229f5f | checkpoint | Spacer Frame Installation if required. (ITP Reference Item 5)
a87979ac-06d4-4e99-82f7-e6aaefb00a8f | checkpoint | Change of direction/bend Installation, correct bending radius used as per drawing. (ITP Reference Item 6)
333936bd-24ef-4be2-9e99-69381801f33f | checkpoint | Glue Conduits together. (ITP Reference Item 7)
6987a898-3ce5-4f8a-a5de-6ab949600aeb | checkpoint | 300mm cover of backfill above conduits. (ITP Reference Item 9)
8f0fea9b-58bd-4345-9e8a-4aa51bceb2c8 | checkpoint | Warning tape installation above 300mm cover. (ITP Reference Item 10)
dec68183-4c9b-4ee1-9342-effcea72e79a | checkpoint | Back fill & compact. (ITP Reference Item 11)
96c28ed0-6797-4ae4-b00d-b769a9c6d3bb | signoff | Signoff Required from Heyday & Multiplex
3d9dc89b-30c6-419b-a47d-9320633a0ebf | checkpoint | Record photo evidence. (ITP Reference Item 14)
6ef4f278-b682-4732-b309-dda39a361785 | checklist | Quality - Light & Power Circuit Rough-In |  | Quality - Light & Power Circuit Rough-In
01f55dbc-9321-42c9-8588-c4faba57d6e3 | checkpoint | Receipt of cable delivery to site & storage. (ITP Reference Item 1)
3779156b-7aa8-4293-98fc-e9c4a61a862d | checkpoint | Correct size & cable type. (ITP Reference Item 2) HOLD POINT
02fd3b3d-fed5-4ef9-a1eb-73eddf8ff184 | checkpoint | Installed to correct cable routing arrangements & circuit number. (ITP Reference Item 3)
3ce64644-d2fd-44a9-acc1-15989cddc134 | checkpoint | Installed to final location. (ITP Reference Item 4)
1db46d67-0d00-48c0-bd70-c109140314f1 | checkpoint | Photo evidence captured of cable installation. (ITP Reference Item 5)
da9add73-c80d-4e8d-a6a0-086057f02b00 | signoff | Signoff Required from Heyday & Multiplex
cd19afae-43c1-494e-97bd-9a30d61e02a9 | checklist | Quality - Light Fitting Installation |  | Quality - Light Fitting Installation
fad17488-ad94-4b71-80cd-90db66bcd739 | section | Quality - Light Fitting Installation
89ecbeb9-1176-423a-a888-6e80c6c51b71 | checkpoint | Installed to the correct location as per drawings
0168e49d-c352-4cae-8363-eed09392b39c | checkpoint | Installed correct size and light fitting type
c53357d7-708d-4ff4-8f0b-7f960ca71412 | checkpoint | Correct Operation
04d30ae1-e08f-42ea-8806-db9349c16e3d | checkpoint | Installed to the correct Circuit & DB Destination
5b70a775-2872-4c45-919a-788a71d64678 | checkpoint | Correct labelling of light fitting (if required)
eb0747c8-65ab-474a-930b-ad1bca04f6de | signoff | Signoff Required from Heyday
443eca7d-a2e8-4c87-9677-f00b0242b663 | checklist | Quality - Light Pole Installation |  | Quality - Light Pole Installation
b332fb7b-427d-414c-b5cb-8e86f4847882 | section | Details
ab2d546b-f890-4fc1-81ae-7bc52acf70ba | checkpoint | Receipt of Pole Lights to site & storage. (ITP Reference Item 1)
1f8e819f-a4c7-406e-825d-37a9e6f5c53a | checkpoint | Select correct Pole Light Type for location. (ITP Reference Item 2) HOLD POINT
d7ce0c2f-d79b-4f14-817d-8498cb0cc100 | checkpoint | Install to the location as per Heyday IFC Drawings (ITP Reference Item 3)
0e2a6517-9ab1-4b35-85b0-3ce2f0bd3a56 | checkpoint | Connection to footing and levelling (ITP Reference Item 4)
2370bfe8-a969-4806-8e87-158d373a1720 | checkpoint | Base Plate Grouting (ITP Reference Item 5)
767d3422-cd9a-4ace-abe0-d8e0cf04d7e7 | checkpoint | Termination of Light Pole (ITP Reference Item 6)
e3fca214-7759-443c-952c-8c2daf00b1b9 | checkpoint | Photo evidence captured of Light Pole Installation. (ITP Reference Item 7)
eb807203-b6aa-40ce-bc9c-3a9203c55658 | signoff | Signoff Required from Heyday & Multiplex
bc06466f-09e0-4844-adac-aec4b5269f76 | checklist | Quality - LV and Communication - Pit and Pipe Inspection |  | LV and Communication - Pit and Pipe Inspection
8014076b-6fd0-4f39-92bc-06436c30abbd | checkpoint | Cover Slab and correct Pit installed per shop drawing.
7f8c709e-47a2-46a9-97f3-9530310e73c8 | checkpoint | Pit Lid installed to correct FSL
7392339a-0e99-4210-9eee-1c4acde014c7 | checkpoint | Conduits from pit out have been mandueled using correct size.
2762682b-f76d-4347-b346-e128b9f353ef | checkpoint | Ropes installed in conduits
4a19f46c-9fca-48f7-87c8-9ef56fa500f7 | signoff | Signoff Required from Heyday
e9793bd1-f449-4e14-bf49-ad1a79f8ff50 | checkpoint | Photo of pits installed.
ba235e82-281b-4be6-86a7-99b15884cf5b | checklist | Quality - Main Switchboard Install |  | Quality - Main Switchboard Install
4e2cdcce-3851-423a-a541-3b034abfec6f | checkpoint | Receipt of switchboard delivery to site
af37baef-ea2c-4d09-9044-e0784b0f5248 | checkpoint | set out to be confirmed with latest Switchboards Shop drawings
716a9f94-20d4-4671-948f-dc7edc48366e | checkpoint | Correct alignment to set out drawings
b2e7b34e-3d88-4de2-b56b-a13cac0dbf56 | signoff | Signoff Required from Heyday & Multiplex
4592a97d-1ffe-468f-9314-db6d31bb43bc | checkpoint | Correct bracket and safe fixing
e1732cfa-bc3c-438f-99ff-b6c05049e4c7 | checkpoint | Photos of boards attached
3197a15c-fb25-4da8-93c2-1071feb4a30a | checklist | Quality - Mains and Sub Mains |  | Quality Mains and Sub Mains
5995aabe-eb0b-4f72-bd17-b11af3d003ea | checkpoint | Receipt of cable containment delivery to site & storage. (ITP Reference Item 1)
454354e1-cd28-4ebc-a495-5ba71e40b723 | checkpoint | Cable storage & handling. (ITP Reference Item 2)
f84e2ad5-6f64-4be4-992c-2b0d33e84078 | checkpoint | Correct cable size & type. (ITP Reference Item 3)
355beeb6-9c31-4d23-b970-601bca7f4c7c | signoff | Signoff Required from Heyday & Multiplex
f1021e10-0d78-4abb-a08a-31619a07b4b0 | checkpoint | Cable pulling tension to not exceed manufacturer's recommendations. (ITP Reference Item 4)
260eca92-0c0f-4aab-a131-bc516cea6278 | checkpoint | Cable lubrication if required. (ITP Reference Item 5)
90df3d73-26f0-4bd0-82b7-0e057a263b0f | checkpoint | Installed to latest drawings – schematics/single line diagram & cable containment drawings. (ITP Reference Item 6)
92eb3322-198d-4c8d-b841-6b7ca9b79fbb | checkpoint | Correct cable tag installed. (ITP Reference Item 7)
526951e3-3236-44db-8c32-95480e8172d6 | checkpoint | Photo evidence captured for cable containment install. (ITP Reference Item 8)
cd03cf1f-383d-4515-970e-26c0bb9ee7b3 | signoff | Signoff Required from Heyday & Multiplex
86aa87a6-b5d4-4b51-9765-f9fe0fc446b6 | checklist | Quality - Pole Light Footings Installation ITC |  | Pole Light Footings Installation ITC
93472ed9-c576-4bed-b079-e12233246175 | checkpoint | Receipt of foundation cages delivery to site & storage. (ITP Reference Item 1)
791b4fb7-fecc-41d7-ba76-cc69cb27162e | checkpoint | Set out (Correct pier locations as per approved shop drawings). (ITP Reference Item 2)
19e95f7b-a15c-46ca-a66e-1812cf73670b | checkpoint | Correct trenching alignment & depth with excavator and auger. (ITP Reference Item 3)
22f2ae71-60be-47d2-a9f0-112b19deee8c | checkpoint | Install cage and rag bolts to correct finish level. (ITP Reference Item 4)
13281cde-694f-4b1e-9787-09b3d6d65227 | checkpoint | Install conduits and formatube. (ITP Reference Item 5)
23fa6f29-6099-4518-9c9d-54ac3c86a3d9 | signoff | HOLD POINT inspection prior to concrete
cd81f109-9a77-4b22-a318-90a67a3acbd7 | checkpoint | Concrete installation with tremie pipe. (ITP Reference Item 6)
17ea0ec2-33b1-4fee-be15-8539fba8033e | checkpoint | Photo evidence captured for cable containment install. (ITP Reference Item 7)
1d223f93-c353-40b4-95bf-e85ae1de063a | signoff | Signoff Required from Heyday & Multiplex
f008c625-0eb2-41be-bb21-70905f27afe1 | checklist | Quality - Pole Light Pier Installation ITC |  | Quality - Pole Light Pier Installation ITC
150bb9b1-6ff3-4517-a999-29c791e0df61 | checkpoint | Receipt of foundation cages delivery to site & storage. (ITP Reference Item 1)
40a15249-fc25-438a-a714-c3ec4f9948c6 | checkpoint | Set out (Correct pier locations as per approved shop drawings). (ITP Reference Item 2)
70c1d0ea-0b23-418f-af30-df6a3e39d09c | checkpoint | Correct trenching alignment & depth with excavator and auger. (ITP Reference Item 3)
a554b496-d39e-49df-ada2-7b544e3a5299 | checkpoint | Install cage and rag bolts to correct finish level. (ITP Reference Item 4)
df47fdc0-37ca-4661-9466-466795668e86 | checkpoint | Install conduits and formatube. (ITP Reference Item 5)
adbead86-a352-4716-ae61-5a3fcb4bca6c | signoff | HOLD POINT inspection prior to concrete
eef05d75-6bdd-4963-a418-fea84d40db8f | checkpoint | Concrete installation with tremie pipe. (ITP Reference Item 6)
ecb7f41c-9222-488e-a9dc-2ae0d04db3fa | checkpoint | Photo evidence captured for cable containment install. (ITP Reference Item 7)
755b64e9-dc2a-4a45-92c7-18cf070d7538 | signoff | Signoff Required from Heyday & Multiplex
74ef4895-c901-4195-b1e6-568fa108d3a6 | checklist | Quality - Pole Light Pier Installation ITP |  | Quality - Pole Light Pier Installation ITP
d141cdf8-2c92-468d-981a-8d40874001e6 | checkpoint | Approved IFC Drawings
6d19f8f7-788c-5e0d-bc33-76dd10f80676 | note | Review drawings and revision status with Heyday drawing register, ensuring to only work to AFC drawings, and approved documents:
6537a2f2-5fc0-5d31-ad24-477d3b5fdbe7 | note | WSA50-MPX-02702-EL-DRG-000321[05]
50142c21-8e58-54b0-a011-450d0a00704e | note | WSA50-MPX-02702-EL-DRG-000324[01]
5ede2959-a4a4-5661-90b8-2e133bcd7ac8 | note | WSA50-MPX-02702-EL-DRG-000304[03]
1b604985-bcd6-5249-b8dc-453724b876b5 | note | WSA50-MPX-02702-ST-DRG-001202[04]
b906b77c-0024-4d28-b9bf-a934707889b0 | checkpoint | Material
4d042522-c3ed-59c0-98b3-e389f0bc615a | note | Only use material approved by MPX through the required sample process listed on Heyday samples register as approved:
9dcf734f-1498-43bc-b595-e006ecacecff | checkpoint | Receipt of foundation cages delivery to site& storage.
e5fb6037-18c8-5625-b350-5b308891b02a | note | Review all delivered against approved product submission and confirm conformance. Components parts list, as stated on the purchase order/invoice, to be validated against received items
42000244-686e-4421-a8cb-59ed88c7b67a | checkpoint | Set out (Correct location set out as per approved shop drawings) .
641e1bda-b6cf-535c-a749-bdfc8f2a4302 | note | Set out to be confirmed with latest AFC drawings. WSA50-MPX-02702-EL-DRG-000321[05] WSA50-MPX-02702-EL-DRG-000324[01]
3ce17901-8e6a-45aa-9285-07af72c9dff6 | checkpoint | Correct trenching alignment & depth with Excavator and Auger. If rock is struck, geotech will be required to confirm socket depth
f446e29a-1c71-5f6e-b685-f90d8b55d83d | note | WSA50-MPX-02702-EL-DRG-000321[05] WSA50-MPX-02702-EL-DRG-000324[01]
c8b8768d-7078-4443-93fd-a29b58825976 | checkpoint | Install cage and Ragbolts to correct finish level.
42cae0c5-c6c2-59c4-b958-c38b9208aedf | note | WSA50-MPX-02702-EL-DRG-000321[05] WSA50-MPX-02702-EL-DRG-000324[01]
39ce1519-db25-4e34-adba-82c81eb82cb3 | checkpoint | Install conduits & Formatube.
9432e873-9bf2-5eee-998a-29466ac400f9 | note | WSA50-MPX-02702-EL-DRG-000321[05] WSA50-MPX-02702-EL-DRG-000324[01]
03299ee3-8868-4dd6-97a4-ed326639b3b9 | checkpoint | Concrete installation using Tremie Pipe
0f27ed9f-3b54-5939-ac39-1a396cf37601 | note | WSA50-MPX-02702-EL-DRG-000321[05] WSA50-MPX-02702-EL-DRG-000324[01]
aff63e29-d37a-430a-b815-0b2ac0cb1d1c | checkpoint | Photo evidence captured for asset install
5f6419e0-e42e-5b67-978e-8347f3b8d982 | note | Photo evidence to be captured, stored and provided for formal submission where applicable/outlined within ITP
2401931c-f442-410d-a3b9-fdbcc09f344c | checkpoint | Completion of installation
bc61b16b-a422-592b-a8e3-872930dbfdba | note | Heyday supervisor to ensure that all work has been completed to relevant standards & approved drawings
1ffd0d95-180e-4ef8-8820-4b993ed022ab | checkpoint | Photo Evidence
44f4be71-9bd2-5438-9773-100944729e64 | note | Heyday supervisor to capture & submit photo evidence as part of completed works specified within ITC
d3dd1b34-8145-42d8-945f-de334445dffa | checkpoint | As-built survey & report
e1c38bfd-eb43-5e6e-a058-5a000c373a09 | note | Heyday supervisor to submit As-built drawings as part of completed works
c39d730b-b3ac-4805-bcfa-347c07a5600f | signoff | Signoff Required from Heyday & Multiplex
2a7a5575-2a12-47c2-a292-10a24024510d | checklist | Quality - Power and Lighting Subcircuits |  | Quality - Power and Lighting Subcircuits
70aa64d9-0d08-47a5-8647-185834a86644 | checkpoint | Receipt of cable containment delivery to site & storage. (ITP Reference Item 1)
84059ae9-7244-4dd8-9a39-ebc63fff828d | checkpoint | Correct size & cable type. (ITP Reference Item 2)
4a470d59-f780-42db-bffe-6da8cc16b798 | signoff | Signoff Required from Heyday & Multiplex
db00ad9e-a369-4a3c-bd2f-9ccd89e5e646 | checkpoint | Installed to correct cable routing arrangements & circuit number. (ITP Reference Item 3)
4219368a-1076-4619-8929-abca8707cfec | checkpoint | Installed to final location. (ITP Reference Item 4)
20a0c556-952f-4aa0-bd5d-f94f701bcb09 | checkpoint | Photo evidence captured for cable containment install. (ITP Reference Item 5)
1edfb0b5-9856-4905-aedf-671e3f5cee52 | signoff | Signoff Required from Heyday & Multiplex
14710401-9c29-4f39-b42b-46d1e98b2241 | checklist | Quality - Precast Pit Install |  | Quality - Precast Pit Install
086a6b84-79c1-498b-8fd5-7a0d0772c2d7 | checkpoint | Receipt of Precast pit delivery to site & storage
b14f26fa-c956-42c1-b0eb-9aff33b5c57e | checkpoint | Pit is built to approved shop drawings (photos attached)
130f2cdf-1e80-4855-95c0-2cd47b51596c | checkpoint | correct trenching and alignment & depth
9aded11b-2e7c-4a43-8a19-631766a35474 | checkpoint | installed to correct finish level
c15d1211-1381-4840-9688-999120feaeba | checkpoint | correct back fill installed around pit
81f8fe16-d331-4056-87d5-6661de7afbed | signoff | Signoff Required from Heyday & Multiplex
cb7ac338-822e-4947-bc3d-0bac0e0bc5a9 | checkpoint | Install correct pit lid
8de1c1e5-d080-4a8f-9755-8cb1dff3eead | checkpoint | Photo of pit installed attached.
3ca3689f-77c0-48c2-ab24-e1d735cf09e7 | checklist | Testing & Commissioning - 3 Phase Subcircuit |  | 3 Phase Subcircuit
861fd99c-dca8-43d2-8e4b-f8409081293a | section | Pre-requisite Works
6da69891-19bb-46f6-a2d4-9b9cf3d8e4bc | checkpoint | Insulation Damage
7225f360-ac04-4778-95db-9dbcc07e76ac | checkpoint | Correct Type of Termination
3971722c-baa9-43a9-aa06-c86c6056edfb | checkpoint | Correct Colour Code
9708cbf1-ec02-4027-9710-1f71e383629d | checkpoint | Correct Outlet Rating and Size
e327169b-3ebd-4006-adbb-d344cb7384ca | checkpoint | Earth Continuity
d1fad654-d6b7-5aaa-ad18-5ced852d1212 | textbox | Resistance (Ω)
21706f16-3e14-4132-869a-39878965623e | checkpoint | Polarity Check
a878f000-c1ad-5c8c-917d-0e62e1a0e5c2 | button | No Transposition | YES,NO
b8ec0463-70f4-5599-97fb-21e80b4abc49 | button | Switch in Active | YES,NO
9cac9730-f4a3-4380-b5fb-b44eee12d42e | section | Insulation Resistance
96dd6692-f9e5-4dbd-8b51-64a37deb1e6e | checkpoint | R-W
2b39491a-1d6a-511a-82f4-71cfabd13a8c | button | Insulation Resistance shall not be less than 1MΩ (Tested at 250VDC/500VDC) | >200MΩ,>500MΩ,N/A
d348ccc8-6968-5dae-a021-9c9ceffa5e6f | textbox | Actual Reading if <200MΩ/<500MΩ
f206d7ac-521d-4be4-8f41-eea8e2e1e3bf | checkpoint | R-B
52a2c584-84aa-5609-880b-8300f96e8f5e | button | Insulation Resistance shall not be less than 1MΩ (Tested at 250VDC/500VDC) | >200MΩ,>500MΩ,N/A
f9cb7812-44c5-52af-a9b2-3ffb8d4e72a6 | textbox | Actual Reading if <200MΩ/<500MΩ
882b4c0f-8dcb-4d8c-8881-b4c7b13c157a | checkpoint | W-B
c6af3168-67a5-5e0e-935f-deba5b39563d | button | Insulation Resistance shall not be less than 1MΩ (Tested at 250VDC/500VDC) | >200MΩ,>500MΩ,N/A
92fa960a-d385-55d2-a305-6489a079a3f0 | textbox | Actual Reading if <200MΩ/<500MΩ
8ed72945-9322-49ab-879b-2450c3ad8f68 | checkpoint | R-N
f3510836-c94f-5348-bc00-0fe3bd323739 | button | Insulation Resistance shall not be less than 1MΩ (Tested at 250VDC/500VDC) | >200MΩ,>500MΩ,N/A
8f7cadda-8d23-53d8-af25-7ee29ed9e6e2 | textbox | Actual Reading if <200MΩ/<500MΩ
3ce7661c-5fca-41d4-a5a5-790a3a4b01c6 | checkpoint | W-N
4037876f-d6e5-5dbc-9a61-0e8ea3923279 | button | Insulation Resistance shall not be less than 1MΩ (Tested at 250VDC/500VDC) | >200MΩ,>500MΩ,N/A
d477f3c7-aa58-5755-aa05-0b066a1b7cef | textbox | Actual Reading if <200MΩ/<500MΩ
9651f12e-c9a4-442d-bc8c-f11c854fa56e | checkpoint | B-N
4605fcfd-7b25-5173-a9e7-a07339fd902c | button | Insulation Resistance shall not be less than 1MΩ (Tested at 250VDC/500VDC) | >200MΩ,>500MΩ,N/A
a0128354-5305-5bf4-8282-5f7a8295fc7f | textbox | Actual Reading if <200MΩ/<500MΩ
6e4631a7-7c3b-405e-ab1b-9f82b89f9fd9 | checkpoint | R-E
c64a6297-5d59-5b92-87a9-d2b62a3fbf04 | button | Insulation Resistance shall not be less than 1MΩ (Tested at 250VDC/500VDC) | >200MΩ,>500MΩ,N/A
144b208d-ae23-5be7-9e51-128cf9d3dcc2 | textbox | Actual Reading if <200MΩ/<500MΩ
0fccc83f-b50d-4cc0-a288-d4c98f56d0fd | checkpoint | W-E
a0b931b0-76eb-54d1-bfa0-459efcda5dcf | button | Insulation Resistance shall not be less than 1MΩ (Tested at 250VDC/500VDC) | >200MΩ,>500MΩ,N/A
84054121-9153-5416-93f7-c6d93908d8d6 | textbox | Actual Reading if <200MΩ/<500MΩ
fc799b05-5f47-4321-a8db-0c227ad69d10 | checkpoint | B-E
729c09c8-067e-5ce3-8113-46aaef757ae0 | button | Insulation Resistance shall not be less than 1MΩ (Tested at 250VDC/500VDC) | >200MΩ,>500MΩ,N/A
f51bf965-727e-5964-8a37-3fb5928b1a41 | textbox | Actual Reading if <200MΩ/<500MΩ
827f6e60-be17-4eca-9c30-2c54ef6f95c4 | checkpoint | N-E
977a6a16-6d9e-51d3-9adc-0d181d6c3fed | button | Insulation Resistance shall not be less than 1MΩ (Tested at 250VDC/500VDC) | >200MΩ,>500MΩ,N/A
22efc18d-777c-5ae2-9787-29ab2333ca6e | textbox | Actual Reading if <200MΩ/<500MΩ
e60f69f2-5a59-44f0-8566-b462615f9a6b | section | Voltage
cac5f44a-a6bc-43b1-bc53-f27a0da64f14 | checkpoint | Red - White
d4f6e39a-cf4b-52ba-bdcb-be3fcffe2da4 | textbox | Voltage (V)
04166c8d-957b-4eff-8864-5075cad5d374 | checkpoint | Red - Blue
c2419cc4-d59c-522d-bc84-c1b9e086ff6d | textbox | Voltage (V)
8d39a288-efcc-46a4-94b9-e7db2c44ff87 | checkpoint | White - Blue
b6a6b526-117f-5e79-8caf-03a2f65b3c2c | textbox | Voltage (V)
37f3f198-3fa3-4e3c-8adc-2d6c6cbb04a1 | checkpoint | Red - Neutral
84e20906-51b7-5586-ba8a-2d4a0116eb57 | textbox | Voltage (V)
ba9cca36-b89a-4d4e-91ec-08c54b9d4d4d | checkpoint | White - Neutral
5b8dd4b2-2a55-5141-8932-7780c4377448 | textbox | Voltage (V)
105d0dae-3ddb-45ad-8b9a-83a2318b7f89 | checkpoint | Blue - Neutral
d043e074-431b-5586-a349-5e7e8b33c605 | textbox | Voltage (V)
f2f49762-0dc4-40de-95b0-61b04776d6e4 | checkpoint | Red - Earth
d88e464b-bed5-5f0c-af21-50d796bb2403 | textbox | Voltage (V)
2d1255f8-a0dd-4086-9488-3b81ccfe8362 | checkpoint | White - Earth
525be556-c6cd-5964-97e9-9b8c22e9604b | textbox | Voltage (V)
f436332f-ea9d-4c26-baaf-6498f0980e05 | checkpoint | Blue - Earth
a12e795b-46a0-5ee2-be31-e824ee9c758c | textbox | Voltage (V)
4bb0e1c9-4368-4df3-bb6e-c9fb61376ee0 | section | Earth Fault Loop Impedance Test / RCD-RCBO Tripping Test
b0df5f2e-1ff1-49a7-8eba-c133f962acfe | checkpoint | Impedance - (N/A if the circuit is RCD Protected)
b044fe0b-852f-5b44-844f-169a2ebc699d | textbox | Record Inpedance (Ω)
b93650ce-1006-567a-bce0-c07128c7e1cf | textbox | Target Impedance (Ω)
79eb7072-a04e-4b6a-85e5-30b4b5f2109d | checkpoint | RCD-RCBO Tripping Test
abf38619-a914-59e4-97ed-521a8167c7c6 | textbox | Trip Current (mA)
273439a4-eb3c-5eaa-b343-12c237a4b61d | textbox | Trip Time (ms)
6aa7fba7-6aac-4dd5-a301-11e58a52dfb3 | signoff | Checked By (Heyday):
c4fab001-6d7f-4e61-9514-e45467024253 | checklist | Testing & Commissioning - Communications Cabling |  | Communications Cabling
55d94b5c-3689-4cb2-8f73-9160690a51be | checkpoint | Cable installed to Manufacturers requirements
f4a63d89-7085-4de9-a646-9ff3b5e2c2b7 | checkpoint | Cable Labelled
57b1b891-a26a-4284-b199-006ddec485d7 | checkpoint | Cable Terminated
0b118d6f-2240-4905-9767-72c4a3c64569 | checkpoint | Cable Tested
61d91b88-697a-4bdc-a7a3-1d7e495d395f | checkpoint | As-Builts reflects installed Cable Number and Location
86dbe344-1f18-4c57-9799-284e4f4985ac | signoff | Checked By (Heyday):
075cbb8f-7395-4215-990a-36ee8f123766 | checklist | Testing & Commissioning - Distribution Boards (Energised) |  | Distribution Boards (Energised)
ac8d2b3a-1062-4805-9ee2-f6ed983b5857 | section | Phase Voltage Reading
a53ff1c6-2797-40a2-a2f8-f7d38489ecdc | checkpoint | Red - White
41085b71-2ea6-5b63-a473-f908e40c84db | textbox | Voltage (V)
16a098d4-cc95-4d40-b7f2-5a6f971a8dae | checkpoint | Red - Blue
196e18ef-44d6-5e0c-a2a1-3e123df518ec | textbox | Voltage (V)
5f5f3b6a-f863-41d2-b2f2-ae73ae753490 | checkpoint | White - Blue
dd4fb89a-49d2-5cb5-81f7-9353800034b4 | textbox | Voltage (V)
2c7982e1-caca-49f5-b608-0d810e12fc87 | checkpoint | Red - Neutral
84ea402e-0a70-5ef7-875a-b3d7242e3e72 | textbox | Voltage (V)
23082f5e-1a0c-4b41-87eb-0d83fd061e60 | checkpoint | White - Neutral
3559dc80-e4b9-529a-b961-94b338fdf2a5 | textbox | Voltage (V)
d20cf236-03c4-48ec-bb3d-a76d4c0a7931 | checkpoint | Blue - Neutral
b5c0d298-c429-55a3-b066-19c0ef1adec4 | textbox | Voltage (V)
828bffa7-26e3-4c1a-9bae-5901fdb6fa71 | checkpoint | Red - Earth
5e97d0e2-e2ab-5fd5-b47a-2336dfd51118 | textbox | Voltage (V)
1258b1f5-490b-4bed-a1f2-aa12c5f28b2c | checkpoint | White - Earth
ac623e8d-cf6b-505d-bb88-361d6a1997e1 | textbox | Voltage (V)
5b1ac89f-0558-43f0-863a-940529d8515e | checkpoint | Blue - Earth
3970221d-9189-52b1-8a60-1654c34deea7 | textbox | Voltage (V)
2817d947-17af-4959-86d2-ad261376d5c6 | section | Phase Rotation
b88f8ba0-5ca0-416a-833c-5540c7146713 | checkpoint | Direction
ae1d7739-bc6e-5e73-89bd-a6284a3ee7fb | button | Direction | Clockwise,Anti-Clockwise
60203d98-7d92-49d7-941d-68aecd92f89d | signoff | Checked By (Heyday):
ab447333-a299-4292-8db0-7bf6f22c0c5a | checklist | Testing & Commissioning - Distribution Boards (Pre-Energisation) |  | Distribution Boards (Pre-Energisation)
8977fb2d-d688-4cf3-ba87-cb3b8fa58f11 | section | Physical Checks
53931865-a78a-45ab-97ba-c708723ce19b | checkpoint | Confirm board's dimensions are in accordance with approved shop drawings (provide drawings reference in the Comments section)
406cc207-1337-4249-b626-ad3c99a32f08 | checkpoint | Confirm correct circuit identification and labelling
9fe77cb5-17a2-4cbd-986f-6b77e11a3212 | checkpoint | Confirm the board busbars and cables are tighten as per manufacturer recommendations and standards. Provide applied torque in the Comment section
803faee4-c37d-40fe-9c85-2e74fc369c5b | checkpoint | Confirm correct phase identification of busbars and cables inside the board
47ec17c8-ae92-4b4d-866c-ff0d9ea6aee2 | checkpoint | Confirm correct size of earthing conductors
63b54de8-ad3b-41d3-a0f3-fc5241186aa9 | checkpoint | Confirm no visual damage to the equipment or meters. Mark the observed issues in a Comment section (if any)
64c1c2c8-43ed-4fd4-bb5b-5d012ed1db54 | section | Mechanical Checks
cf8b9aa7-08fd-4c0e-91c8-cbb9f004a809 | checkpoint | Repeat manual closing and opening of moulded case circuit breakers for 3 times
49cfc303-218e-487c-81da-99c451f007b0 | checkpoint | Repeat manual closing and opening of miniature circuit breakers for 3 times
bcb84516-3183-41b4-96f5-4fce85c25419 | checkpoint | Repeat mounting and dismounting of power fuses for 1 time
aa08c339-65f9-48dd-bb4c-bcb7bb3ecc17 | checkpoint | Repeat mounting and dismounting of control fuses 1 time
bc551d4c-f188-4b41-92fa-cc1e5bb9ac39 | checkpoint | Conduct the torque test for all bolted connections and confirm the torque is in accordance with manufacturer recommendations and standards.
48adfc55-5257-4635-a37d-8aaa1cdb361a | checkpoint | Conduct pull test for all cables connected to MCBs and Termination blocks
21404c63-9e24-472c-9e6b-fcff18e7f796 | section | Preliminary Checks
28c77213-b2ae-49b2-8713-4e8526be9db4 | checkpoint | 1. Confirm all fuses Removed in board’s Control Sections
8dfbd3cf-e1f3-4186-92f7-84d6786be3cd | checkpoint | 2. Confirm Main Breaker Closed
19f52456-4a04-4556-af92-67733c2ddd7c | checkpoint | 3. Confirm Outgoing Breakers Closed
bdf6c1bc-a00d-4ab5-9aff-1bbba6598c13 | section | Insulation Resistance (500V)
95780f93-e76b-4d2f-9976-285f8da63ae6 | checkpoint | 1. Between L1 Phase and Neutral
d13d1e56-7dcb-5e3a-9b5c-a0177a9b705e | button | >10MΩ | YES,NO
acb50fa4-ec67-553a-ac17-a3c84289aef3 | textbox | Actual Reading if <10MΩ
97429c4d-a75b-43ac-b3d6-8e93dea59342 | checkpoint | 2. Between L2 Phase and Neutral
b536bc25-10c9-5f2b-b54e-2d017764b346 | button | >10MΩ | YES,NO
fbc00ebb-87e0-5b6b-b6ea-a7b87cda5dde | textbox | Actual Reading if <10MΩ
56504dc8-adab-47d4-b32b-f0ef6bf26930 | checkpoint | 3. Between L3 Phase and Neutral
bf84e43c-e7a0-5de6-8d9d-eaaa028eb099 | button | >10MΩ | YES,NO
21adcd4d-6cbf-5f5e-b8a8-b96d7ba516f5 | textbox | Actual Reading if <10MΩ
59e61667-dcdb-4fdf-a339-2e207b35bcbb | checkpoint | 4. Between Neutral and Earth
a7c183bc-5dac-5983-b295-3010e75cbb96 | button | >10MΩ | YES,NO
a7e77f7f-29c5-518c-9001-05d65d66e0fa | textbox | Actual Reading if <10MΩ
555ad5dc-50ed-4de6-bb8e-e1c1569a6e90 | checkpoint | 5. Between L1 Phase and Earth
baf66c08-1e2a-5e9b-92bf-4c4497f8506c | button | >10MΩ | YES,NO
a613c700-5f1c-5268-b5ff-dd5877585430 | textbox | Actual Reading if <10MΩ
758028f6-f6fa-43eb-906b-ad9ba25d281f | checkpoint | 6. Between L2 Phase and Earth
1429255c-7841-56ad-8697-2c6d159d4785 | button | >10MΩ | YES,NO
3cb29882-53f7-571c-a986-60f07c038d4a | textbox | Actual Reading if <10MΩ
7d0031ee-ffd7-418b-8ad9-32353aca2e22 | checkpoint | 7. Between L3 Phase and Earth
6b34d913-698f-543f-acbd-b15ce2393323 | button | >10MΩ | YES,NO
eca5e2f2-4f96-54a4-bd9c-d773ef32d661 | textbox | Actual Reading if <10MΩ
95d05598-ce63-4609-bc1e-50944d2c5aac | checkpoint | 8. Between L1 Phase and L2 Phase
f2d0ded0-11dc-5ed7-b174-7ae1e1f2de7f | button | >10MΩ | YES,NO
409049d8-bf8e-5277-b9d3-092b1ed58bf4 | textbox | Actual Reading if <10MΩ
f5ff6e4a-a62f-4e95-aea1-04b18472b68c | checkpoint | 9. Between L1 Phase and L3 Phase
062ccca4-0713-55fd-a25e-95a99c06db87 | button | >10MΩ | YES,NO
94d30298-de90-5b38-bbbd-e6d83151d789 | textbox | Actual Reading if <10MΩ
bb98cdd5-869c-44eb-8f53-98f3bc74dcc8 | checkpoint | 10. Between L2 Phase and L3 Phase
bb2650ae-08aa-536f-bfd8-7ae3895db90c | button | >10MΩ | YES,NO
eabaa815-6458-54b1-aa8c-0d477e6c4d97 | textbox | Actual Reading if <10MΩ
7ce3d526-d0f2-46a6-919a-831e9e8f6dd5 | section | Earth Continuity Test
f3e1e57e-5bd1-4798-b4c6-f29e27628b90 | checkpoint | Earth Continuity
2a6ea1f6-c5ff-500e-9214-32679eb3c7c6 | textbox | Resistance (Ω) - [Target: <0.5Ω]
36c84e5b-0495-4dfc-b941-3b128d44482c | checklist | Testing & Commissioning - Earthing Systems - Construction Tests (Earth System Reticulation) |  | Earthing Systems - Construction Tests (Earth System Reticulation)
5d791298-49e3-4116-b523-c359d010f8b6 | checkpoint | Correct Cable Size and Labelling
3124bc43-3fc7-4493-9eea-108a575e2ae1 | checkpoint | Earth Continuity
c5ad7585-699d-581b-8267-c3d24da56d0e | textbox | Resistance (Ω)
e8f761bb-2760-541e-b5ec-9156d4f317ce | textbox | Target Resistance (Ω)
5c7272eb-5012-417d-9440-1e7547cbd7b6 | signoff | Checked By (Heyday):
cae18be9-29d2-43c5-a730-ba3a912fa0c5 | checklist | Testing & Commissioning - Earthing Systems - Construction Tests (Main Earth System) |  | Earthing Systems - Construction Tests (Main Earth System)
d269a52a-29a7-45f0-ade5-97796ceae758 | checkpoint | RWV Industries – Earthing Test Report. Steel Reinforcement Continuity
aa286d59-6b01-4cdd-895a-a4bae9404a65 | checkpoint | RWV Industries – Earthing Test Report. Footing Earthing
8d60bbbe-1ea3-4ffc-acc6-cc9659a95a68 | checklist | Testing & Commissioning - Emergency Lighting |  | Emergency Lighting
c2dfcdbf-2955-419d-b108-ffede429bf4f | checkpoint | Pre-requisite Works
22880dd4-2579-4d39-b8c9-957b8934c66f | checkpoint | Correct Location & Labelling
919b553b-f5f3-4c09-8f17-9d5c2b61169a | checkpoint | Correct Software Mapping
bc6f4cea-40bb-4efd-b470-b4392c182cc9 | checkpoint | Discharge Autonomy Test
e7af81ef-61e0-4cde-9f0b-c1aae177aa04 | signoff | Checked By (Heyday):
f8f7170d-7d95-45ff-a33e-8660a43544f1 | checklist | Testing & Commissioning - HV/LV Transformers |  | HV/LV Transformers
0969b89b-13b4-4408-9f80-44764c16f940 | checkpoint | Schneider Electric Transformer QA/QC Test Report – Installation Configuration Page 3.
71e45806-0bf8-420a-9058-dc8022588864 | checkpoint | Schneider Electric Transformer QA/QC Test Report – Pre-Testing inspection Page 4.
3db19474-7cc3-4bc9-96d7-b8a25713e7af | checkpoint | Schneider Electric Transformer QA/QC Test Report – Transformer Test - Page 4:
f8c6c0e2-0485-509a-931b-46c872a5edc9 | note | Continuity test on HV and LV Windings
3faf0bd7-0a5a-5492-be65-9c05fe1f5766 | note | ○ Insulation Resistance Test LV Winding to Earth
a9a2e7ec-06f4-5b0c-89c3-d73ab8bec5d5 | note | ○ Winding Resistance
d5f48f7a-6630-5728-8eb8-e0783cbc2636 | note | ○ Winding Ration verification (taps: +2.5%, +1.25%, 0, -1.25%, -2.5% )
07063b97-3ec1-52e0-b91d-4ecb899353d4 | note | ○ Vector Groups
b63500bd-c421-55e0-9a61-593f3e871930 | note | ○ Check bushings
bb642782-7878-5cb6-a87d-4afc54389d15 | note | ○ Control cubicle visual inspection
8d2f3627-9622-502b-9733-5ad37a7f6000 | note | ○ Control Cabling within the control cubicle visual inspection and connection verification against approved schematics
c61de0f1-9a75-591c-8fd3-a5716389ee98 | note | ○ Confirm opening of LV door operates “normally open contact when doors are closed”
5c13a156-5bca-4154-a40f-5738c1d988f4 | signoff | Checked By (Heyday):
4f516721-9264-4603-a113-5d0c70e71377 | checklist | Testing & Commissioning - Lighting Control |  | Lighting Control
8c82fdbe-8112-4b24-8d84-0462942894a2 | checkpoint | Pre-requisite Works
f6adb625-199d-424f-91ee-be65f1df8ba3 | checkpoint | Correct Location & Labelling
857c855a-81e6-4de5-a16a-74858e79f3c5 | checkpoint | Manual Control
e0ecd3a3-ac7c-4d58-81db-b765f2d3fefa | checkpoint | Occupancy Sensor or PE Cell Control
420e3ac5-6120-45c2-9561-ce56de03204b | signoff | Checked By (Heyday):
ff0e237c-dd3c-4bd6-9493-b3cb341861c7 | checklist | Testing & Commissioning - Load Bank |  | Load Bank
536dda0e-5101-4baf-9bdf-b0735aff5fb9 | section | WSA20-MPX-04000-EL-ITC-31143000 - Component Tests (Pre-commissioning)
7bdbd1de-9025-4189-85e4-2fcb1213e2e6 | checkpoint | Sephco Commissioning Checklist
f3d07a75-f318-4c18-bc0e-9b2acceba9c5 | signoff | Checked By (Heyday):
0ab4814e-ddcd-49f8-8d06-d7ee539439a5 | checklist | Testing & Commissioning - Low Voltage Busduct (Energised) |  | Low Voltage Busduct (Energised)
56b517ed-d914-41f2-96a7-965ae9efdff1 | section | Phase Rotation
4c6ab7d8-e371-4454-b5bd-85d1fc9e87e2 | checkpoint | Direction
a30d2ede-1096-5c42-975d-8a1be371ca17 | button | Direction | Clockwise,Anti-Clockwise
fa9a7ff6-7c7a-431a-983e-756bb25dea55 | signoff | Checked By (Heyday):
8e265440-c473-440d-a516-0359dd4e6393 | section | Voltage
94d46092-4876-4725-b9f8-5d7434200652 | checkpoint | Red - White
4acfc2d5-d4cd-5a9e-a48e-4556de77b138 | textbox | Voltage (V)
cea9d429-b75d-431a-85a7-aa3358f67df3 | checkpoint | Red - Blue
33b3e158-b999-558b-8219-4378cabaf116 | textbox | Voltage (V)
f78d8e9d-64fb-4a16-9fee-f2eae06c45c3 | checkpoint | White - Blue
3aa40e1d-b21a-5f71-8fac-e8968bdbf5e1 | textbox | Voltage (V)
1898309a-844d-4694-b4ce-867734163b9e | checkpoint | Red - Neutral
f5241f11-686a-59f5-9ff4-cfdbe0b920e4 | textbox | Voltage (V)
9fe0a72a-67fd-4f6d-b4bc-657002c5487f | checkpoint | White - Neutral
1e87b879-5ba3-5d4b-825b-a059e4ff959c | textbox | Voltage (V)
d5eb50a9-bf63-4c23-82f2-2807888f24dd | checkpoint | Blue - Neutral
bf6b7655-9c2e-5ff2-9973-938cf3c6aaf6 | textbox | Voltage (V)
5659b85a-684e-49c6-9618-92a793aea502 | checkpoint | Red - Earth
2b3b47e3-65cb-5550-b872-92b0c10c686f | textbox | Voltage (V)
747676ca-124e-403e-9c65-c5ba6e57922d | checkpoint | White - Earth
1f5ad7ba-1296-50a3-8a73-943d46b0379a | textbox | Voltage (V)
a24327c9-3e70-4ccc-bb76-6fd489037fda | checkpoint | Blue - Earth
b045f50e-7da0-5ed0-af29-d3fad1980b0c | textbox | Voltage (V)
4d8d5f35-7891-47d0-8ebd-e1cb5724390f | signoff | Checked By (Heyday):
13cf0cf9-c3da-4e9c-bb52-18cc0215eece | checklist | Testing & Commissioning - Low Voltage Busduct (Pre-Energisation) |  | Low Voltage Busduct (Pre-Energisation)
2683ac7d-d83d-434f-86db-4bc68ec544c8 | section | Pre-requisite Works
6f6e2026-e685-47f6-96eb-26aab5f17835 | checkpoint | Insulation Damage
fbb93c2b-c852-4a57-b3e1-c9ab11a568fc | checkpoint | Correct Type of Termination
cfc0e5d9-f976-494b-9421-9032e5ad627c | checkpoint | Correct Colour Code
4478576e-9436-47da-943e-dbc0c0770867 | checkpoint | Correct Size and Labelling
0af3d548-923b-45c1-9792-4072fb23bf3a | checkpoint | Correct Routing
52688ba0-c53b-4ecf-9ceb-ed2c6bea4ef1 | section | Continuity Testing
2bbbeb81-d76f-4ab7-9b37-4af81c15d03e | checkpoint | Red Phase
bccf9913-d1d2-56f3-a607-88c92ed9ccab | textbox | Resistance (Ω)
f6644a85-f277-584c-b823-e4aabc9fe3fa | textbox | Target Resistance (Ω)
fb88138b-a601-468d-a400-b241f2a7d8f1 | checkpoint | White Phase
0b7948c2-7d82-5100-8f1b-4cea01b30f18 | textbox | Resistance (Ω)
66424b14-26aa-5233-a73e-8fa6cc8050f6 | textbox | Target Resistance (Ω)
9c311428-b330-40eb-b40c-1dd67b1725aa | checkpoint | Blue Phase
52743c86-7a1e-5846-9ed4-16d922e5a47a | textbox | Resistance (Ω)
5f38758d-f8b6-51ab-a26e-c74dd36d841b | textbox | Target Resistance (Ω)
b34c5bdc-1be4-4637-b9d2-444cd99281de | checkpoint | Neutral
f370275e-68f7-5955-8861-2dcb1588eb3e | textbox | Resistance (Ω)
585a13f3-7590-5d8a-bbc8-95d5275da47a | textbox | Target Resistance (Ω)
30c50d31-0f05-4055-a918-1ca7a5211171 | checkpoint | Earth
3b368092-9571-5aa2-a2a7-e0730ef000fd | textbox | Resistance (Ω)
b7961f1e-bd19-544e-968b-da79a8efb990 | textbox | Target Resistance (Ω)
fb07be62-3a2f-4f9c-b77d-500cab4e5db9 | section | Insulation Resistance
4b1c9924-2f9e-4a2f-9e95-666cf0fe70da | checkpoint | R-W
71e52e0f-a926-568d-a8cd-a92f6c639b94 | button | Insulation Resistance shall not be less than 1MΩ (Tested at 500VDC, 1000VDC) | >500MΩ,>1000MΩ,N/A
236615dc-9f7f-5d83-b480-8f4a2ee5b083 | textbox | Actual Reading if <500MΩ/<1000MΩ
40e123b4-db69-43d8-9785-4b395c22ffc5 | checkpoint | R-B
970d468e-6b01-5be9-b3b6-05d5078c0aab | button | Insulation Resistance shall not be less than 1MΩ (Tested at 500VDC, 1000VDC) | >500MΩ,>1000MΩ,N/A
33641d8f-e337-533a-a805-87211cbf3a91 | textbox | Actual Reading if <500MΩ/<1000MΩ
8d09ae7e-c911-4b43-af36-414ea08fcce7 | checkpoint | W-B
b3b8d3a8-65a5-5c5d-aeec-ccbf4ea127a9 | button | Insulation Resistance shall not be less than 1MΩ (Tested at 500VDC, 1000VDC) | >500MΩ,>1000MΩ,N/A
ee127d77-1bf2-5c44-b48e-7269a34edaeb | textbox | Actual Reading if <500MΩ/<1000MΩ
160b2c93-6069-4671-95ba-e72256df6f8b | checkpoint | R-N
bd4e072d-3fcf-52ff-82b9-294e57745273 | button | Insulation Resistance shall not be less than 1MΩ (Tested at 500VDC, 1000VDC) | >500MΩ,>1000MΩ,N/A
7ec26620-539d-538d-ba0d-db4f4d700f79 | textbox | Actual Reading if <500MΩ/<1000MΩ
2218ed7b-c321-493c-b1f1-41861b0b0a42 | checkpoint | W-N
f2522ff5-f858-50ac-afa5-d36327eba8b7 | button | Insulation Resistance shall not be less than 1MΩ (Tested at 500VDC, 1000VDC) | >500MΩ,>1000MΩ,N/A
a8e1d7e2-1f9d-5fae-a962-5a9ff4b7e50e | textbox | Actual Reading if <500MΩ/<1000MΩ
a13a077c-4e34-4816-acfd-d56ca034e416 | checkpoint | B-N
e6c30564-7894-53de-84e1-27f305aa7aee | button | Insulation Resistance shall not be less than 1MΩ (Tested at 500VDC, 1000VDC) | >500MΩ,>1000MΩ,N/A
53ed9870-e3ff-5a45-9d16-70ec0141be7e | textbox | Actual Reading if <500MΩ/<1000MΩ
55c6628d-118f-484b-8659-a501d45e9040 | checkpoint | R-E
b0dfed67-2b0a-5d94-afbf-b0695936573b | button | Insulation Resistance shall not be less than 1MΩ (Tested at 500VDC, 1000VDC) | >500MΩ,>1000MΩ,N/A
1dd8bfc4-1c23-5ce6-8bd8-e776a7524c53 | textbox | Actual Reading if <500MΩ/<1000MΩ
b868133f-b4b3-4beb-a629-a4b3ae5e6ccf | checkpoint | W-E
8f12b33d-2867-5720-809f-451dd09a8a35 | button | Insulation Resistance shall not be less than 1MΩ (Tested at 500VDC, 1000VDC) | >500MΩ,>1000MΩ,N/A
11d0aeb0-8c74-5805-8a27-3c9ffc096d80 | textbox | Actual Reading if <500MΩ/<1000MΩ
2f1e5474-67ca-4290-a4c0-d0c00ab0fa5f | checkpoint | B-E
91374eda-c96c-52e7-8d39-0ea32572ab8c | button | Insulation Resistance shall not be less than 1MΩ (Tested at 500VDC, 1000VDC) | >500MΩ,>1000MΩ,N/A
14a493d0-eeb2-5290-9728-f1b86a8b0eba | textbox | Actual Reading if <500MΩ/<1000MΩ
c9a0cae2-b286-4106-845c-1cc0f3a2c670 | checkpoint | N-E
5c0881ea-f11e-5a26-9ea2-899b372ad1a0 | button | Insulation Resistance shall not be less than 1MΩ (Tested at 500VDC, 1000VDC) | >500MΩ,>1000MΩ,N/A
9ec664f6-3127-5687-85f9-817771475f51 | textbox | Actual Reading if <500MΩ/<1000MΩ
475fb419-ba6d-4392-acf5-3dc809c6e54a | signoff | Checked By (Heyday):
adf41567-33c7-4edd-a2e3-b2eb8e5ca8a8 | checklist | Testing & Commissioning - Low Voltage Cables - Mains/Submains (Energised) |  | Low Voltage Cables - Mains/Submains (Energised)
2b0dd3a0-2840-4fd7-838c-e64206f9de3f | section | Phase Rotation
a6e4ad7e-ec83-4416-8528-d65f1ab998b5 | checkpoint | Direction
28ea72d6-4a91-5a15-94c5-2854db45b57b | button | Direction | Clockwise,Anti-Clockwise
c26a325e-78ba-45d6-91e6-5860806890c3 | signoff | Checked By (Heyday):
e88e7031-561f-46cd-bbb9-0199c3ac78cb | section | Voltage
86f8e276-da9e-4b97-ba69-9d5b6f4dd122 | checkpoint | Red - White
93653f00-3b32-5550-844e-7b7cf8710501 | textbox | Voltage (V)
6ed9be45-6b56-4b49-87da-ea502410a2e4 | checkpoint | Red - Blue
b368877c-44f2-56ed-8d65-302019e35b3e | textbox | Voltage (V)
db14faf0-0b83-49f8-b05e-3ed90cd33602 | checkpoint | White - Blue
71305fd4-cd21-5a08-90d9-04d103c384bf | textbox | Voltage (V)
b2cb4bf8-69b4-4225-a2f7-6c2d237fc507 | checkpoint | Red - Neutral
50f8d9fd-9169-58b7-8c5c-2ad5568d5af6 | textbox | Voltage (V)
0eb3a0b2-9ab2-43bb-98b4-86a8a5174f99 | checkpoint | White - Neutral
15d9f414-9e57-5b37-8804-20266311e4d0 | textbox | Voltage (V)
b70d7c3e-3add-4007-ad5d-b1ca733190b5 | checkpoint | Blue - Neutral
69e62051-5aa3-5258-8375-5880247be8a5 | textbox | Voltage (V)
8d2bbccf-f4e9-4131-99ab-030da4b330d2 | checkpoint | Red - Earth
85db411d-c77e-5ae5-9482-8871a3b373c5 | textbox | Voltage (V)
0725d234-197f-4880-b767-b9be6da1b33c | checkpoint | White - Earth
58452f28-615b-5268-8df2-6aa3d6bad2f7 | textbox | Voltage (V)
1cfb0202-de30-4657-b8ff-6952e850a957 | checkpoint | Blue - Earth
45e1a898-8aef-5fe6-a258-43e9f2f26db6 | textbox | Voltage (V)
8982ac97-a732-4e66-a639-4970c71168cf | signoff | Checked By (Heyday):
f5b959a8-9496-4502-9f36-3c5ce66f64bc | checklist | Testing & Commissioning - Low Voltage Cables - Mains/Submains (Pre-Energisation) |  | Low Voltage Cables - Mains/Submains (Pre-Energisation)
018edeaf-369d-4f29-b1bf-c91bde4328eb | section | Pre-requisite Works
23f86157-f72b-4ffa-a768-98665b79837f | checkpoint | Insulation Damage
57bacc0d-557a-45ca-93e7-ece22f64ffd4 | checkpoint | Correct Type of Termination
9684c7b9-19a0-48c9-b01a-cccbab0659ff | checkpoint | Correct Cable Size and Labelling
57d6eede-c12c-4a00-be4c-750031f4f70e | section | Insulation Resistance
0cf19de5-79a4-4ab0-8d41-dc57fd701299 | checkpoint | R-W
9a8a942c-c760-54ab-8156-7f923929fb81 | button | Insulation Resistance shall not be less than 1MΩ (Tested at 500VDC/1000VDC) | >500MΩ,>1000MΩ,N/A
ce678e18-59f2-501b-974a-b76616a2e263 | textbox | Actual Reading if <500MΩ/<1000MΩ
d4ef7fc9-293d-4bb1-a821-0d89ceace40b | checkpoint | R-B
1c60b3a6-1e7b-5679-9483-48e4dd4f3da1 | button | Insulation Resistance shall not be less than 1MΩ (Tested at 500VDC/1000VDC) | >500MΩ,>1000MΩ,N/A
dd511f61-20d5-518f-81f4-fc71cc02430e | textbox | Actual Reading if <500MΩ/<1000MΩ
88eebd9e-2491-41ab-8bc2-7495c59d63f0 | checkpoint | W-B
00092a90-1d66-57c2-9ac1-af0166a8fdba | button | Insulation Resistance shall not be less than 1MΩ (Tested at 500VDC/1000VDC) | >500MΩ,>1000MΩ,N/A
ccd93f11-247b-50bb-8940-faffeea99973 | textbox | Actual Reading if <500MΩ/<1000MΩ
0dbda30a-d146-4689-8032-1a754f027c24 | checkpoint | R-N
c2567637-4493-5346-b1b1-6608d53e6dbe | button | Insulation Resistance shall not be less than 1MΩ (Tested at 500VDC/1000VDC) | >500MΩ,>1000MΩ,N/A
f42ca530-cdd3-5eec-9abc-41f8a9593ad3 | textbox | Actual Reading if <500MΩ/<1000MΩ
30776b3e-d58f-4dc9-bb62-41c38d10f98d | checkpoint | W-N
9e43d7f4-0af4-5ba6-96d7-5ca6707f7408 | button | Insulation Resistance shall not be less than 1MΩ (Tested at 500VDC/1000VDC) | >500MΩ,>1000MΩ,N/A
d3ac676d-4354-5beb-9005-912a85b0d966 | textbox | Actual Reading if <500MΩ/<1000MΩ
2970f94b-cb79-43a9-9ea1-b18274f0ac88 | checkpoint | B-N
591d006c-3ed7-56f8-8464-c575b772c723 | button | Insulation Resistance shall not be less than 1MΩ (Tested at 500VDC/1000VDC) | >500MΩ,>1000MΩ,N/A
4cc71dfc-b209-54b8-bc83-e89b7f48d10d | textbox | Actual Reading if <500MΩ/<1000MΩ
3d6923be-a1f5-449f-a6e0-8f4ed98390f2 | checkpoint | R-E
c2fab04d-bf8f-581c-b555-5ed80cce206e | button | Insulation Resistance shall not be less than 1MΩ (Tested at 500VDC/1000VDC) | >500MΩ,>1000MΩ,N/A
55cce7c7-7810-582e-8a6b-369795d3b0c6 | textbox | Actual Reading if <500MΩ/<1000MΩ
c9c38127-6fdd-48a2-9520-4253554c02e0 | checkpoint | W-E
06e4a05b-ae5f-5741-8393-5b16751588c6 | button | Insulation Resistance shall not be less than 1MΩ (Tested at 500VDC/1000VDC) | >500MΩ,>1000MΩ,N/A
2282f52b-da13-536e-ac5b-4cba786a817b | textbox | Actual Reading if <500MΩ/<1000MΩ
256e178d-ee3e-4d6a-b835-ea77f714c7d4 | checkpoint | B-E
4e9f2bd5-abdc-5f0e-87ca-b8c4ecf750c6 | button | Insulation Resistance shall not be less than 1MΩ (Tested at 500VDC/1000VDC) | >500MΩ,>1000MΩ,N/A
75306665-e77b-5cf6-8ce6-a29309f9b014 | textbox | Actual Reading if <500MΩ/<1000MΩ
90b33d64-3d90-45ba-8441-9a370fc4ba0d | checkpoint | N-E
7d47d5a8-e5e5-54b1-bf15-f8deabff2b62 | button | Insulation Resistance shall not be less than 1MΩ (Tested at 500VDC/1000VDC) | >500MΩ,>1000MΩ,N/A
71eef9c5-5789-5d90-89ea-0b68c00ea9b5 | textbox | Actual Reading if <500MΩ/<1000MΩ
52006caf-6350-4285-8d32-6a0561fdbfed | section | Continuity Testing
904dd9ec-4232-4529-a23d-9924bf54ff18 | checkpoint | Red Phase
cf4db43d-bd8a-5d5d-8efe-a99fe73bd4d0 | textbox | Resistance (Ω)
bbc273bf-6757-59b2-b065-7b79be06a427 | textbox | Target Resistance (Ω)
8a010c34-ad3f-44f6-b612-187c1b52df72 | checkpoint | White Phase
c53816fc-336b-5f0c-82dc-5a69b57952ab | textbox | Resistance (Ω)
96675194-8fbd-56aa-93d5-0408c0aa5faf | textbox | Target Resistance (Ω)
b3d56b96-05a0-4893-95d7-00bf5811b4fe | checkpoint | Blue Phase
c1062c2d-c386-55f0-99cd-12016163d1ee | textbox | Resistance (Ω)
88f65101-39fd-5748-b7cf-2b25ec17919b | textbox | Target Resistance (Ω)
b5e9a7d4-309f-452f-b5fb-5b1bdeb93dae | checkpoint | Neutral
736f3782-a7c4-588c-acd2-268a4a03e69f | textbox | Resistance (Ω)
615464c5-2962-5723-9c3e-de0d1a961057 | textbox | Target Resistance (Ω)
fbe6cce2-e362-42d8-ac3c-ed5f1e81b0a9 | checkpoint | Earth
2ee539aa-933f-56c0-9220-1db1e740fc7b | textbox | Resistance (Ω)
17f9b7f0-2c20-5abe-a210-21c0556a83fd | textbox | Target Resistance (Ω)
0963f175-9fe2-4d9e-a431-045b23711916 | signoff | Checked By (Heyday):
3e42762d-bf31-4d36-829b-e5be308b1a59 | checklist | Testing & Commissioning - Main Switchboards (Energised) |  | Main Switchboards (Energised)
f9aa158d-c33c-45ef-8941-ff151efe3e40 | section | Phase Voltage Reading
f96731dc-15c4-4ade-b71a-c95e9777c215 | checkpoint | Red - White
f4a3c1c8-4e6c-58fe-92a1-38c60f07d84d | textbox | Voltage (V)
46972991-0c7b-473b-9eaf-8a516c8c437a | checkpoint | Red - Blue
9012a56a-eb3f-549c-a99e-4ab59a18706f | textbox | Voltage (V)
eb36847c-ed6d-4567-9d58-f3b164fd3df1 | checkpoint | White - Blue
7730bb55-8399-5410-a6d8-9e321f2c3b55 | textbox | Voltage (V)
a1f0e0e5-888d-439a-b021-188f1611623e | checkpoint | Red - Neutral
1b9de252-2bcb-50f7-a8a4-21296a1917d1 | textbox | Voltage (V)
5982f28f-419b-436a-a8c8-e8c3a795f156 | checkpoint | White - Neutral
fd5ad721-6b4d-581b-98cd-16572b17c288 | textbox | Voltage (V)
c968da2a-b6d4-4aef-b161-053f68e23df1 | checkpoint | Blue - Neutral
5e1fa804-47a1-5108-b5c5-98b30ca5c998 | textbox | Voltage (V)
3be6019e-bce6-494d-9680-40f2b59f2946 | checkpoint | Red - Earth
27a4ef16-3301-50ce-998e-8dc1a2448f00 | textbox | Voltage (V)
264f3f81-f0b1-451c-98da-05ef1aedaaff | checkpoint | White - Earth
1dee7dae-4540-58c6-980a-81266bf5e66f | textbox | Voltage (V)
eb645a35-eaac-4c73-a941-28e7662351d0 | checkpoint | Blue - Earth
fef4a341-e45a-5d94-b3d8-5d6cc06e2ce8 | textbox | Voltage (V)
03d24af3-4139-436a-b530-ee2eb31b26b6 | section | Phase Rotation
0983e440-0629-44a5-acde-f06ac1b4807b | checkpoint-no-value | Direction
53223924-832f-5e8b-9414-bec236d33ab5 | button | Direction: | Clockwise,Anti-Clockwise
06501d42-3386-43fb-b9da-0d8237b6d947 | signoff | Checked By (Heyday):
50866f89-092f-4410-b11b-5e2c0f371df3 | checklist | Testing & Commissioning - Main Switchboards (Pre-Energisation) |  | Main Switchboards (Pre-Energisation)
8fae24b8-93ff-44e4-9f3e-3d4d4fd11b95 | section | Physical Checks
e709c7be-8e7d-4169-9abe-3cb7607e04ab | checkpoint | 1. Confirm boards dimensions are in accordance with approved shop drawings (provide drawings reference in the Comments section)
f12a6ef1-c025-4c3f-8e3c-aabbcbac8a65 | checkpoint | 2. Confirm correct MSB Form of Separation, Provide actual Form of Separation in Comments section
4bacf871-43d7-44b1-9ca7-931eb3d5c73e | checkpoint | 3. Confirm the Layout of fitted components (ACBs, MCCBs, MEN, ATS) is in accordance with approved shop drawings (provide drawings reference in the Comments section)
5acd8e26-1e16-488f-bf1f-2688b05a237b | checkpoint | 4. Confirm that Brand of fitted components is in accordance with approved shop drawings (provide drawings reference in the Comments section)
c3e92977-4409-4e3c-b8a0-114bf210be9f | checkpoint | 5. Confirm meters location, types and labels are in accordance with approved shop drawings
134840f7-5341-470d-a375-90551e836a99 | checkpoint | 6. Confirm the circuit breakers rating is in accordance with discrimination study (provide discrimination study reference in the Comments section)
0763de31-405b-4e72-857d-2ced3f82e9c9 | checkpoint | 7. Confirm Trip units and protection relay settings are set in accordance with discrimination study
109d65e8-a0df-42f4-8a18-a6457d59aadf | checkpoint | 8. Confirm correct circuit identification and labelling
f10e2dcb-9875-47f0-b4d8-958e1fd394ee | checkpoint | 9. Confirm easy access to controls termination
9a611db2-39d4-4660-b50b-1fcb1452706a | checkpoint | 10. Confirm correct location, access and sufficient support for incoming cables
8083287d-4ea4-4e47-8888-070a7be1c4f8 | checkpoint | 11. Confirm correct location, access and sufficient support for outgoing cables
dd201025-c906-4ded-af65-32c021351bff | checkpoint | 12. Confirm the board busbars and cables are tighten as per manufacturer recommendations and standards. Provide applied torque in a Comment section
a596d58c-b005-485b-9c07-51013801b5a8 | checkpoint | 13. Confirm correct phase identification of busbars and cables inside the board
bc2f44c9-0e12-4027-9ac0-857eef3646d5 | checkpoint | 14. Confirm correct size of incoming power cables as per approved cable schedule
5db9f0ed-1af7-439a-be14-ef8d2771c4d1 | checkpoint | 15. Confirm correct size of earthing conductors
3039bea8-eb57-44dd-beda-50bce13c367b | checkpoint | 16. Confirm no visual damage to the equipment or meters. Mark the observed issues in a Comment section (if any)
1e94d923-98c2-4cf3-83f4-8e81fb3f9ed2 | section | Mechanical Checks
ed460c2b-4e25-45f6-a336-77a8cc25c8ae | checkpoint | 1. Repeat closing and opening of air circuit breakers for 3 times using the front panel operating buttons and charging handle
0e70d6de-0d05-46e6-a482-c5df4089c862 | checkpoint | 2. Repeat racking of air circuit breaker in and out of chassis for 2 times to verify correct functionality of sliding mechanism
33e985fc-0800-4089-ac92-b78eaf79d6fb | checkpoint | 3. Repeat closing and opening of air circuit breakers for 3 times using the front panel operating buttons and charging handle
7606501e-6b84-4d59-bf66-647360d4245e | checkpoint | 4. Repeat manual closing and opening of moulded case circuit breakers for 3 times
8365c25d-b9eb-4b26-a107-e3ec28f0ca3f | checkpoint | 5. Repeat manual closing and opening of miniature circuit breakers for 3 times
cfa73a8c-32bd-498f-92f4-6645a8c83db8 | checkpoint | 6. Repeat mounting and dismounting of control fuses 1 time
1bbac3cf-816d-429e-8593-6f95117b09fa | checkpoint | 7. Repeat mounting and dismounting of control fuses 1 time
4df04b50-8603-4e17-a06d-09346cb9d6c6 | checkpoint | 8. Verify integrity of mechanical interlocking system between ASBs (MCCBs) by closing Source 1 Breaker and confirm that Source 2 Breaker is mechanically interlocked
ba24e470-4526-445c-8da5-7f158e4f0fa9 | checkpoint | 9. Verify integrity of mechanical interlocking system between ASBs (MCCBs) by closing Source 2 Breaker and confirm that Source 1 Breaker is mechanically interlocked
a9a85573-39a3-48ad-acb5-79c2bccd745e | checkpoint | 10. Conduct the torque test for all bolted connections and confirm the torque is in accordance with manufacturer recommendations and standards
722dc086-3965-41eb-8544-d40f6e036103 | section | Switch Gear Busbar - Preliminary Checks
7f37c3cd-7b41-49b4-8dd7-d0952e802c69 | checkpoint | 1. Confirm all fuses Removed in board’s Control Sections
420447a3-a867-4e5e-b379-dad0ffae8c6d | checkpoint | 2. Confirm Main Incomers ACBs/MCCBs are Closed
0cad5f1a-3ffc-4c5c-b91f-9a473d0f7771 | checkpoint | 3. Confirm Bus-coupler is Closed (if exist)
216adc9a-95a4-48a8-822a-97fe489b05c1 | checkpoint | 4. Confirm Outgoing Feeders is Closed
31e36a40-14f8-4cbe-9a16-a63c06e2e646 | checkpoint | 5. Confirm Main Panel Neutral to Earth Link(s) was Removed
3521c02c-fa2e-4164-9e0a-e2a75858c4bd | checkpoint | 6. Confirm Neutral link on Transient Voltage Surge Suppressor is Opened
f4d3a76f-555b-4d08-b1d6-4d5b74b52e15 | checkpoint | 7. Confirm All Long Time rating Plugs From ACB's are Removed (if applicable)
b93d32c8-fa8d-49b1-9124-61c88bd8b5a1 | section | Switch Gear Busbar - Insulation Resistance (1000V)
fce186ff-8fe9-420b-baa6-25a24b2687eb | checkpoint | 1. Between L1 Phase and Neutral
5d0fa9d4-3057-5f7b-95f7-ee58f147495d | button | >10MΩ | YES,NO
80a0e736-fd6c-580a-9dfe-e4566efffaa5 | textbox | Actual Reading if <10MΩ
f51eb97c-857c-41ad-8a95-47625b23dfba | checkpoint | 2. Between L2 Phase and Neutral
67010062-53c3-58b0-aaf0-1fce18f8b9f5 | button | >10MΩ | YES,NO
ce4e99d7-d9b1-56ef-8de3-f1adc0c6dea7 | textbox | Actual Reading if <10MΩ
90fd0fcf-c627-4718-8cc7-77d1c29a1fed | checkpoint | 3. Between L3 Phase and Neutral
4411ae80-a470-52a3-8e98-2e78a4fd4846 | button | >10MΩ | YES,NO
bd565b3f-87dd-59b9-8dbb-46149c449d56 | textbox | Actual Reading if <10MΩ
13d3855a-a1b4-46e7-8ccc-b27564e8a236 | checkpoint | 4. Between Neutral and Earth
91779843-aadc-5e9e-8df5-c8484ba1da16 | button | >10MΩ | YES,NO
0d181df8-1b98-5f4c-ba7b-187a701c47b8 | textbox | Actual Reading if <10MΩ
f95ee146-bbb8-4e2f-a4df-c8e5d3f26450 | checkpoint | 5. Between L1 Phase and Earth
4c632dfa-483b-5787-adb5-28360c6c913f | button | >10MΩ | YES,NO
39b1bc1e-1c12-50dd-8316-88afe5fca0cf | textbox | Actual Reading if <10MΩ
d30595f0-a3f8-4402-b31c-336b98e222bb | checkpoint | 6. Between L2 Phase and Earth
46836438-d796-5460-aa13-7cae26b1fd97 | button | >10MΩ | YES,NO
9e6f285d-66fd-56cf-b709-4c5083cc1e73 | textbox | Actual Reading if <10MΩ
fe251e3b-f2e0-47da-a196-2c7bede637f4 | checkpoint | 7. Between L3 Phase and Earth
6120150e-b479-5ebb-b823-3d0597e4012d | button | >10MΩ | YES,NO
371fa103-6b1b-5a1d-a8ff-22b0a9a90fe0 | textbox | Actual Reading if <10MΩ
6b83d718-c6ab-4eae-9a93-cbf60e348f7f | checkpoint | 8. Between L1 Phase and L2 Phase
6c31f4b8-d3b5-5a40-aec8-1cace3e40112 | button | >10MΩ | YES,NO
e6e64b91-a4fa-503d-a906-c38b723cab43 | textbox | Actual Reading if <10MΩ
322c5bc1-a6a4-468a-90e9-2fbb787585a4 | checkpoint | 9. Between L1 Phase and L3 Phase
acae8a88-5a0b-5a84-932f-bd9473732356 | button | >10MΩ | YES,NO
c3ac8128-d9c4-5287-a16f-68a7a4233fc7 | textbox | Actual Reading if <10MΩ
5467d427-0bfe-4a76-93c0-dafb6762aab2 | checkpoint | 10. Between L2 Phase and L3 Phase
c32f53a4-5b47-5025-8e58-dd468a5b1ae8 | button | >10MΩ | YES,NO
c60a138e-3cbd-5d99-a5d7-e1830a41f33d | textbox | Actual Reading if <10MΩ
1101a10d-756f-4e13-8fda-4961a22ab017 | section | Current Transformer Checks
6e28df17-fe33-4990-b850-65e3962369b9 | checkpoint | Current Transformer Checks
2ca59f02-67a2-5beb-b332-0c51245ac3ca | textbox | CT ID | YES,NO
a0a82070-b7f4-5def-a4e8-ed1406108b82 | button | CT Polarity is Correct | YES,NO
a6f07223-c23c-528e-8fc1-033de1f54bd3 | button | No crossed phase CT connections | YES,NO
ef0bddc3-f045-565f-8180-9f59cbbe3652 | button | No phase sequence CT connection errors | YES,NO
63bf9fa9-ae18-4cdd-93aa-59a4170eb7de | signoff | Checked By (Heyday):
62d202b1-8c66-4e1e-8901-ccb27238b552 | checklist | Testing & Commissioning - PFC |  | PFC
1944b174-f008-4363-8bdf-1c008fa2b047 | checkpoint | WSA20-MPX-04000-EL-ITC-31102000 - Construction Tests (Pre-energisation)
f68e9d2d-b76e-4654-afa5-0ea82486de02 | checkpoint | WSA20-MPX-04000-EL-ITC-31073000 - Component Test (Energised)
9b9b1768-ae07-4672-ae74-d1727c05c53a | checkpoint | CT Ratio Verification (V,A,kVA) L1/L2/L3 - Component Test (Energised)
c057c646-daba-4f37-a524-666f830967de | checkpoint | Power Factor Correction Controller Configuration as per manufacturers recommendations - Component Test (Energised)
7b4885d9-2b6b-4d72-93c7-cb464dd5b560 | signoff | Checked By (Heyday):
55687e49-7ac5-41c7-95bb-08c0e7c58654 | checklist | Testing & Commissioning - PMCS |  | PMCS
6d39116f-93ac-4c31-b733-b41891044e4a | section | WSA20-MPX-04000-EL-ITC-31183000 - Component Tests (Pre-commissioning)
0f3e7711-e0b9-4442-9cde-9544fac38446 | checkpoint | Schneider Point to Point Validation ITP - RIOM
363f12e9-42ca-4ebd-9f72-465cb421c246 | checkpoint | Schneider Point to Point Validation ITP - PAC
909ed226-bacd-4172-948f-6bb3a9774ffe | checkpoint | Schneider Point to Point Validation ITP - EPS
4170b671-0120-496a-950c-fc6c643c72a1 | checkpoint | Schneider Point to Point Validation ITP - PFC
4bce19cd-c9e5-44b5-8633-e57edd635592 | checkpoint | Schneider Point to Point Validation ITP - UPS
512c4451-1ea2-4d4c-92e5-aa9bedb5a86f | checkpoint | Schneider Point to Point Validation ITP - EV
fb8cc9f5-9762-4676-8db2-7fb9a4072ff9 | checkpoint | Schneider Point to Point Validation ITP - IEM
fef1adbb-cd17-4792-83f6-ddad180e93d7 | checkpoint | Schneider Point to Point Validation ITP - eGSE
e0760722-56ae-4c39-9758-f4ad831a7800 | checkpoint | Schneider Point to Point Validation ITP - GEN
0d4a2136-bbf3-4120-9af8-aa4ee417b934 | checkpoint | Schneider Point to Point Validation ITP - LCS
f2e4baf3-db16-42c1-856b-c5d1ea2af0dc | checkpoint | Schneider Point to Point Validation ITP - EML
32ac393c-b449-49c8-8c01-4537449c011d | checkpoint | Schneider Point to Point Validation ITP - PV
2aaa59e8-f9a9-40e8-95e6-eb37298f6b25 | signoff | Checked By (Heyday):
ff22da6d-3cf0-4ac7-84a6-1401d58129f9 | section | WSA20-MPX-04000-EL-ITC-31184000 - System Acceptance Tests (Commissioning)
42e63be9-0b4d-45fa-a96c-67f05aaa6664 | checkpoint | Schneider WSA LV PMCS Cx ITP - RIOM
b1cacbf7-ed0f-4b96-9a82-abceea0421a7 | checkpoint | Schneider WSA LV PMCS Cx ITP - PAC
8c03faf9-2e4c-4ef7-9741-bad9b0bbc42d | checkpoint | Schneider WSA LV PMCS Cx ITP - EPS
d1aca762-82b0-4fa7-9cd5-d65258b3be37 | checkpoint | Schneider WSA LV PMCS Cx ITP - PFC
d5f5901f-5e6f-4899-b397-55aa27f163eb | checkpoint | Schneider WSA LV PMCS Cx ITP - UPS
c0daf05b-b0eb-4b4e-8f71-b97e9dc4a6e4 | checkpoint | Schneider WSA LV PMCS Cx ITP - EV
8ace8b4e-3b9a-43be-9525-4151be7b76cc | checkpoint | Schneider WSA LV PMCS Cx ITP - IEM
559e5a9a-153d-4f70-9936-accb5ef23056 | checkpoint | Schneider WSA LV PMCS Cx ITP - eGSE
e76c6a77-eb82-4ce1-b0ab-43b760b35fd1 | checkpoint | Schneider WSA LV PMCS Cx ITP - GEN
d50a52b4-a611-4608-996c-f6ed4059e72b | checkpoint | Schneider WSA LV PMCS Cx ITP - LCS
04659ead-350e-4522-adac-90c797c5c308 | checkpoint | Schneider WSA LV PMCS Cx ITP - EML
f983179a-9ad1-4eb9-a581-a3b64af3d443 | checkpoint | Schneider WSA LV PMCS Cx ITP - PV
5575884b-b5f1-4f3a-bcf7-d8139b45eee7 | signoff | Checked By (Heyday):
54731133-f18a-4d97-95e6-64aee3d66a70 | checklist | Testing & Commissioning - PMCS - (Energised) |  | PMCS - Energised
b70035bd-c922-47e0-9f91-0f5759ee6df6 | section | WSA20-MPX-04000-EL-ITC-31184000 - System Acceptance Tests
7ccf45df-e107-415e-9a6d-9245237e61b7 | checkpoint | Schneider WSA LV PMCS Cx ITP - RIOM
35fe0e6a-d70a-45f6-b5a0-9076eb4e528f | checkpoint | Schneider WSA LV PMCS Cx ITP - PAC
e0f9faba-82f3-4bde-aeea-b94722c0dd90 | checkpoint | Schneider WSA LV PMCS Cx ITP - EPS
b4961f39-3aa9-4694-9dc6-de81d5c81979 | checkpoint | Schneider WSA LV PMCS Cx ITP - PFC
86227350-4ca3-4fa3-b4b7-31f467675a19 | checkpoint | Schneider WSA LV PMCS Cx ITP - UPS
afe2194c-92fd-4db9-b886-e7adbef9c63c | checkpoint | Schneider WSA LV PMCS Cx ITP - EV
aa8f5b05-c914-45f0-85ac-f98ad2a0887a | checkpoint | Schneider WSA LV PMCS Cx ITP - IEM
8ad6dd46-99e8-4ea3-86e9-acb9990841c3 | checkpoint | Schneider WSA LV PMCS Cx ITP - eGSE
d330c9ca-c23a-4890-8100-15367f9d3983 | checkpoint | Schneider WSA LV PMCS Cx ITP - GEN
e8108dda-ac8d-427e-ac1a-b770391d63df | checkpoint | Schneider WSA LV PMCS Cx ITP - LCS
68acecc8-1749-4a90-a9db-d88123034461 | checkpoint | Schneider WSA LV PMCS Cx ITP - EML
13681449-c97e-47ca-83d4-503418a2b151 | checkpoint | Schneider WSA LV PMCS Cx ITP - PV
eba7d451-5aae-4829-a17e-b3335210cf9c | signoff | Checked By (Heyday):
6c383b39-f825-4304-9fd9-14040470c7da | checklist | Testing & Commissioning - PMCS - (Pre-Energisation) |  | PMCS - (Pre-Energisation)
80cb1efa-9413-4588-bbd4-416d894354f7 | section | WSA20-MPX-04000-EL-ITC-31183000 - Component Tests
0bc2971f-c935-4b69-be54-5aed9a755752 | checkpoint | Schneider Point to Point Validation ITP - RIOM
64746830-809f-4404-a799-04603a3e90e9 | checkpoint | Schneider Point to Point Validation ITP - PAC
3711391c-514f-4938-9967-a2538ffa1220 | checkpoint | Schneider Point to Point Validation ITP - EPS
007fcd38-df52-4f21-b06c-149e50cb0e72 | checkpoint | Schneider Point to Point Validation ITP - PFC
f61dbfe3-d3f0-4a24-bfd3-13f971c6385d | checkpoint | Schneider Point to Point Validation ITP - UPS
8a8b9076-eb21-4099-9cc0-ec74a028bc5f | checkpoint | Schneider Point to Point Validation ITP - EV
ca18920f-89c7-4222-8b3a-f7735b3a43bf | checkpoint | Schneider Point to Point Validation ITP - IEM
691ce5d3-7b5e-40f8-9a3e-b54ef81e8ac9 | checkpoint | Schneider Point to Point Validation ITP - eGSE
f03a126f-5637-4d04-af33-7b8030637f22 | checkpoint | Schneider Point to Point Validation ITP - GEN
aad1bf93-4560-481f-9bb8-940ce1c9a995 | checkpoint | Schneider Point to Point Validation ITP - LCS
75178553-dde5-47ef-9dbb-d4d130d134b8 | checkpoint | Schneider Point to Point Validation ITP - EML
c0da70a4-fe4c-4380-a6f9-7184ad3bf353 | checkpoint | Schneider Point to Point Validation ITP - PV
ac3afc66-f236-4331-9cfd-25ccb6c4835a | signoff | Checked By (Heyday):
10d56c3d-cdad-465f-b948-220f28af9777 | checklist | Testing & Commissioning - Single Phase Subcircuit |  | Single Phase Subcircuit
99fcf775-d9d9-45aa-bc40-72ea8e95beac | section | Pre-requisite Works
b6245e80-1e48-4375-9cfc-b3295cba6b21 | checkpoint | Insulation Damage
c960e5b7-636f-44eb-8b9e-1acc1f6c3372 | checkpoint | Correct Type of Termination
830d7519-7adc-4fe4-990f-97619c9fa743 | checkpoint | Correct Colour Code
6623d9a4-6615-4c48-a1c0-4c32931da7b4 | checkpoint | Correct Outlet Rating and Size
6af80b46-6884-4add-b7f2-b4eb130de2b9 | checkpoint | Earth Continuity
060aa90b-811f-5ad5-a5da-76c27b44531f | textbox | Resistance (Ω)
7eec440f-bc3f-455d-bf19-55fc824a350a | checkpoint | Polarity Check
440b6016-299e-5394-867f-385fa07202af | button | No Transposition | YES,NO
053b0de7-0eb6-5547-9d2d-46e1f3bf95e9 | button | Switch in Active | YES,NO
f4a80d27-97cd-4a26-b498-168f68df6e9a | section | Insulation Resistance
8ba76168-4007-4b84-a280-12de7c138cd0 | checkpoint | R-N
537274d1-6646-5c85-9b27-ebf56328087c | button | Insulation Resistance shall not be less than 1MΩ (Tested at 250VDC/500VDC) | >200MΩ,>500MΩ,N/A
6dafc51c-6de6-5824-870b-a7a7a90a7265 | textbox | Actual Reading if <200MΩ/<500MΩ
db4bc454-6f5c-491f-a3a3-dfaca4127ad2 | checkpoint | R-E
8982dd66-b9fb-5b80-853e-77054ede7db5 | button | Insulation Resistance shall not be less than 1MΩ (Tested at 250VDC/500VDC) | >200MΩ,>500MΩ,N/A
ae800fe7-c015-5255-b809-77f63aec3189 | textbox | Actual Reading if <200MΩ/<500MΩ
40c2ab33-5545-4ccd-9b21-54406f15e189 | checkpoint | N-E
b6de9cfe-c2d0-5ae3-97a9-4ecc322b1504 | button | Insulation Resistance shall not be less than 1MΩ (Tested at 250VDC/500VDC) | >200MΩ,>500MΩ,N/A
7eaa26a2-e6bf-5dbe-bc66-803628eeb184 | textbox | Actual Reading if <200MΩ/<500MΩ
28c42bf5-375b-4323-800e-8f7333eb5598 | section | Voltage
c4eb594f-a5e8-4bda-ad37-025dc2ed4b10 | checkpoint | Red - Neutral
40d5203f-80a5-5632-8e29-135176de772d | textbox | Voltage (V)
23234cdd-c1ec-4a2d-a172-b8a9451f300a | checkpoint | Red - Earth
fb73a258-9d7e-5f99-b38f-64a76c6df601 | textbox | Voltage (V)
b0eba347-4d78-4768-a547-43d5a8d27339 | section | Earth Fault Loop Impedance Test / RCD-RCBO Tripping Test
9af5b6e3-ad80-4327-acd6-fd1c0042d1b4 | checkpoint | Impedance - (N/A if the circuit is RCD Protected)
ca658463-6c9b-535c-9f84-e77a01da0d98 | textbox | Record Inpedance (Ω)
35a29d49-1248-5728-ad7c-5f968884a5b1 | textbox | Target Impedance (Ω)
4429efd3-4f70-4c1d-b68e-8e99ef5835f9 | checkpoint | RCD/RCBO Tripping Test
e3ba2339-b613-58ff-83a6-2095d2667dcd | textbox | Trip Current (mA)
e0ca11a2-eb7e-51dd-ad53-5839c860a2f7 | textbox | Trip Time (ms)
858b7cb6-6ac1-489a-b2ee-fa203eaa4510 | signoff | Checked By (Heyday):
eb8a49ae-7f4d-4e38-9f02-6cdfbf19ebe8 | checklist | Testing & Commissioning - Solar Photovoltaic System (Energised) |  | Solar Photovoltaic System (Energised)
c81c44e5-267c-40b2-a310-23bc182cb8ef | checkpoint | SCS Commissioning Checklist Section 5 (System Measurements – AC Measurements)
a426b55b-f3e5-4f30-8dd8-13ee8bc08ab1 | signoff | Checked By (Heyday):
2e96ad2c-caef-477a-9068-962baf335263 | checklist | Testing & Commissioning - Solar Photovoltaic System (Pre-energisation) |  | Solar Photovoltaic System (Pre-energisation)
a03a5368-d0b8-481b-9289-debec47e63ce | checkpoint | SCS Commissioning Checklist Section 5 (System Measurements – Inverter)