## zres_siteapp_NEW
Id | Type | Name | Values | Prompting Name | Postfix | Resource Id
| checklist | Quality Mains and Sub Mains |  | Quality Mains and Sub Mains
56941fac-2db1-48ab-b940-3632c17ac0fb | section | Details
481c366a-fe5f-4bf9-b08e-3fe618e39573 | checkpoint | Receipt of cable containment delivery to site & storage. (ITP Reference Item 1)
c1f2e221-dde5-4dad-9b44-c6afb6999b40 | checkpoint | Cable storage & handling. (ITP Reference Item 2)
a952b6d5-c1b0-4efa-bc98-18fecdf45664 | checkpoint | Correct cable size & type. (ITP Reference Item 3)
2e077f6e-060a-4e49-a276-969004145f0b | signoff | Signoff Required from Heyday & Multiplex
dd8f2a5e-5bac-4622-9945-985f7020ddc9 | checkpoint | Cable pulling tension to not exceed manufacturer's recommendations. (ITP Reference Item 4)
7199c90a-99f7-4c2e-ad30-b8eb856528f1 | checkpoint | Cable lubrication if required. (ITP Reference Item 5)
cc57e662-d195-4557-b8fc-88991a964bdd | checkpoint | Installed to latest drawings – schematics/single line diagram & cable containment drawings. (ITP Reference Item 6)
3700b49e-c745-4dde-9bf2-634c32593cff | checkpoint | Correct cable tag installed. (ITP Reference Item 7)
89bedb52-fb10-432d-9c5e-92594ea32e40 | checkpoint | Photo evidence captured for cable containment install. (ITP Reference Item 8)
2007734c-08ee-4ea7-bd50-d84c77daae1f | signoff | Signoff Required from Heyday & Multiplex
| checklist | Substation Earthing Inspection |  | Substation Earthing Inspection
62a898b2-f6e0-4591-bc14-0522ba8a9ad1 | section | Details:
cc096a5a-a547-4918-8c51-0dae4ac1849d | checkpoint | Visual Inspection of Pit
2ccf85d8-44ed-5696-a9fe-27b45edd008a | note | Photo Required of Pit
cfa7a13d-7bee-4cbd-b8da-81dedcf3f58d | checkpoint | Earth Resistance from Pit Earth Rod to Earth Bar
67446d85-d979-5751-a367-9cbdd434a363 | note | Earth Resistance to be <0.5Ω
7d3aed57-4013-5bac-931e-5a7f90003aa0 | note | Photo of Multimeter with results from Earth Rod to Earth Bar
6a32d84d-266b-4ff3-9e8f-293b4d104a9f | signoff | Checked By (Heyday):
| checklist | Testing & Commissioning - UPS (Energised) |  | UPS (Energised)
f3e1cbad-b2ae-4e94-b407-8a4890326fde | section | Details
fdfaaa2d-ff73-42fa-a03d-542a79ed959a | checkpoint | Commissioning & Installation / Start-up Report - Unit pre start-up check – Page 7
e799e765-75f6-4b34-9a13-8ca4acee5b53 | checkpoint | Commissioning & Installation / Start-up Report - Unit Functional Check – Page 7
0a01ea4f-cb67-4be8-b374-02ed1def6419 | checkpoint | Commissioning & Installation / Start-up Report - Unit Final Inspection – Page 8
| checklist | Testing & Commissioning - UPS (Pre-Energistation) |  | UPS (Pre-Energistation)
0e4869ae-5b31-45c1-82bf-e47ce2268876 | section | Details
9fce7efb-00fa-4dbe-8da7-cb82428781d1 | checkpoint | Commissioning & Installation / Start-up Report - System Room Check – Page 6
76622146-1a89-4937-b3b6-b3b6251e014f | checkpoint | Commissioning & Installation / Start-up Report - System Check – Page 6.
| checklist | Testing & Commissioning - UPS (System Commissioning) |  | UPS (System Commissioning)
5b7606ba-d5ae-41fc-8376-13c2d4483875 | section | Details
57bc2b37-cbf2-41b6-be97-f08b875fd4cc | checkpoint | UPS – Functional Performance Test Report
66cfeccd-867d-5d84-b88f-b0e6be08bdd0 | note | The following tests are conducted (see Schneider Electric - Site Acceptance test protocol for results and trends):
248e2182-3c88-548a-9d16-83cbfe1cffe2 | note | ○ Load Transfer test
3165be1c-67e3-513d-ba2d-739729acf2db | note | ○ Inverter to bypass transition on NO LOAD
ba06c38d-84b0-57ab-bb2f-af01b1a45b9e | note | ○ Inverter to bypass transition on FULL LOAD
4ad73757-b2d1-5e11-93d0-de966663e293 | note | ○ Load step test (0%-50%-0%)
6abf185b-84cd-59af-a6a5-7d2db2ef381f | note | ○ Load step test (25%-75%-25%)
af8c85e8-d471-58c9-95fd-2b7d7aa46aa1 | note | ○ Load step test (50%-100%-50%)
8b7ebabc-e30a-5299-a59e-03185a8dd2c9 | note | ○ Load step test (75%-100%-75%)
1869e058-9c4b-5cda-9106-e67d703976e6 | note | ○ Load step test (0%-100%-0%)
cc904bb5-37bd-559e-8661-48790dccc0b4 | note | ○ THDi and THDv measurements (0%, 25%, 50%,75%, 100%)
10f48170-9c16-5cb5-b41d-534c75ee3fd1 | note | ○ Expected Results: Total Harmonic Distortion (THD) is to be under 5%
36eb3717-5cff-57d2-b2b6-e013a4b9f1ac | note | ○ UPS efficiency calculation (Unity PF@0%, 25%, 50%, 75%, 100%)
a6c23fcf-6893-5fce-a12b-7cb207ee50e1 | note | ○ UPS battery discharge test (15min EOL)
293955cf-2d1d-4d00-b4c9-a555503de06c | signoff | Checked By (Heyday):