## WWMH F20525
QMD07 INSPECTION & TEST PLAN
| Project Name: | Albert Crescent 3 Waters Renewal |  |  |  |  | ITP No: | 1
| Client | Invercargill City Council |  |  |  |  | Prepared By: | Jay Arthur
| Scope of Work | Installation WWMH F20525 |  |  |  |  | Date: | 2025-04-08
REFERENCE DOCUMENTS | [5 empty] | LEGEND
AS/NZS 3500 | [5 empty] | Test and Inspection Codes:
Project Drawings and Specification Document Section D | [5 empty] | H = Hold Point - Stop work until seen - Signed Record
NZS 3114 | [5 empty] | Work shall not proceed past the Hold Point until realeased by the organisation imposing the Hold Point
NZS 3109 | [5 empty] | I = In-process Inspection - Work continues - Signed Record
Formal inspection activity to be undertaken and recorded
W = Witness Inspection - Work Continues - Signature if Witness
An inspection point that may be witnessed by the organisation imposing the Witness Point
S = Activity subject to ongoing monitoring
APPROVAL/REVISION HISTORY | [5 empty] | Any activity that is subject to ongoing monitoring
Rev | Status | Approved By | Signature |  | Date | R = Records Review - Signed record per package
Review of text reports/records or other evidence of compliance
Responsible Inspectorate (RI) (may be modified to meet site specific requirements)
PM - Project Manager
REVIEWED BY | [5 empty] | FM - Foreman
Position |  | Name | Signature |  | Date Reviewed | CR - Council Representative
SUB - Subcontractor Representative
ITP COMPLETE
Position |  | Name | Signature |  | Date
Project Manager |  | Jay Arthur |  |  | 2025-04-08
ID : WWMH F20525
OP. No. | Operation To Be Inspected Or Tested |  | Controlled By : (Position) | Accept / Reject Criteria | Spec. Ref, Procedure Or Method Statement | Frequency Of Inspection OR Test | HOLD POINT | Puna Wai Civil | Client | Comments
1 | Manhole base Preparation (Pre-cast or in-situ) |  | CR | Clean and dry base - Correct bedding material and compaction - Reinforcement and formwork inspected - Waterproofing components in place | Project Drawings D18 Construction Methodology | Prior to placing concrete or setting precast base | I
2 | Manhole Cyclinder Installation |  | FM | - Correct alignment and verticality - Joints sealed with approved material - Steps/lifting holes sealed - Wall thickness and type verified | D18 – Precast Installations Manufacturer specs NZS 3109 | Prior to backfilling | H
3 | Pipe protrusions into manhole |  | FM | -Flexible joint within 1metre of the manhole | D18.3 INSTALLATION | Prior to pouring corbels | H
4 | Internal Benching and Channeling |  | PM | Smooth trowelled finish - Accurate channel fall to spec - Benching slope toward channel - No honeycombing or cracks | D18.3 - AS/NZS 3500 - Formed finish F3 as specified in NZS 3114 | After completion of benching/invert | H
5 | Manhole Cover and Frame Installation |  | PM | - Infiltration check - Visual condition check - Manhole dimensions - Functional access features | D15.2 MATERIALS Maestro DIMHMCFHS MH cover | Before handover or commissioning | H
6
QMD07

## WWMH F20538
QMD07 INSPECTION & TEST PLAN
| Project Name: | Albert Crescent 3 Waters Renewal |  |  |  |  | ITP No: | 2
| Client | Invercargill City Council |  |  |  |  | Prepared By: | Jay Arthur
| Scope of Work | Installation WWMH F20538 |  |  |  |  | Date: | 2025-04-08
REFERENCE DOCUMENTS | [5 empty] | LEGEND
AS/NZS 3500 | [5 empty] | Test and Inspection Codes:
Project Drawings and Specification Document Section D | [5 empty] | H = Hold Point - Stop work until seen - Signed Record
NZS 3114 | [5 empty] | Work shall not proceed past the Hold Point until realeased by the organisation imposing the Hold Point
NZS 3109 | [5 empty] | I = In-process Inspection - Work continues - Signed Record
Formal inspection activity to be undertaken and recorded
W = Witness Inspection - Work Continues - Signature if Witness
An inspection point that may be witnessed by the organisation imposing the Witness Point
S = Activity subject to ongoing monitoring
APPROVAL/REVISION HISTORY | [5 empty] | Any activity that is subject to ongoing monitoring
Rev | Status | Approved By | Signature |  | Date | R = Records Review - Signed record per package
Review of text reports/records or other evidence of compliance
Responsible Inspectorate (RI) (may be modified to meet site specific requirements)
PM - Project Manager
REVIEWED BY | [5 empty] | FM - Foreman
Position |  | Name | Signature |  | Date Reviewed | CR - Council Representative
SUB - Subcontractor Representative
ITP COMPLETE
Position |  | Name | Signature |  | Date
Project Manager |  | Jay Arthur |  |  | 2025-04-08
ID : WWMH F20538
OP. No. | Operation To Be Inspected Or Tested |  | Controlled By : (Position) | Accept / Reject Criteria | Spec. Ref, Procedure Or Method Statement | Frequency Of Inspection OR Test | HOLD POINT | Puna Wai Civil | Client | Comments
1 | Manhole base Preparation (Pre-cast or in-situ) |  | CR | Clean and dry base - Correct bedding material and compaction - Reinforcement and formwork inspected - Waterproofing components in place | Project Drawings D18 Construction Methodology | Prior to placing concrete or setting precast base | I
2 | Manhole Cyclinder Installation |  | FM | - Correct alignment and verticality - Joints sealed with approved material - Steps/lifting holes sealed - Wall thickness and type verified | D18 – Precast Installations Manufacturer specs NZS 3109 | Prior to backfilling | H
3 | Pipe protrusions into manhole |  | FM | -Flexible joint within 1metre of the manhole | D18.3 INSTALLATION | Prior to pouring corbels | H
4 | Internal Benching and Channeling |  | PM | Smooth trowelled finish - Accurate channel fall to spec - Benching slope toward channel - No honeycombing or cracks | D18.3 - AS/NZS 3500 - Formed finish F3 as specified in NZS 3114 | After completion of benching/invert | H
5 | Manhole Cover and Frame Installation |  | PM | - Infiltration check - Visual condition check - Manhole dimensions - Functional access features | D15.2 MATERIALS Maestro DIMHMCFHS MH cover | Before handover or commissioning | H
6
QMD07

## SWMH S21358
QMD07 INSPECTION & TEST PLAN
| Project Name: | Albert Crescent 3 Waters Renewal |  |  |  |  | ITP No: | 3
| Client | Invercargill City Council |  |  |  |  | Prepared By: | Jay Arthur
| Scope of Work | Installation SWMH S21358 |  |  |  |  | Date: | 2025-04-08
REFERENCE DOCUMENTS | [5 empty] | LEGEND
AS/NZS 3500 | [5 empty] | Test and Inspection Codes:
Project Drawings and Specification Document Section D | [5 empty] | H = Hold Point - Stop work until seen - Signed Record
NZS 3114 | [5 empty] | Work shall not proceed past the Hold Point until realeased by the organisation imposing the Hold Point
NZS 3109 | [5 empty] | I = In-process Inspection - Work continues - Signed Record
Formal inspection activity to be undertaken and recorded
W = Witness Inspection - Work Continues - Signature if Witness
An inspection point that may be witnessed by the organisation imposing the Witness Point
S = Activity subject to ongoing monitoring
APPROVAL/REVISION HISTORY | [5 empty] | Any activity that is subject to ongoing monitoring
Rev | Status | Approved By | Signature |  | Date | R = Records Review - Signed record per package
Review of text reports/records or other evidence of compliance
Responsible Inspectorate (RI) (may be modified to meet site specific requirements)
PM - Project Manager
REVIEWED BY | [5 empty] | FM - Foreman
Position |  | Name | Signature |  | Date Reviewed | CR - Council Representative
SUB - Subcontractor Representative
ITP COMPLETE
Position |  | Name | Signature |  | Date
Project Manager |  | Jay Arthur |  |  | 2025-04-08
ID: SWMH S21358
OP. No. | Operation To Be Inspected Or Tested |  | Controlled By : (Position) | Accept / Reject Criteria | Spec. Ref, Procedure Or Method Statement | Frequency Of Inspection OR Test | HOLD POINT | Puna Wai Civil | Client | Comments
1 | Manhole base Preparation (Pre-cast or in-situ) |  | CR | Clean and dry base - Correct bedding material and compaction - Reinforcement and formwork inspected - Waterproofing components in place | Project Drawings D18 Construction Methodology | Prior to placing concrete or setting precast base | I
2 | Manhole Cyclinder Installation |  | FM | - Correct alignment and verticality - Joints sealed with approved material - Steps/lifting holes sealed - Wall thickness and type verified | D18 – Precast Installations Manufacturer specs NZS 3109 | Prior to backfilling | H
3 | Pipe protrusions into manhole |  | FM | -Flexible joint within 1metre of the manhole | D18.3 INSTALLATION | Prior to pouring corbels | H
4 | Internal Benching and Channeling |  | PM | Smooth trowelled finish - Accurate channel fall to spec - Benching slope toward channel - No honeycombing or cracks | D18.3 - AS/NZS 3500 - Formed finish F3 as specified in NZS 3114 | After completion of benching/invert | H
5 | Manhole Cover and Frame Installation |  | PM | - Infiltration check - Visual condition check - Manhole dimensions - Functional access features | D15.2 MATERIALS Maestro DIMHMCFHS MH cover | Before handover or commissioning | H
6
QMD07

## SWMH S21359
QMD07 INSPECTION & TEST PLAN
| Project Name: | Albert Crescent 3 Waters Renewal |  |  |  |  | ITP No: | 4
| Client | Invercargill City Council |  |  |  |  | Prepared By: | Jay Arthur
| Scope of Work | Installation SWMH S21359 |  |  |  |  | Date: | 2025-04-08
REFERENCE DOCUMENTS | [5 empty] | LEGEND
AS/NZS 3500 | [5 empty] | Test and Inspection Codes:
Project Drawings and Specification Document Section D | [5 empty] | H = Hold Point - Stop work until seen - Signed Record
NZS 3114 | [5 empty] | Work shall not proceed past the Hold Point until realeased by the organisation imposing the Hold Point
NZS 3109 | [5 empty] | I = In-process Inspection - Work continues - Signed Record
Formal inspection activity to be undertaken and recorded
W = Witness Inspection - Work Continues - Signature if Witness
An inspection point that may be witnessed by the organisation imposing the Witness Point
S = Activity subject to ongoing monitoring
APPROVAL/REVISION HISTORY | [5 empty] | Any activity that is subject to ongoing monitoring
Rev | Status | Approved By | Signature |  | Date | R = Records Review - Signed record per package
Review of text reports/records or other evidence of compliance
Responsible Inspectorate (RI) (may be modified to meet site specific requirements)
PM - Project Manager
REVIEWED BY | [5 empty] | FM - Foreman
Position |  | Name | Signature |  | Date Reviewed | CR - Council Representative
SUB - Subcontractor Representative
ITP COMPLETE
Position |  | Name | Signature |  | Date
Project Manager |  | Jay Arthur |  |  | 2025-04-08
ID: SWMH S21359
OP. No. | Operation To Be Inspected Or Tested |  | Controlled By : (Position) | Accept / Reject Criteria | Spec. Ref, Procedure Or Method Statement | Frequency Of Inspection OR Test | HOLD POINT | Puna Wai Civil | Client | Comments
1 | Manhole base Preparation (Pre-cast or in-situ) |  | CR | Clean and dry base - Correct bedding material and compaction - Reinforcement and formwork inspected - Waterproofing components in place | Project Drawings D18 Construction Methodology | Prior to placing concrete or setting precast base | I
2 | Manhole Cyclinder Installation |  | FM | - Correct alignment and verticality - Joints sealed with approved material - Steps/lifting holes sealed - Wall thickness and type verified | D18 – Precast Installations Manufacturer specs NZS 3109 | Prior to backfilling | H
3 | Pipe protrusions into manhole |  | FM | -Flexible joint within 1metre of the manhole | D18.3 INSTALLATION | Prior to pouring corbels | H
4 | Internal Benching and Channeling |  | PM | Smooth trowelled finish - Accurate channel fall to spec - Benching slope toward channel - No honeycombing or cracks | D18.3 - AS/NZS 3500 - Formed finish F3 as specified in NZS 3114 | After completion of benching/invert | H
5 | Manhole Cover and Frame Installation |  | PM | - Infiltration check - Visual condition check - Manhole dimensions - Functional access features | D15.2 MATERIALS Maestro DIMHMCFHS MH cover | Before handover or commissioning | H
6
QMD07

## Water
QMD07 INSPECTION & TEST PLAN
| Project Name: | Albert Crescent 3 Waters Renewal |  |  |  |  | ITP No: | 5
| Client | Invercargill City Council |  |  |  |  | Prepared By: | Jay Arthur
| Scope of Work | Installation Water main and Structures |  |  |  |  | Date: | 2025-04-08
REFERENCE DOCUMENTS | [5 empty] | LEGEND
Project Drawings and Specification Document Section D | [5 empty] | Test and Inspection Codes:
NZS 4404 | [5 empty] | H = Hold Point - Stop work until seen - Signed Record
AS/NZS 4020 | [5 empty] | Work shall not proceed past the Hold Point until realeased by the organisation imposing the Hold Point
AS/NZS 2280 | [5 empty] | I = In-process Inspection - Work continues - Signed Record
AS/NZS 2566.2 | [5 empty] | Formal inspection activity to be undertaken and recorded
MoH Drinking Water Standards | [5 empty] | W = Witness Inspection - Work Continues - Signature if Witness
An inspection point that may be witnessed by the organisation imposing the Witness Point
S = Activity subject to ongoing monitoring
APPROVAL/REVISION HISTORY | [5 empty] | Any activity that is subject to ongoing monitoring
Rev | Status | Approved By | Signature |  | Date | R = Records Review - Signed record per package
Review of text reports/records or other evidence of compliance
Responsible Inspectorate (RI) (may be modified to meet site specific requirements)
PM - Project Manager
REVIEWED BY | [5 empty] | FM - Foreman
Position |  | Name | Signature |  | Date Reviewed | CR - Council Representative
SUB - Subcontractor Representative
ITP COMPLETE
Position |  | Name | Signature |  | Date
Project Manager |  | Jay Arthur |  |  | 2025-04-08
ID: W11674-W11675
OP. No. | Operation To Be Inspected Or Tested |  | Controlled By : (Position) | Accept / Reject Criteria | Spec. Ref, Procedure Or Method Statement | Frequency Of Inspection OR Test | HOLD POINT | Puna Wai Civil | Client | Comments
1 | Excavation |  | FM | Excavation depth, bedding material, trench width | D2 Buried Pipelines NZS 4404 AS/NZS 2566.2 | As works progress | S
2 | Pipe material delivery and storage |  | FM/CR | Inspection for damage, conformity with specs | D1.24 | Upon arrival | I
3 | Pipe laying (PE/ductile iron) |  | FM | Alignment, gradient, jointing method | D2 AS/NZS 2566.2 | As works progress | S
4 | Valve and fitting installation |  | FM | Correct location, bedding, supports | D5 AS/NZS 2280 | After completion of each valve and fitting installed | H
5 | Thrust blocks / anchor blocks |  | FM | Dimensions, concrete strength, curing | D5.7 NZS 4404 | After completion of each thrust block | H
6 | Pipe bedding and backfilling |  | FM | Correct layer thickness, compaction testing | D2.7 AS/NZS 2566.2 | As works progress | S
7 | Lateral Installation |  | FM | Alignment, jointing method | D8 AS/NZS 2566.2 | As works progress | S
8 | Hydrostatic pressure testing |  | PM/CR | M7 Pressure rebound test | D2.9 AS/NZS 2566.2 | Prior to comission | I
9 | Disinfection and flushing |  | PM/CR | Chlorination to 50 mg/L, 24 hr retention, residual test | D2.9 AS/NZS 4020 MoH Drinking Water Standards | Prior to comission | I
10 | Final connections and commissioning |  | FM | Visual inspection, isolation checks, flow direction | D2 NZS 4404 | As works progress | H
11
QMD07

## Foulsewer F13717
QMD07 INSPECTION & TEST PLAN
| Project Name: | Albert Crescent 3 Waters Renewal |  |  |  |  | ITP No: | 6
| Client | Invercargill City Council |  |  |  |  | Prepared By: | Jay Arthur
| Scope of Work | Installation Foulsewer main F13717 |  |  |  |  | Date: | 2025-04-08
REFERENCE DOCUMENTS | [5 empty] | LEGEND
Project Drawings and Specification Document Section D | [5 empty] | Test and Inspection Codes:
NZS 4404 | [5 empty] | H = Hold Point - Stop work until seen - Signed Record
AS/NZS 4020 | [5 empty] | Work shall not proceed past the Hold Point until realeased by the organisation imposing the Hold Point
NZS 3107 | [5 empty] | I = In-process Inspection - Work continues - Signed Record
AS/NZS 2566.2 | [5 empty] | Formal inspection activity to be undertaken and recorded
IPWEA CCTV Guidelines | [5 empty] | W = Witness Inspection - Work Continues - Signature if Witness
AS/NZS 2032 | [5 empty] | An inspection point that may be witnessed by the organisation imposing the Witness Point
S = Activity subject to ongoing monitoring
APPROVAL/REVISION HISTORY | [5 empty] | Any activity that is subject to ongoing monitoring
Rev | Status | Approved By | Signature |  | Date | R = Records Review - Signed record per package
Review of text reports/records or other evidence of compliance
Responsible Inspectorate (RI) (may be modified to meet site specific requirements)
PM - Project Manager
REVIEWED BY | [5 empty] | FM - Foreman
Position |  | Name | Signature |  | Date Reviewed | CR - Council Representative
SUB - Subcontractor Representative
ITP COMPLETE
Position |  | Name | Signature |  | Date
Project Manager |  | Jay Arthur |  |  | 2025-04-08
ID: F13717
OP. No. | Operation To Be Inspected Or Tested |  | Controlled By : (Position) | Accept / Reject Criteria | Spec. Ref, Procedure Or Method Statement | Frequency Of Inspection OR Test | HOLD POINT | Puna Wai Civil | Client | Comments
1 | Excavation |  | FM | Excavation depth, bedding material, trench width | D2 Buried Pipelines NZS 4404 AS/NZS 2566.2 | As works progress | S
2 | Pipe material delivery and storage |  | FM/CR | Inspection for damage, conformity with specs | D1.24 | Upon arrival | I
3 | Pipe laying (uPVC) |  | FM | Alignment, gradient, jointing method | D2.7 - AS/NZS 2566.2 | As works progress | S
4 | Compaction of backfill material |  | FM | Correct aggregates, 200mm layer depth, Plateau test, clegg readings, NDM testing | D2.7.7 - AS/NZS 2566.2 | 200mm layers Clegg result every 6m NDM result every 120m | S
5 | Lateral Installation |  | FM | Alignment, gradient, jointing method, concrete around junctions and bends as required | D4 - AS/NZS 2566.2 | As works progress | S
6 | Foul Sewer main pressure testing |  | FM/CR | Leakage testing including laterals | D2.9 - AS/NZS 2566.2 | After completion of main and lateral installation | I
7 | Pipe bedding and backfilling |  | FM | Correct layer thickness, compaction testing | D2.7 - AS/NZS 2566.2 | As works progress | S
8 | Cleaning and CCTV new main |  | PM | No debris or defects | D2.9 - AS/NZS 2566.2 | Prior to comission | I
9
10
QMD07

## Foulsewer F13725
QMD07 INSPECTION & TEST PLAN
| Project Name: | Albert Crescent 3 Waters Renewal |  |  |  |  | ITP No: | 7
| Client | Invercargill City Council |  |  |  |  | Prepared By: | Jay Arthur
| Scope of Work | Installation Foulsewer main F13725 |  |  |  |  | Date: | 2025-04-08
REFERENCE DOCUMENTS | [5 empty] | LEGEND
Project Drawings and Specification Document Section D | [5 empty] | Test and Inspection Codes:
NZS 4404 | [5 empty] | H = Hold Point - Stop work until seen - Signed Record
AS/NZS 4020 | [5 empty] | Work shall not proceed past the Hold Point until realeased by the organisation imposing the Hold Point
NZS 3107 | [5 empty] | I = In-process Inspection - Work continues - Signed Record
AS/NZS 2566.2 | [5 empty] | Formal inspection activity to be undertaken and recorded
IPWEA CCTV Guidelines | [5 empty] | W = Witness Inspection - Work Continues - Signature if Witness
AS/NZS 2032 | [5 empty] | An inspection point that may be witnessed by the organisation imposing the Witness Point
S = Activity subject to ongoing monitoring
APPROVAL/REVISION HISTORY | [5 empty] | Any activity that is subject to ongoing monitoring
Rev | Status | Approved By | Signature |  | Date | R = Records Review - Signed record per package
Review of text reports/records or other evidence of compliance
Responsible Inspectorate (RI) (may be modified to meet site specific requirements)
PM - Project Manager
REVIEWED BY | [5 empty] | FM - Foreman
Position |  | Name | Signature |  | Date Reviewed | CR - Council Representative
SUB - Subcontractor Representative
ITP COMPLETE
Position |  | Name | Signature |  | Date
Project Manager |  | Jay Arthur |  |  | 2025-04-08
ID: F13725
OP. No. | Operation To Be Inspected Or Tested |  | Controlled By : (Position) | Accept / Reject Criteria | Spec. Ref, Procedure Or Method Statement | Frequency Of Inspection OR Test | HOLD POINT | Puna Wai Civil | Client | Comments
1 | Excavation |  | FM | Excavation depth, bedding material, trench width | D2 Buried Pipelines NZS 4404 AS/NZS 2566.2 | As works progress | S
2 | Pipe material delivery and storage |  | FM/CR | Inspection for damage, conformity with specs | D1.24 | Upon arrival | I
3 | Pipe laying (uPVC) |  | FM | Alignment, gradient, jointing method | D2.7 - AS/NZS 2566.2 | As works progress | S
4 | Compaction of backfill material |  | FM | Correct aggregates, 200mm layer depth, Plateau test, clegg readings, NDM testing | D2.7.7 - AS/NZS 2566.2 | 200mm layers Clegg result every 6m NDM result every 120m | S
5 | Lateral Installation |  | FM | Alignment, gradient, jointing method, concrete around junctions and bends as required | D4 - AS/NZS 2566.2 | As works progress | S
6 | Foul Sewer main pressure testing |  | FM/CR | Leakage testing including laterals | D2.9 - AS/NZS 2566.2 | After completion of main and lateral installation | I
7 | Pipe bedding and backfilling |  | FM | Correct layer thickness, compaction testing | D2.7 - AS/NZS 2566.2 | As works progress | S
8 | Cleaning and CCTV new main |  | PM | No debris or defects | D2.9 - AS/NZS 2566.2 | Prior to comission | I
9
10
QMD07

## Stormwater S13459
QMD07 INSPECTION & TEST PLAN
| Project Name: | Albert Crescent 3 Waters Renewal |  |  |  |  | ITP No: | 8
| Client | Invercargill City Council |  |  |  |  | Prepared By: | Jay Arthur
| Scope of Work | Installation Stormwater main S13459 |  |  |  |  | Date: | 2025-04-08
REFERENCE DOCUMENTS | [5 empty] | LEGEND
Project Drawings and Specification Document Section D | [5 empty] | Test and Inspection Codes:
NZS 4404 | [5 empty] | H = Hold Point - Stop work until seen - Signed Record
AS/NZS 4020 | [5 empty] | Work shall not proceed past the Hold Point until realeased by the organisation imposing the Hold Point
NZS 3107 | [5 empty] | I = In-process Inspection - Work continues - Signed Record
AS/NZS 2566.2 | [5 empty] | Formal inspection activity to be undertaken and recorded
IPWEA CCTV Guidelines | [5 empty] | W = Witness Inspection - Work Continues - Signature if Witness
AS/NZS 2032 | [5 empty] | An inspection point that may be witnessed by the organisation imposing the Witness Point
S = Activity subject to ongoing monitoring
APPROVAL/REVISION HISTORY | [5 empty] | Any activity that is subject to ongoing monitoring
Rev | Status | Approved By | Signature |  | Date | R = Records Review - Signed record per package
Review of text reports/records or other evidence of compliance
Responsible Inspectorate (RI) (may be modified to meet site specific requirements)
PM - Project Manager
REVIEWED BY | [5 empty] | FM - Foreman
Position |  | Name | Signature |  | Date Reviewed | CR - Council Representative
SUB - Subcontractor Representative
ITP COMPLETE
Position |  | Name | Signature |  | Date
Project Manager |  | Jay Arthur |  |  | 2025-04-08
ID: S13459
OP. No. | Operation To Be Inspected Or Tested |  | Controlled By : (Position) | Accept / Reject Criteria | Spec. Ref, Procedure Or Method Statement | Frequency Of Inspection OR Test | HOLD POINT | Puna Wai Civil | Client | Comments
1 | Excavation |  | FM | Excavation depth, bedding material, trench width | D2 Buried Pipelines NZS 4404 AS/NZS 2566.2 | As works progress | S
2 | Pipe material delivery and storage |  | FM/CR | Inspection for damage, conformity with specs | D1.24 | Upon arrival | I
3 | Pipe laying (uPVC) |  | FM | Alignment, gradient, jointing method | D2.7 - AS/NZS 2566.2 | As works progress | S
4 | Compaction of backfill material |  | FM | Correct aggregates, 200mm layer depth, Plateau test, clegg readings, NDM testing | D2.7.7 - AS/NZS 2566.2 | 200mm layers Clegg result every 6m NDM result every 120m | S
5 | Lateral Installation |  | FM | Alignment, gradient, jointing method, concrete around junctions and bends as required | D4 - AS/NZS 2566.2 | As works progress | S
6 | Pipe bedding and backfilling |  | FM | Correct layer thickness, compaction testing | D2.7 - AS/NZS 2566.2 | As works progress | S
7 | Cleaning and CCTV new main |  | PM | No debris or defects | D2.9 - AS/NZS 2566.2 | Prior to comission | I
8
9
10
11
QMD07

## Stormwater S13440
QMD07 INSPECTION & TEST PLAN
| Project Name: | Albert Crescent 3 Waters Renewal |  |  |  |  | ITP No: | 9
| Client | Invercargill City Council |  |  |  |  | Prepared By: | Jay Arthur
| Scope of Work | Installation Stormwater main S13440 |  |  |  |  | Date: | 2025-04-08
REFERENCE DOCUMENTS | [5 empty] | LEGEND
Project Drawings and Specification Document Section D | [5 empty] | Test and Inspection Codes:
NZS 4404 | [5 empty] | H = Hold Point - Stop work until seen - Signed Record
AS/NZS 4020 | [5 empty] | Work shall not proceed past the Hold Point until realeased by the organisation imposing the Hold Point
NZS 3107 | [5 empty] | I = In-process Inspection - Work continues - Signed Record
AS/NZS 2566.2 | [5 empty] | Formal inspection activity to be undertaken and recorded
IPWEA CCTV Guidelines | [5 empty] | W = Witness Inspection - Work Continues - Signature if Witness
AS/NZS 2032 | [5 empty] | An inspection point that may be witnessed by the organisation imposing the Witness Point
S = Activity subject to ongoing monitoring
APPROVAL/REVISION HISTORY | [5 empty] | Any activity that is subject to ongoing monitoring
Rev | Status | Approved By | Signature |  | Date | R = Records Review - Signed record per package
Review of text reports/records or other evidence of compliance
Responsible Inspectorate (RI) (may be modified to meet site specific requirements)
PM - Project Manager
REVIEWED BY | [5 empty] | FM - Foreman
Position |  | Name | Signature |  | Date Reviewed | CR - Council Representative
SUB - Subcontractor Representative
ITP COMPLETE
Position |  | Name | Signature |  | Date
Project Manager |  | Jay Arthur |  |  | 2025-04-08
ID: S13440
OP. No. | Operation To Be Inspected Or Tested |  | Controlled By : (Position) | Accept / Reject Criteria | Spec. Ref, Procedure Or Method Statement | Frequency Of Inspection OR Test | HOLD POINT | Puna Wai Civil | Client | Comments
1 | Excavation |  | FM | Excavation depth, bedding material, trench width | D2 Buried Pipelines NZS 4404 AS/NZS 2566.2 | As works progress | S
2 | Pipe material delivery and storage |  | FM/CR | Inspection for damage, conformity with specs | D1.24 | Upon arrival | I
3 | Pipe laying (uPVC) |  | FM | Alignment, gradient, jointing method | D2.7 - AS/NZS 2566.2 | As works progress | S
4 | Compaction of backfill material |  | FM | Correct aggregates, 200mm layer depth, Plateau test, clegg readings, NDM testing | D2.7.7 - AS/NZS 2566.2 | 200mm layers Clegg result every 6m NDM result every 120m | S
5 | Lateral Installation |  | FM | Alignment, gradient, jointing method, concrete around junctions and bends as required | D4 - AS/NZS 2566.2 | As works progress | S
6 | Pipe bedding and backfilling |  | FM | Correct layer thickness, compaction testing | D2.7 - AS/NZS 2566.2 | As works progress | S
7 | Cleaning and CCTV new main |  | PM | No debris or defects | D2.9 - AS/NZS 2566.2 | Prior to comission | I
8
9
10
11
QMD07

## Asphalt Reinstatement
QMD07 INSPECTION & TEST PLAN
| Project Name: | Albert Crescent 3 Waters Renewal |  |  |  |  | ITP No: | 10
| Client | Invercargill City Council |  |  |  |  | Prepared By: | Jay Arthur
| Scope of Work | Asphalt Reinstatement |  |  |  |  | Date: | 2025-04-08
REFERENCE DOCUMENTS | [5 empty] | LEGEND
Project Drawings and Specification Document Section D | [5 empty] | Test and Inspection Codes:
NZTA P40 | [5 empty] | H = Hold Point - Stop work until seen - Signed Record
NZTA B/2 | [5 empty] | Work shall not proceed past the Hold Point until realeased by the organisation imposing the Hold Point
NZTA P42 | [5 empty] | I = In-process Inspection - Work continues - Signed Record
NZTA M/10 | [5 empty] | Formal inspection activity to be undertaken and recorded
W = Witness Inspection - Work Continues - Signature if Witness
An inspection point that may be witnessed by the organisation imposing the Witness Point
S = Activity subject to ongoing monitoring
APPROVAL/REVISION HISTORY | [5 empty] | Any activity that is subject to ongoing monitoring
Rev | Status | Approved By | Signature |  | Date | R = Records Review - Signed record per package
Review of text reports/records or other evidence of compliance
Responsible Inspectorate (RI) (may be modified to meet site specific requirements)
PM - Project Manager
REVIEWED BY | [5 empty] | FM - Foreman
Position |  | Name | Signature |  | Date Reviewed | CR - Council Representative
SUB - Subcontractor Representative
ITP COMPLETE
Position |  | Name | Signature |  | Date
Project Manager |  | Jay Arthur |  |  | 2025-04-08
Asphalt Reinstatement
OP. No. | Operation To Be Inspected Or Tested |  | Controlled By : (Position) | Accept / Reject Criteria | Spec. Ref, Procedure Or Method Statement | Frequency Of Inspection OR Test | HOLD POINT | Puna Wai Civil | Client | Comments
1 | Saw cutting of existing pavement |  | PM/CR | Edge alignment, depth, and cleanliness | D12.4 - NZTA P40 | Prior to reinstatement | S
2 | Placement and compaction of basecourse |  | PM/CR | Layer thickness and compaction testing, preparation tolerance -/+5mm | D2.7.7.2 - NZTA B/2 | As works progress | I
3 | Tack coating edges and base |  | SUB | Uniform application, coverage check | D12.4 - NZTA P42 – Tack Coat Application | As works progress | S
4 | Placement of asphalt (AC mix) |  | SUB | Correct temperature and spread rate | D12.4 - NZTA M/10 – Asphalt Mix Requirements | As works progress | S
5 | Compaction of asphalt layers |  | SUB | Rolling pattern, compaction | D12.4 - NZTA M/10, B2 – Asphalt Compaction | As works progress | S
6 | Joint sealing and finish |  | SUB | Seam bonding and surface appearance | D12.4 - NZTA P40 – Joints and Finish | Post Paving | S
7 | Final inspection and sign-off |  | PM/CR | All specs met, records submitted | Contract Conditions | Final Walk over | I
9
10
11
QMD07