## Master List Templates
Id | Type | Name | Values | Prompting Name
8f1df2a9-920c-50cd-bd21-5f261f2893fd | checklist | Defect / Issue to be rectified |  | ADD new defect / issue to be rectified [RENAME CHECKLIST TO LOCATION & DETAILS OF DEFECT]
1ce33f58-bceb-5bb5-b5a7-61ac5e21fa4d | checkpoint | Upload photo of defect / issue to be rectified. Add comments if necessary.
97acd7e5-f320-523a-9616-f769c9258094 | checkpoint | Has issue been rectified / defect been closed out? Upload photo
bab1d5a9-a3d7-58ff-a01f-4224a18aac6b | note | Only PASS once issue is rectified / defect is closed out
3a7fcaa2-7d4c-58ac-a353-e604d973278a | checklist | Document Attachment ITP (V.220421) |  | Document Attachment ITP (V.220421)
90417bc2-d69e-5f12-91e8-4743f1522568 | checkpoint | Documents/Drawings attached for reference - Pass once attached
86fd7cdf-eb03-59ff-a8fb-9cbb6063cc31 | checklist | LM-FOR-50-ITR-303.6 F.E Installation |  | LM-FOR-50-ITR-303.6 F.E Installation
e7581576-5a10-5963-90b0-44587360e1f6 | section | Inspection
af574a82-b1c1-544f-8842-f6b972f7214f | checkpoint | Check that the extinguisher is conspicuous, readily accessible and in its assigned location in accordance with the approved plan.
b8e2834e-1fbf-5da6-85fa-65a1b72c2c5a | checkpoint | Check that the extinguisher is mounted at the appropriate height in accordance with Figure 3.2.
3ecbf633-88fb-5c61-b47c-f767055bca36 | checkpoint | Check that the anti-tamper device is intact. And that the service tag or label is firmly attached.
ee359504-7b77-53f5-b334-359db05bbab6 | checkpoint | Check that the extinguisher is clean and the operating instructions are legible.
94509bba-18e5-5a1c-8916-351d6871723f | checkpoint | Check that the extinguisher, including any attachments, is not damaged.
5fe8d71c-7a6f-57af-8a1f-66928e1c4f7c | checkpoint | Check that the hose is securely fitted, the nozzle is securely attached, the assembly is free from obstruction, and the hose shows no cracking or other signs of damage or deterioration.
7f17a98a-03e9-5ad1-9a19-55a95b9affdd | checkpoint | Check that the appropriate discharge nozzle is fitted and is not blocked or damaged.
4a98c80d-17f6-5cf1-860c-d4106d1ca02a | checkpoint | Where fitted, check that the pressure indicator is legible, and registering within the operable range.
302afa07-b49d-5426-a8d7-701dfa657548 | checkpoint | Check that the appropriate support bracket is securely attached to wall or other suitable feature.
d80d130d-72f8-5fc9-872b-1fc379f43b15 | section | Completion
b894fd15-4591-5de3-8256-45a1e534edc3 | checkpoint | Works completed to specification/drawings - Attach photos of work below
e9293cc4-ea92-5d10-894f-769075d2bba2 | note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
de0c0b7c-9580-5deb-a42c-8186d99d18b4 | button | Area left clean & tidy | Yes, No
6206a3ec-e6ed-551a-b606-384aa14e7e2f | tickbox | Leemark Sign-Off
54c752ce-77c9-5870-98c8-90c35ee82def | tickbox | Builder Sign-Off
dd71b766-5bfd-5126-8e81-631da7396226 | signoff | Sign-Off - click to Add signature(s)

## Project Checklist Templates
Id | Type | Name | Values | Prompting Name
9cea252b-a162-5832-ba86-10a1052c0cfe | checklist | LM-FOR-30-ITR-301 Sprinkler Installation/Fitoff |  | LM-FOR-30-ITR-301 Sprinkler Installation/Fitoff
6465d6f3-3be2-5499-b503-3c3e618fa07c | section | Sprinkler Rough-In
d43163db-8f22-5249-9081-91480c3ed8d4 | checkpoint | Latest consented drawings checked & referenced
4c86029a-d781-58d4-ab05-31be3edee4f8 | textbox | Drawing & Revision #
0c9e405c-eb3b-5fb4-a1bc-b3def20dbb1d | tickbox | Area clear, tidy and accessible
7e882623-d0b9-5543-949f-3565c5f582d1 | note | Attach Photos/Comments below if any issues & send report to Builder
908a092b-915c-5c08-b50c-ede1e907f1fb | checkpoint | Supports spacing & fixing as per AS2118
0ce6b1a3-908f-57f4-b480-ef7e2ab4bca0 | checkpoint | Pipework installed as per drawings
9f5be1cb-e20d-521e-ba03-b7cd11733d19 | checkpoint | Concealed space sprinklers installed
db639292-eb82-5cfd-91b6-776ba182f82d | checkpoint | All ends blanked off/plugged for testing
abaffbc0-a165-5a7d-968a-9e1ee9f1b2dd | checkpoint | Pipes left out
79f285fd-b900-5728-b3a6-8ef5464c2e30 | note | Fail=Missing, Pass=Complete
21bfabe2-8679-570d-8ffd-0a2ea9d0abb2 | button | Pipes left out - installed | Yes, No
c016619f-d61c-50f0-af4f-4b00068361fe | section | Sprinkler Fit-Off
ab27a27c-92cb-435a-8ae3-4bb23b6462a4 | checkpoint | Latest consented drawings checked & referenced
26126db9-8fcc-5f1c-aebf-4ae0acc68ed4 | textbox | Drawing & Revision #
4cb73ded-86bb-5ad4-96a0-7a4a0807f0cc | tickbox | Area clear, tidy and accessible
b55ca0c7-ad8c-5225-aaff-fccf38678e0c | note | Attach Photos/Comments below if any issues & send report to Builder
f86149be-c970-57fd-975a-1970dbf27b35 | checkpoint | Ceiling grid levelled
d61ada5b-d5ad-556c-afda-15a7b0b6e415 | checkpoint | Sprinklers installed as per drawings
d4116fcb-4c5a-5e06-9763-eeb6318c3f6c | checkpoint | Sprinkler Type & temperature as per drawings
17eac725-bb30-50a9-8f45-34d5f0844ff3 | checkpoint | All escutcheon plates installed
d817b34e-0485-51ac-9c3f-d7acb9574942 | checkpoint | Areas not fitted-off
201d8a31-e059-541f-a7dc-3e638b620821 | note | Fail=Missing, Pass=Complete
768379e9-5ac8-5d6c-9168-efd23450b506 | button | Areas not fitted-off - completed | Yes, No
cbff4ae3-2b4c-528c-a82f-4b4dff05ef2e | checkpoint | Client Sign Off Sheets Complete
bdd1e031-14b5-5238-9027-9fddf2280de3 | checkpoint | Painting carried out
9947fe3a-0d3c-522f-994e-6ac7081bd841 | checkpoint | Pressure Tested (refer ITR 401) - Completed
d80d130d-72f8-5fc9-872b-1fc379f43b15 | section | Completion
b894fd15-4591-5de3-8256-45a1e534edc3 | checkpoint | Works completed to specification/drawings - Attach photos of work below
c78964f1-4cd6-5270-9558-15c0c49bdc13 | note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
b0a55528-8942-598b-9eb1-ced28ae84dfd | button | Area left clean & tidy | Yes, No
0b1ff88a-e14e-52be-8250-4ed037b84d1f | tickbox | Leemark Sign-Off
b97fd727-cc11-517c-bd3b-9c4b7947da9d | tickbox | Builder Sign-Off
dd71b766-5bfd-5126-8e81-631da7396226 | signoff | Sign-Off - click to Add signature(s)
4e059e3a-9e6f-54bd-a056-3c5c5bb09689 | checklist | LM-FOR-30-ITR-301.1 Sprinkler Control Valve |  | LM-FOR-30-ITR-301.1 Sprinkler Control Valve
e8adbc84-b448-5119-bc35-7edd8200d05f | section | Installation
d43163db-8f22-5249-9081-91480c3ed8d4 | checkpoint | Latest consented drawings checked & referenced
63eae8b6-4db3-5755-8c22-4f910cfc456b | textbox | Drawing & Revision #
cfc6d0f8-9e2c-5dbd-ab40-e3084654de18 | tickbox | Area clear, tidy and accessible
55fcae69-bf4d-5e3c-9f91-8083f34f8342 | note | Attach Photos/Comments below if any issues & send report to Builder
d3785afd-be26-556a-8030-d4d52c7c0569 | checkpoint | Supply and Installation pipe works are installed in the correct position and alignment in accordance with the approved drawing/plan
2c03f732-01b0-5eb1-a1f7-51a4c41f25b0 | checkpoint | All supports are completely installed, spaced and bolted down box / assembly secured
fd5662df-1796-5fcf-b393-c5e715bcdaa7 | checkpoint | All roll grooved couplings / flanges are properly tightened
f35d70c8-3be5-5815-a8c4-980cb2f10ce9 | checkpoint | Valve station drain is properly connected to risers drain and building hydraulic drainage
020ced20-c291-5215-ac10-4a1390ec51be | checkpoint | Approved type of Monitored Main Stop Valve is fitted and operational
0acb40dd-f861-597c-a428-a342cf861149 | checkpoint | All specific signage is installed lock shut / lock open including FSV number of M/V’s
396a36da-12c0-540a-8273-786ebdc5d0e3 | checkpoint | Correct size and range of supply and installation pressure gauges with shut-off cocks are fitted
92f8e20c-4a42-5d08-9490-97da44447c0f | checkpoint | Correct type solenoid, flow switch, couplings etc installed
3d59f409-8f3b-4e54-835f-6653abc32006 | checkpoint | Correct size and range of supply and installation pressure gauges with shut-off cocks are fitted
eb6dee05-be6e-54f8-9543-4d4468a8937d | checkpoint | Confirm GFA on solenoid activation/ flow switch/ MV activation
847800a6-8275-5896-a5f4-84928decccd8 | checkpoint | Control Valve is positioned between 1150mm to 1800mm
d80d130d-72f8-5fc9-872b-1fc379f43b15 | section | Completion
b894fd15-4591-5de3-8256-45a1e534edc3 | checkpoint | Works completed to specification/drawings - Attach photos of work below
413b9e40-01d4-5593-9c2c-908a2c419af4 | note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
c1a7b2bc-2eec-57c7-9469-626316ed584d | button | Area left clean & tidy | Yes, No
f1904748-7bb3-5423-bf4a-7fdabd166ea9 | tickbox | Leemark Sign-Off
df0af5be-4991-51bc-a377-c5d2a4300bab | tickbox | Builder Sign-Off
dd71b766-5bfd-5126-8e81-631da7396226 | signoff | Sign-Off - click to Add signature(s)
4dc5b188-092b-566c-b29b-e3d3f27dc698 | checklist | LM-FOR-30-ITR-301.2 Alarm Control Valve |  | LM-FOR-30-ITR-301.2 Alarm Control Valve
e8adbc84-b448-5119-bc35-7edd8200d05f | section | Installation
d43163db-8f22-5249-9081-91480c3ed8d4 | checkpoint | Latest consented drawings checked & referenced
e3cf3bd3-6e2a-57a0-805a-58f6e637fe70 | textbox | Drawing & Revision #
31daee6c-311b-5a94-acee-8508c8b48fb5 | tickbox | Area clear, tidy and accessible
53d79436-49e7-5856-a429-811da5898308 | note | Attach Photos/Comments below if any issues & send report to Builder
d3785afd-be26-556a-8030-d4d52c7c0569 | checkpoint | Supply and Installation pipe works are installed in the correct position and alignment in accordance with the approved drawing/plan
d3fc9e03-0727-5e20-a5c6-d87330da6161 | checkpoint | All supports are completely installed, spaced and bolted down
fd5662df-1796-5fcf-b393-c5e715bcdaa7 | checkpoint | All roll grooved couplings / flanges are properly tightened
8ec0a757-52bd-53e3-97a0-4a3c61680f43 | checkpoint | Correct size and specification of Alarm Valve is installed in accordance with the approved drawing/plan
020ced20-c291-5215-ac10-4a1390ec51be | checkpoint | Approved type of Monitored Main Stop Valve is fitted and operational
3d160c96-05f0-595d-a38c-5a544398af3c | checkpoint | Correct size of alarm line is installed, adequately supported and alarm gong is properly piped to drain
514df684-2414-5810-9f61-6726dc897609 | checkpoint | Correct size of orifice is fitted and piped to drain when system is with retard chamber
b1c5ba1f-c1bc-5729-9de5-3657f2e2c511 | checkpoint | Main waste & test valve is fitted and piped to drain
96d7ab67-182f-54a9-8ae8-cc85ff8fa282 | checkpoint | Correct type and model of Direct Brigade Alarm device is fitted
dfbe0cb1-770f-5d69-9efa-4fb35da5ce62 | checkpoint | Correct model and range of Pressure Switch is fitted
396a36da-12c0-540a-8273-786ebdc5d0e3 | checkpoint | Correct size and range of supply and installation pressure gauges with shut-off cocks are fitted
6415e286-60d7-5188-bfaf-1fab5bafe75d | checkpoint | All signalling devices (Monitored Stop Valve, DBA, Low Pressure Switch), are wired back to FIP
a44b2c31-0538-5a0e-ab55-3c5f70914026 | checkpoint | Control Valve associated pipe works paint touch-up repair is completed
d80d130d-72f8-5fc9-872b-1fc379f43b15 | section | Completion
b894fd15-4591-5de3-8256-45a1e534edc3 | checkpoint | Works completed to specification/drawings - Attach photos of work below
f95e0b10-d8d9-560d-abe9-3efc14231090 | note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
8439c4c1-a4fe-5d3d-8146-77d60391f331 | button | Area left clean & tidy | Yes, No
eca00539-7d4a-5d65-830a-9a0361c0820c | tickbox | Leemark Sign-Off
aa83bd7f-3dce-5320-97e6-05cc938bb076 | tickbox | Builder Sign-Off
dd71b766-5bfd-5126-8e81-631da7396226 | signoff | Sign-Off - click to Add signature(s)
2cdf4022-79b2-5de7-b4f8-ccfcf0fed05b | checklist | LM-FOR-33-ITR-401 Sprinkler & Hydrant hydrostatic test |  | LM-FOR-33-ITR-401 Sprinkler & Hydrant hydrostatic test
92773c79-21d7-53d1-87b7-e42ea3f7d786 | section | Guidelines
37f6445d-78dc-50c9-9d24-ef8faffb8fcf | checkpoint | Guidelines understood - Pass once read
a4c68d39-4aa1-502d-8720-0028fa1b9a7a | note | Guidelines: Fire Sprinkler Systems – 1600kPa or 400kPa above the maximum static pressure for a duration of 2 hours (Check notes on Construction Drawing for nominated test pressure)
2557f4ff-a9c5-5837-b5f0-f6ab3de565fb | note | Fire Hydrant Systems (Low Rise) – 1700kPa or 15 times the design pressure for a duration of 2 hours (Check notes on Construction Drawing for nominated test pressure)
bb560cb1-0dad-5a28-8ad2-0810647c5812 | note | Fire Hydrant Systems (High Rise) – 1050kPa at the highest hydrant in the pressure stage being tested If pressure reading is being taken at the booster, determine the height difference in metres between the top hydrant and the booster and add 10kPa per metre of static pressure to this figure with a minimum test pressure of 1700kPa If in doubt please seek clarification from the Construction Supervisor or the Design Manager
685b5e21-9405-579d-b8f2-96b5b9c79eca | section | Rough In Only OR Rough In & Fit Off Together
9f29aa77-6976-5d3a-adf3-e4d55f0fd7fe | checkpoint | First Sighting - Pass once entered
801dbdfe-c273-5ee5-be62-6f4c647f5001 | textbox | Date
d73faad3-b770-5b06-a32b-3c5d4552a003 | textbox | Time
581682b4-cd9e-5a83-a961-4ca694e0ff1f | textbox | Pressure
fa356fe3-e4cf-529c-a66e-56312dc121ff | button | Photo(s) taken | Yes, No
2777f205-e525-50f1-bdcd-acd3a6bc7245 | button | Leemark Sign-Off - Attach below | Pass, Fail
17eea8ea-5b4c-5487-b428-0837caf89997 | button | Builder Sign-Off - Attach below | Pass, Fail, N/A
b1ca19d8-c57b-5fd0-ba00-fc40f8326b2b | checkpoint | Second Sighting - Pass once entered
7970433a-c86e-5d1e-8dd7-477e8a6b61cb | textbox | Date
da78add1-0ff2-5e7f-9f30-e0c290db91c0 | textbox | Time
89d36721-2f5e-5bc5-a7e4-3c8e1958137c | textbox | Pressure
184d0cea-0cf1-5b85-8e05-6780e9926884 | button | Photo(s) taken | Yes, No
2e12dfd5-1a55-511e-9bb3-a1d363e67b61 | button | Leemark Sign-Off - Attach below | Pass, Fail
5aa044f4-bb22-5442-bf90-7fdf4d7e06bd | button | Builder Sign-Off - Attach below | Pass, Fail, N/A
2c24d488-7f93-5146-bd6c-2217a211c5d9 | section | Fit Off (if required ie if not covered by the above section)
b34488a6-cbcd-5004-90ee-040d52d2049a | checkpoint | Subsequent Sighting - Pass once entered
be264ba9-c1c4-5ad2-84ab-14a07cbb7399 | textbox | Date
a07174b4-eb73-52b7-beac-2388bdeecc6c | textbox | Time
311b1850-7da4-5b6a-bec1-d0c54866f7b7 | textbox | Pressure
2954b052-9a96-55ba-beb0-3f60dba38d95 | button | Photo(s) taken | Yes, No
874dbd26-6c8c-5ae1-8f64-00693fe804c3 | button | Leemark Sign-Off - Attach below | Pass, Fail
f0717548-ff52-5ef4-9efe-57bc95c6d675 | button | Builder Sign-Off - Attach below | Pass, Fail, N/A
d80d130d-72f8-5fc9-872b-1fc379f43b15 | section | Completion
b894fd15-4591-5de3-8256-45a1e534edc3 | checkpoint | Works completed to specification/drawings - Attach photos of work below
fef67b80-09e7-5b11-88c1-1c4d9a2acd7f | note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
8572316f-9f44-5f4d-9ebe-a1aa8f995ebe | button | Area left clean & tidy | Yes, No
c1d2be28-36ca-5022-9cfb-be4d83605ce6 | tickbox | Leemark Sign-Off
f33cc38b-e6aa-5579-b409-283fb1cd80f0 | tickbox | Builder Sign-Off
dd71b766-5bfd-5126-8e81-631da7396226 | signoff | Sign-Off - click to Add signature(s)
398aef93-81f2-5d5a-afa5-184534576046 | checklist | LM-FOR-40-ITR-302.1 Fire Pump Installation |  | LM-FOR-40-ITR-302.1 Fire Pump Installation
e8adbc84-b448-5119-bc35-7edd8200d05f | section | Installation
d43163db-8f22-5249-9081-91480c3ed8d4 | checkpoint | Latest consented drawings checked & referenced
7ba988c4-1210-5056-9030-cbf3f4ef36de | textbox | Drawing & Revision #
5895aa87-e2aa-5d57-8786-040586a0955b | tickbox | Area clear, tidy and accessible
c81ac5a1-0324-5879-93cf-44cbf0d4b6e2 | note | Attach Photos/Comments below if any issues & send report to Builder
088de84c-7237-5409-a42f-feb36c8f8ecb | checkpoint | Pump installation arrangement including suction and discharge pipe works are in accordance with the approved drawing/plan
b5fbfde4-0c74-542c-b58d-694809739674 | checkpoint | Pump clearance is 1000 mm on all four sides and 600 mm between pumps
8f2e10e8-9575-5ab8-8165-b25201777363 | checkpoint | Concrete plinth/foundation height is minimum 150 mm from FFL and 150 mm wider on all four sides of pump base
edac107a-efde-5e62-9af3-dfed2596c240 | checkpoint | Pump base is sitting squarely and bolted down Vibration mounts are properly anchored on plinth or inertia plinth
01a764f3-2f59-5626-9bcc-616056b7c845 | checkpoint | Pump suction and discharge pipework are completely installed and connected Supports are adequately provided
38f23645-ec05-57bb-861d-135b6dc7d167 | checkpoint | Control panels installed and bolted down, MFB have clear access around pump controller 1000mm Arc
ec285001-c249-5b2a-8e24-a47bd2c5c20a | checkpoint | Suction isolation valve installed is OS & Y type
566dde6f-9a61-5df3-8a1a-eece6a730b20 | checkpoint | Non-return valve is installed and located upstream of the isolation valve in pump discharge line
a0d82dfa-4bc5-53dc-8529-d43d2ab74294 | checkpoint | Pump circulation-relief valve for electric driven pump is installed and piped to drain or tank return line
a900469f-df76-51a7-9216-e212268a75b9 | checkpoint | Heat exchanger cooling water harness for diesel driven pump is installed and piped to drain or tank return line
40149c62-d8a8-5112-ad80-b67530f230a1 | checkpoint | Pressure gauge with gauge cock is installed min 2Ø downstream of discharge flange or reducer
201a2fc1-191f-5904-b0ff-fc4256a3501a | checkpoint | Pressure reductions installed on manifold x2 for each stage with M/V’s and Annubar for each stage
e908e4fa-140d-54c0-be7e-53b7dc4af6be | checkpoint | Exhaust connected to pump and installed to approved discharge location
5dbf94f6-eb2a-5556-8a79-42892c8c95c9 | checkpoint | Full tanks have been filled with Diesel; Electric Pumps AND Controls ready for energisation
d80d130d-72f8-5fc9-872b-1fc379f43b15 | section | Completion
b894fd15-4591-5de3-8256-45a1e534edc3 | checkpoint | Works completed to specification/drawings - Attach photos of work below
a043cdf2-6f97-57e5-a4c7-0a29af97a6ce | note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
73e8840c-8302-5f8b-b2f5-f4e0847470e4 | button | Area left clean & tidy | Yes, No
095172ec-d6f0-5e1a-ab1f-18289c0b96e2 | tickbox | Leemark Sign-Off
bb323f9b-d4c0-51e7-9f4c-d3dadcd36a61 | tickbox | Builder Sign-Off
dd71b766-5bfd-5126-8e81-631da7396226 | signoff | Sign-Off - click to Add signature(s)
8300b725-d962-55f7-b4ac-b55918465a0a | checklist | LM-FOR-40-ITR-302.2 Hydrant Installation |  | LM-FOR-40-ITR-302.2 Hydrant Installation
e8adbc84-b448-5119-bc35-7edd8200d05f | section | Installation
d43163db-8f22-5249-9081-91480c3ed8d4 | checkpoint | Latest consented drawings checked & referenced
cdd41034-ea2d-5ba7-9561-5cca67ba7a78 | textbox | Drawing & Revision #
ae91f4d7-e76a-524c-b787-8a7b81d1f4aa | tickbox | Area clear, tidy and accessible
4a781a3a-5731-56e3-976d-b9db0cad8997 | note | Attach Photos/Comments below if any issues & send report to Builder
ec5c5125-4bea-5694-9cf1-8b9207f44c84 | textbox | Hydrant No.
3ad39dfa-233e-508c-b2af-4b1a5c953960 | checkpoint | Hydrant supply pipe works completely installed of correct size, position, elevation, alignment and adequately supported in accordance with approved drawing/plan
06646595-6c37-5aae-b53d-227d691d117a | checkpoint | Hydrostatic pressure testing of installed supply pipe works completed and accepted
6dd48c80-a7e0-5e34-afe3-6e37361dbe02 | checkpoint | Hydrant valves and associated pipes and fittings used are in accordance with the approved specifications and applicable codes/standards
870639f6-6e97-58a9-b081-c3224a30ec67 | checkpoint | Fire Hydrant and associated fire water main isolation valves locations are in accordance with the approved drawing/plan
9f51d2d1-c512-5015-bb7f-82d665b55dfc | checkpoint | Hydrants stand pipe is adequately supported and bolted down. Concrete surround block provided for external hydrant
62596d7c-83a4-5c3b-af45-020d35e5ff07 | checkpoint | Hydrant valve is between 750 to 1200 mm from finish floor/grade level
32192ebb-9b3e-5ee2-acfd-1d35310b4022 | checkpoint | Valve outlet is facing away from the wall and not more than 35O below its horizontal axis. Minimum 300 mm clearance around the valve outlet
1fef2f25-8b2d-5a27-89c4-1942ce6fc623 | checkpoint | Minimum 1000 mm clear space in front of valve outlet is provided
019bc049-244c-53ba-999c-b2517ef64ae3 | checkpoint | Valve handwheel clearance is minimum 100 mm clear of any obstruction at fully open
d80d130d-72f8-5fc9-872b-1fc379f43b15 | section | Completion
b894fd15-4591-5de3-8256-45a1e534edc3 | checkpoint | Works completed to specification/drawings - Attach photos of work below
e8ee2502-d6b5-5081-aee6-a70e0d39c72b | note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
f46232f3-f028-5cd9-91ed-89c80964b0f3 | button | Area left clean & tidy | Yes, No
1aa5ca8e-5a39-5e16-b97f-407b5536fad3 | tickbox | Leemark Sign-Off
1d791761-cca4-5e58-9384-f6da145828f3 | tickbox | Builder Sign-Off
dd71b766-5bfd-5126-8e81-631da7396226 | signoff | Sign-Off - click to Add signature(s)
e7d72730-3100-5749-a7c1-d45a8b40431f | checklist | LM-FOR-40-ITR-302.3 Hose Reel Installation |  | LM-FOR-40-ITR-302.3 Hose Reel Installation
e8adbc84-b448-5119-bc35-7edd8200d05f | section | Installation
d43163db-8f22-5249-9081-91480c3ed8d4 | checkpoint | Latest consented drawings checked & referenced
beccd307-5e64-513d-be22-d0a82afd43dc | textbox | Drawing & Revision #
49527502-66c4-546d-9c79-451c625cf136 | tickbox | Area clear, tidy and accessible
c2d3e043-8b0c-5267-8263-c0b31080a3c9 | note | Attach Photos/Comments below if any issues & send report to Builder
4a7e9c81-d300-59ac-9cec-217ca7855fa3 | textbox | Hose Reel No.
0a0ba801-62d8-5411-8fd2-e62b89ec489a | checkpoint | Hose Reel supply pipe works completely installed of correct size, position, elevation, alignment and adequately supported in accordance with approved drawing/plans
9a560a4c-13d4-5f50-8c39-47261e5490df | checkpoint | Hydrostatic pressure testing of installed pipe works completed and accepted
019a9076-e1ad-5356-adf7-563652796e3d | checkpoint | Hose Reel and associated valves, pipes and fitting used are in accordance with the approved specifications and applicable codes/standards
68e507bf-ead5-560b-a688-7603bb25521f | checkpoint | Hose Reel located along normal path of travel to nearest exit and readily accessible
eb9f5050-c8de-532d-9dc5-da6b70ff4a7a | checkpoint | Verify and confirm hose length to be 36-metres or 40-meters
45451fa0-1bf7-53f4-b8ed-6b06940972f8 | checkpoint | Hose reel spindle is 1400 mm minimum to 2400 mm maximum above floor level. Stop valve is 1000 + 100 mm above floor level
a1e04f8e-49bc-56f2-ac27-9b0ad786e687 | checkpoint | Minimum radial clearance of 100 mm between the reel rim and cabinet/cavity to the sides, above and below
94b42990-a21a-5f54-8bb2-a971b1a32857 | checkpoint | Minimum 100 mm clearance around the stop valve handwheel/handle
7ad936be-f917-5485-bca1-b98389e38723 | checkpoint | Any defects found on the hose reel assembly have been corrected
d80d130d-72f8-5fc9-872b-1fc379f43b15 | section | Completion
b894fd15-4591-5de3-8256-45a1e534edc3 | checkpoint | Works completed to specification/drawings - Attach photos of work below
035dd4b7-8868-5e99-b7a2-54d67698db42 | note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
6cd0001c-b2a8-5178-a18e-3265737fef86 | button | Area left clean & tidy | Yes, No
33ead7f9-a7d2-5d55-aba7-4def99bf4178 | tickbox | Leemark Sign-Off
0b2f874e-953f-58eb-897c-e3c6e5e8aa51 | tickbox | Builder Sign-Off
dd71b766-5bfd-5126-8e81-631da7396226 | signoff | Sign-Off - click to Add signature(s)
a8e869a8-f63b-54d5-92b5-69038a63db49 | checklist | LM-FOR-40-ITR-302.4 Tank Installation |  | LM-FOR-40-ITR-302.4 Tank Installation
e8adbc84-b448-5119-bc35-7edd8200d05f | section | Installation
d43163db-8f22-5249-9081-91480c3ed8d4 | checkpoint | Latest consented drawings checked & referenced
ea817d6c-8a94-55fb-9d58-bec16ba87ffa | textbox | Drawing & Revision #
35172532-b69f-529b-bc37-ae4cdabb36b3 | tickbox | Area clear, tidy and accessible
605a0c9c-5bcd-50c4-9584-4c70b57d1396 | note | Attach Photos/Comments below if any issues & send report to Builder
fd3c03e9-fc9a-5a78-9d70-10f7a48db3a8 | checkpoint | Tank installation/construction is completed including associated pipe works in accordance with the approved drawing/plan
9516e73f-5ad4-48d5-b797-5c40669367c0 | checkpoint | Ensure internal tie-rods are tensioned correctly before tank is sealed
0c60debb-dde2-5cd9-aca8-f8b2b5656bfb | tickbox | Builder Sign-Off
39198f89-8b94-5dce-9d1a-e8c9c5d50920 | checkpoint | Tank is free from dents, buckling, cracks, and internal is clean and free of any debris and construction materials
1d16e36f-f44c-54d7-9d9d-ffe52085a008 | checkpoint | Tank internal liner (if provided) is complete and properly bonded to tank wall/shell
8cd4155e-ef4f-5846-8b78-34a58067c6f9 | checkpoint | Tank quick infill line including associated infill valve and isolation valve installed and adequately supported
d80b7b8b-af10-50bc-b571-884c1f5277b8 | checkpoint | Tank suction isolation valve is fitted in the correct position and operational in accordance with the approved drawing/plan
0a825d98-eb7f-5f1d-af42-a304a6dbad6b | checkpoint | Tank suction vortex inhibitor is fitted in the correct position and elevation in accordance with the approved drawing/plan
5812f02d-de35-5c01-b99d-30c3acd9fc37 | checkpoint | Tank overflow is fitted in the correct position, elevation and properly piped to drain Adequate drain available
c9b6905d-5eb3-5b7b-a8fc-8585fbea4849 | checkpoint | Tank drain/sludge isolation valve is fitted and blank off
989ad281-8267-525f-99fe-cbcfb81b1cd1 | checkpoint | Tank external water level indicator is fitted and operational
1f0fb308-8ece-5553-98d5-c95bdbf13241 | checkpoint | Tank internal and external access ladders are fitted & secured
5b3e6fc0-2162-593c-b068-78802c90d062 | checkpoint | Tank access hatch is fitted and provided with lockable cover
2ecb7980-f135-5426-bb2d-9334db848cab | checkpoint | Ball float for infill pilot line is fixed tightly, close to the manhole and away from the discharge path of tank infill
59469748-c96a-5fdc-ade7-8862fbc201cf | checkpoint | Tank is located with minimum of 600 mm clearance around tank perimeter and roof line
5087ccac-6285-40d6-b793-f9d5668955c5 | checkpoint | Filling of Tank with water. John Holland approval required before proceeding to fill
e6310e1a-feb4-5bb7-ac50-c67fc2b46efb | tickbox | Builder Sign-Off
d80d130d-72f8-5fc9-872b-1fc379f43b15 | section | Completion
b894fd15-4591-5de3-8256-45a1e534edc3 | checkpoint | Works completed to specification/drawings - Attach photos of work below
b60f143d-c07a-5068-bfed-9b4f46e59220 | note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
86c85bff-be0a-5094-a846-d2864f35143b | button | Area left clean & tidy | Yes, No
04a330a0-9f27-5ae7-8f8b-a8377944ebb2 | tickbox | Leemark Sign-Off
9d3b327b-b68f-5c5d-bea4-c1703bf409ca | tickbox | Builder Sign-Off
dd71b766-5bfd-5126-8e81-631da7396226 | signoff | Sign-Off - click to Add signature(s)
3db67214-93e1-527a-b7c0-a771d58f5b8b | checklist | LM-FOR-40-ITR-302.5 Booster Assembly |  | LM-FOR-40-ITR-302.5 Booster Assembly
e8adbc84-b448-5119-bc35-7edd8200d05f | section | Installation
d43163db-8f22-5249-9081-91480c3ed8d4 | checkpoint | Latest consented drawings checked & referenced
02a046fc-2268-5eab-b905-10f082b2855d | textbox | Drawing & Revision #
4e595ccf-9bee-588e-bb0e-8c0ed5e1ff50 | tickbox | Area clear, tidy and accessible
cb69792d-9f95-51f4-9e24-c1885692a9a7 | note | Attach Photos/Comments below if any issues & send report to Builder
02330769-6dc6-56ab-abee-4c0c7f30c5a2 | checkpoint | All pipework are installed in the correct position and alignment in accordance with the approved drawing/plan
aa9af366-5ef8-5499-b32b-bfeabd0bbea3 | checkpoint | All pipework have been pressure tested and accepted in accordance to approved pressure testing procedure
726e5cc5-80bb-5e9b-a416-d061faecc85f | checkpoint | Fire Brigade Booster is located within sight of the main entrance to the building
49217c89-1ea9-51b9-a67e-a30c75031e08 | checkpoint | Concrete plinth provided for the booster location and hard stand for fire brigade pumping appliance
61a42766-6df9-5712-9344-ff5c15123e63 | checkpoint | Feed Hydrant is located within 8 metres from fire brigade appliance hard stand
281e6307-2396-5dd0-bfd7-37210533bc0a | checkpoint | Fire water storage tank suction point (Storz) is located within 4 metres from fire brigade appliance hard stand
b63456b9-9fdf-5eac-b80b-25eab8b6594e | checkpoint | Fire water storage tank suction point (Storz) is located within 10 metres from fire brigade booster inlet connection
42aab1ba-eb65-5840-8436-517c6a0f7946 | checkpoint | Centre distance between feed hydrant and booster inlet connection is 450 mm minimum and 5 m maximum
0d493d1c-a6ea-5a1b-9e30-357e76e04117 | checkpoint | The height of Feed Hydrant Outlet and Booster Inlet Connection is minimum 750 mm and maximum 1200 mm from FFL
93f6c0ce-d88a-5025-9fce-0e142eead985 | checkpoint | Valves face minimum 150-mm from door and valve handles are 100-mm from cabinet sides
a65cceaa-58ba-53c7-a0f0-a3b3f7f7b3b4 | checkpoint | The number of feed hydrant outlet installed is equal to number of fire brigade booster assembly inlets
ee65e64e-5dfb-5516-ada4-59fab3844e8c | checkpoint | The required number of fire brigade booster inlets installed is suitable for the system requirement or minimum of 2 inlets
dcc370b8-0c61-5341-8bb9-f98a73fa294b | checkpoint | Full flow non-return valve of correct size is installed in the proper location
e25ef715-9194-53ea-8a9f-c560ccb14a2b | checkpoint | Approved type of cabinet enclosure is installed as required
d80d130d-72f8-5fc9-872b-1fc379f43b15 | section | Completion
b894fd15-4591-5de3-8256-45a1e534edc3 | checkpoint | Works completed to specification/drawings - Attach photos of work below
10d7b352-bdb3-51b8-82a9-a3efcadb8304 | note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
64cd79a9-19e8-5205-823a-a11b45096632 | button | Area left clean & tidy | Yes, No
35f5e669-b281-5bc1-b50d-5d6b277d2ff5 | tickbox | Leemark Sign-Off
dd5863b3-a96d-5963-8841-ad56e58cb9ca | tickbox | Builder Sign-Off
dd71b766-5bfd-5126-8e81-631da7396226 | signoff | Sign-Off - click to Add signature(s)
f293e514-7a7b-5f96-95c0-e301f1a1d78e | checklist | LM-FOR-50-ITR- 303.5 Fire Detection Fit Off (V160421) |  | LM-FOR-50-ITR- 303.5 Fire Detection Fit Off (V160421)
11ea1445-3c9d-5c50-9466-57b90f1ad9ec | section | Fit-Off
d43163db-8f22-5249-9081-91480c3ed8d4 | checkpoint | Latest consented drawings checked & referenced
4c9fe21e-c8ba-51af-a6b6-ac181799e0a2 | textbox | Drawing & Revision #
65489623-1de5-5a61-b65d-4e5e2e58ed84 | tickbox | Area clear, tidy and accessible
0ffeb54d-9e4b-5f30-aaf6-741352a3a878 | note | Attach Photos/Comments below if any issues & send report to Builder
d2aa0f2e-43f6-531a-a774-441d8c7d5b0c | checkpoint | Have all devices been installed in the correct position with no obstructions
7849beb6-b62b-56d7-8bdb-e34ef1d29a87 | checkpoint | Have all detectors been installed in the correct position and addressed
0a27b38e-4a4b-5422-aeda-ebb518ba0022 | checkpoint | Have all input/output modules been installed in the correct position and addressed, with all enclosures sealed
0b00d4e3-f653-5293-a0c8-12c57a4ccbbe | checkpoint | Have all magnetic door holders been installed correctly
25b3ee31-4380-5497-98c2-84ec231124a4 | checkpoint | Have all input/output devices been installed and addressed for security fire trips
48d381f9-eb27-5d96-bbfe-8a8da3ed02cc | checkpoint | Have all input/output devices been installed and addressed for mechanical fire trips
376ff4bf-42c5-59ae-aec8-1c0c54773056 | checkpoint | Have all input/output devices been installed and addressed for AS 1668 Fan Controls
24165e3c-6978-5591-b18f-e7826ede5624 | checkpoint | Have the ELV and LV segregation rules been applied as per AS/CAS 009 (including 90 degrees crossovers) – Double check to make sure no other trades have been in after fireworks
c1003bbd-6a75-56c3-b9d5-c3b1d211f0c7 | checkpoint | Have all cables and conduits been installed in the correct position for devices
6b59f6dc-3f60-599c-8a5a-6af5e10ee3fd | checkpoint | Have all devices been terminated for testing purposes
ec30b90e-7ee3-512c-b0ee-d309d137d2bf | section | Cable Feeds
5312575f-67ec-51e1-b91b-9d9965176552 | checkpoint | Have all cable feeds been connected to the first device
daad72c8-62e2-5ce3-b6e1-c487f697af88 | checkpoint | Have all cable feeds been connected to the last device
e243cc04-4750-5916-99bf-48d2e0581a61 | checkpoint | Have cable feeds been connected at the panel
11b3a826-b908-5473-b2f4-a4da7f1b23f4 | section | Visual Check
3d92684e-b9fd-540d-91ca-14d8649f0c47 | checkpoint | Check that no other services are run with or attached to fire detection cables
849a0bf2-9aee-5c6e-b51d-d949c1684357 | checkpoint | Check that no cables have been damaged
c7074107-d9be-5908-bfe2-d39aa6f19ad7 | checkpoint | Check that all final cable locations are correct and match up with the “For Construction Drawings” and “Reflected Ceiling Plans”
12fedbea-0cf1-5f72-bf6a-a716357aa06c | checkpoint | Check that all address tags and labels are clear and readable
730b71db-d281-5daa-b636-6470c0180bc8 | checkpoint | Have devices and address been noted on “As Constructed Drawings” for handover
43a7ec54-bb62-5908-be77-3bc83a24d443 | checkpoint | Have all stickers been installed to fire rated walls and smoke walls for penetrations
144fcaec-399f-590d-bb2b-670302d87a4e | checkpoint | Has photographic evidence been taken and recorded for all penetrations?
d80d130d-72f8-5fc9-872b-1fc379f43b15 | section | Completion
b894fd15-4591-5de3-8256-45a1e534edc3 | checkpoint | Works completed to specification/drawings - Attach photos of work below
8927abec-dd91-51be-8d95-92d6633174a5 | note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
ed02e78a-5e03-529f-ac61-96cabc61772c | button | Area left clean & tidy | Yes, No
961fc0c9-7527-55f3-b631-774419ecc963 | tickbox | Leemark Sign-Off
5c2fcbcb-a73c-53ba-897e-4bc87e64137e | tickbox | Builder Sign-Off
dd71b766-5bfd-5126-8e81-631da7396226 | signoff | Sign-Off - click to Add signature(s)
bfacae64-88d5-537e-9c08-4ce30324bf67 | checklist | LM-FOR-50-ITR-303.1 Fire Panel Installation |  | LM-FOR-50-ITR-303.1 Fire Panel Installation
907e5889-d4f6-5070-8f08-309d964bd6f3 | section | Fire Indicator Panel
d43163db-8f22-5249-9081-91480c3ed8d4 | checkpoint | Latest consented drawings checked & referenced
2b520512-a6b4-5c00-86bf-eb1126185f22 | textbox | Drawing & Revision #
c882904c-e04d-50e0-8064-46401f748fc4 | tickbox | Area clear, tidy and accessible
23de8cb7-b93c-59b1-a97c-deecddf48499 | note | Attach Photos/Comments below if any issues & send report to Builder
b2321c59-c4ab-5204-9f78-925a10f24437 | checkpoint | Are visual indicators and controls not less than 750 mm from the floor
8d9420f8-3f4a-52bb-bdee-e37e86968544 | checkpoint | Are visual indicators and controls not more than 1850 mm from the floor
f3414b2e-0611-5d3e-9aa6-a71d36094086 | checkpoint | Connected to Brigade - Is the fire indicator panel clearly visible and readily accessible within the designated building entry point or the fire control room
fe2377a1-3943-57e2-9c4c-5a62fc52b9fc | checkpoint | Not Connected to Brigade - Is the fire indicator panel in a secure location and clearly visible and readily accessible to authorized personnel
8778cc5a-77c4-534d-b2b8-78002ad04a20 | section | Accessibility
b93d4820-97ae-59f3-854d-2f2d38652b82 | checkpoint | Is the fire indicator panel obscured by a door (if No, continue to CLEARANCE)
603a7921-9d56-5fd1-834d-a1bbf9d9090b | checkpoint | Is the door marked in a contrasting colour to the general colour scheme with the words “FIRE PANEL” in letters not less than 50mm high
6b200959-ed86-545f-893a-fe58a320bfb7 | checkpoint | Is the door absent of locks
09d7dc5b-fcb7-5c6c-b5e4-177e55cc4984 | checkpoint | Where the door reduces the CIE sounder sound level below the CIE requirement, means are provided to give the required sound level outside the covering door
5c079a8f-4a71-5459-bdc7-971bf932c608 | checkpoint | A minimum clearance is maintained from the enclosure as shown
00b38fe1-76e5-5bb7-9e80-36cd52f57442 | section | Power sources
9a9de1ef-07c7-57e4-a9f2-4a335f4e5ed0 | checkpoint | Is the battery enclosure located such that the batteries are readily accessible for inspection
3dd2c6ae-db7f-5bbb-a4c6-245bdd6d0b51 | checkpoint | Are the connecting leads to the battery clearly labelled to reduce the possibility of reverse connections to the battery
dc9739e5-17ee-51bd-8761-52ccef9a06a6 | checkpoint | The battery is not be tapped for intermediate voltages
6202645d-663b-5604-8467-362363fa59d9 | checkpoint | All connections are made using suitable connectors
2519d09b-5217-5412-9e48-c50fa10b6235 | section | Sub-Indicator Panels
8c5d1c3c-3915-54b2-8798-6cfcc3a10f35 | checkpoint | The SIP shall only serve areas on one level of a building unless - Pass once below considered
07f2ffb0-9149-5c18-978d-b55585b22705 | button | (a) The SIP serves the entire building | Yes, No, N/A
2d153f4b-45d2-549d-8158-6bc4c73c36e8 | button | (b) All zones connected to the SIP are readily accessible without leaving the area served by the SIP; or | Yes, No, N/A
809fd165-f75d-5ee4-8f2a-b417191b2f91 | button | (c) The location of each zone in alarm at the SIP can be identified at the designated building entry point | Yes, No, N/A
7913de1a-136c-503a-b07a-7b31b9f0a4a0 | button | Where the SIP serves the entire building, it shall be installed in accordance with the requirements for an FIP | Yes, No, N/A
3f7f4242-80d9-5e64-973e-12d50af04109 | button | If the SIP serves a specific area, is it located at the main point of entry into that area | Yes, No, N/A
2423cd6a-ced2-52e0-9dce-335ce826af4a | section | Wiring
bbf5f778-c421-5bbc-b8d4-c1512f178773 | checkpoint | The extra low voltage wiring of the fire detection and alarm system is be kept separate and distinct from all other systems
5155e46d-ede8-583f-a8b8-11b412557c82 | checkpoint | The extra low voltage wiring of the fire detection and alarm system is installed in accordance with the requirements of AS/ACIF S009
51be89ab-4777-5453-bb75-8652f1759edd | checkpoint | Other wiring is installed in accordance with the electrical safety requirements of AS/NZS
c95c3c84-0a8d-552c-b50c-6d3b7fb0e33d | checkpoint | Externally energized circuits at voltages in excess of extra low voltage, except the power source for CIE, do not enter any CIE enclosure
d80d130d-72f8-5fc9-872b-1fc379f43b15 | section | Completion
b894fd15-4591-5de3-8256-45a1e534edc3 | checkpoint | Works completed to specification/drawings - Attach photos of work below
ea0acfe0-0620-50fe-8edc-8e27a4361378 | note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
b7a2f552-c7ba-5013-ba95-948a2c20ae9f | button | Area left clean & tidy | Yes, No
d41a53f0-de19-5968-b69d-a214bfbc698e | tickbox | Leemark Sign-Off
ed2c61f9-ebb2-53a6-ac24-4f9cef3ba6ab | tickbox | Builder Sign-Off
dd71b766-5bfd-5126-8e81-631da7396226 | signoff | Sign-Off - click to Add signature(s)
f2d7a84d-769d-51b7-8b87-74be5d7004eb | checklist | LM-FOR-50-ITR-303.2 Ewis Installation |  | LM-FOR-50-ITR-303.2 Ewis Installation
a1596c2a-5d45-5fea-8352-c94c52f08b6b | section | Cabling
d43163db-8f22-5249-9081-91480c3ed8d4 | checkpoint | Latest consented drawings checked & referenced
d784685c-39ef-5104-88b6-ee81f8727f95 | textbox | Drawing & Revision #
343f4623-c336-5e9d-bf30-0ebe50f11381 | tickbox | Area clear, tidy and accessible
88c8164b-14ff-5561-929b-c17b67f13306 | note | Attach Photos/Comments below if any issues & send report to Builder
9ae80a36-2d4e-54c1-a46a-2270b153ec8e | checkpoint | Have all cable supports been installed in the correct position with no obstructions
dd05b8ac-5e35-591c-ba53-1546ab3c9f01 | checkpoint | Have all cables been cable tied to soffit / catenary wire with no sagging or obstructions
576269da-5339-5bd6-8d11-bd6c9fad8bde | checkpoint | Have all cables been installed for speakers and horns
b983e950-b9a4-54e2-9968-d7007648de8b | checkpoint | Have all cables been installed for warden intercom points
32d23c76-d73f-5725-b9b7-1a0069b09a43 | checkpoint | Have all cables been installed for emergency call points
d12335ee-1558-537f-a0ac-e43c85b928ef | checkpoint | Have all cables been installed for strobes
489271ce-8c44-5dd2-8849-71672f2419d9 | checkpoint | Have all cables been installed for background music inputs
7b5002de-2316-53a9-bebf-5feac5a1a764 | checkpoint | Have all cables been installed for microphone inputs
7785cce1-a604-5189-8a9d-226566584938 | checkpoint | Have the ELV and LV segregation rules been applied as per AS/CAS 009 (including 90 degrees crossovers)
48a40f21-0cd7-58de-9e97-f9fe7aa07773 | checkpoint | Have all cables been installed in the correct position for devices
944335ec-5d96-54bc-a05c-fae87484f55b | checkpoint | Have all cables been joined through for testing purposes or fitted with end of line devices
ec30b90e-7ee3-512c-b0ee-d309d137d2bf | section | Cable Feeds
f7a826fc-d3da-4a0e-8286-87140a2b2662 | checkpoint | Have all cable supports been installed in the correct position with no obstructions
50fb123c-916f-546a-9f79-05b976d719eb | checkpoint | Have all cable feeds been installed in the correct position
a9146f1f-94df-594d-89fa-8117510750cb | checkpoint | Have all cables been tied to cable tray with steel ties with no sagging or obstructions
de05cfd0-93f4-5afe-9e3a-2d6ed7a50015 | checkpoint | Have all cable trays been installed correctly and secured including joiners and bends
37bd51dd-4cd7-5fc5-bff3-96fa0d81631b | checkpoint | Have the modified cable trays been re-galvanized
11b3a826-b908-5473-b2f4-a4da7f1b23f4 | section | Visual Check
d2c93664-6131-5454-9f1d-51eec9232fd2 | checkpoint | Check that no other services are run with or attached to occupant/emergency warning cables
849a0bf2-9aee-5c6e-b51d-d949c1684357 | checkpoint | Check that no cables have been damaged
c7074107-d9be-5908-bfe2-d39aa6f19ad7 | checkpoint | Check that all final cable locations are correct and match up with the “For Construction Drawings” and “Reflected Ceiling Plans”
8d76a686-6c75-530c-844e-0daf6b45458b | checkpoint | Have all cable runs, cable trays and penetrations been mark on “As Constructed Drawings” for handover
43a7ec54-bb62-5908-be77-3bc83a24d443 | checkpoint | Have all stickers been installed to fire rated walls and smoke walls for penetrations
b41d9cc1-5fe2-5955-9af8-f7b4eeb59fe6 | checkpoint | Has photographic evidence been taken and recorded for all penetrations
d80d130d-72f8-5fc9-872b-1fc379f43b15 | section | Completion
b894fd15-4591-5de3-8256-45a1e534edc3 | checkpoint | Works completed to specification/drawings - Attach photos of work below
cf64f9ab-f4da-5cc9-8a3a-a1e77ba9815d | note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
1c403649-4c9c-56ea-9f38-d9abe926b57f | button | Area left clean & tidy | Yes, No
38e89389-e703-5b74-b9c0-385a42d4009c | tickbox | Leemark Sign-Off
c074a16e-fd4d-5562-b567-7f2d94d90e09 | tickbox | Builder Sign-Off
dd71b766-5bfd-5126-8e81-631da7396226 | signoff | Sign-Off - click to Add signature(s)
c0da6b68-75f3-51fc-8e44-6142868a5e44 | checklist | LM-FOR-50-ITR-303.3 Ewis Installation Fit Off |  | LM-FOR-50-ITR-303.3 Ewis Installation Fit Off
1603ca4e-b1fc-5389-a8d3-ea92f6a40b0d | section | EWIS Fit-Off
d43163db-8f22-5249-9081-91480c3ed8d4 | checkpoint | Latest consented drawings checked & referenced
0f762fc6-3578-589f-8764-0de9f526d416 | textbox | Drawing & Revision #
8b39662d-2ae1-5410-acad-8f11626a3716 | tickbox | Area clear, tidy and accessible
145487e6-0f19-57a4-8844-42ea0e1128f0 | note | Attach Photos/Comments below if any issues & send report to Builder
d2aa0f2e-43f6-531a-a774-441d8c7d5b0c | checkpoint | Have all devices been installed in the correct position with no obstructions
49454916-dea8-5435-9c54-d3793e3e3880 | checkpoint | Have all speakers / horns been installed in the correct location
8d97f643-5fa6-5d93-b000-ab1b709f3ed2 | checkpoint | Have all warden intercom points been installed in the correct location
1156b0a2-bbaa-5ea9-9a27-df75c1972106 | checkpoint | Have all emergency call points been installed in the correct location
8aad9d8f-484a-54f2-95cc-dc7f0b25f183 | checkpoint | Have all strobes been installed in the correct location
c8fd860e-f16b-5059-a3ef-427095de55c1 | checkpoint | Have all background music points been installed in the correct location
d338d7dd-107d-50c0-8d81-c2244cef04c3 | checkpoint | Have all microphone points been installed in the correct location
d90bbf6d-30e1-520c-981c-fdd1d78ab0ff | checkpoint | Have the ELV and LV segregation rules been applied as per AS/CAS 009 (including 90 degrees crossovers) – Double check to make sure no other trades have been in after warning system works
c1003bbd-6a75-56c3-b9d5-c3b1d211f0c7 | checkpoint | Have all cables and conduits been installed in the correct position for devices
6b59f6dc-3f60-599c-8a5a-6af5e10ee3fd | checkpoint | Have all devices been terminated for testing purposes
ec30b90e-7ee3-512c-b0ee-d309d137d2bf | section | Cable Feeds
6c6c5aba-aa62-5851-a7e1-afb729a0e67d | checkpoint | Have all cable supports been connected to the first device
7108a3c5-6748-54e7-b97d-b9fb83890383 | checkpoint | Have all end of lines been fitted and measured
7314b1f3-cb17-5760-84ea-7f6e7620ed65 | checkpoint | Have cables feeds been connected at the panel
11b3a826-b908-5473-b2f4-a4da7f1b23f4 | section | Visual Check
57ec8c66-0fd8-5ebd-9ce2-594ae0f23d7e | checkpoint | Check that no other services are run with or attached to occupant/emergency warning cables or devices
512764d8-a9cd-58a4-ae76-7f62f8ee5bf5 | checkpoint | Check that no cables or devices have been damaged
b050a0a7-1d6c-59df-9dd9-081a9dbf747e | checkpoint | Check that all final device locations are correct and match up with the “For Construction Drawings” and “Reflected Ceiling Plans”
719283c7-1c69-556c-a110-0b13c0c30c98 | checkpoint | Have devices and readings been noted on “As Constructed Drawings” for handover
43a7ec54-bb62-5908-be77-3bc83a24d443 | checkpoint | Have all stickers been installed to fire rated walls and smoke walls for penetrations
b41d9cc1-5fe2-5955-9af8-f7b4eeb59fe6 | checkpoint | Has photographic evidence been taken and recorded for all penetrations
d80d130d-72f8-5fc9-872b-1fc379f43b15 | section | Completion
b894fd15-4591-5de3-8256-45a1e534edc3 | checkpoint | Works completed to specification/drawings - Attach photos of work below
defdd847-4fe4-51a5-ab02-274e6763d8e1 | note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
8e906a06-a652-52e6-949c-7a3ddedaabe6 | button | Area left clean & tidy | Yes, No
0aeab7df-3e66-58aa-86e0-452b73cc1600 | tickbox | Leemark Sign-Off
cf6a6f08-f545-50a7-9b27-f51c35aea053 | tickbox | Builder Sign-Off
dd71b766-5bfd-5126-8e81-631da7396226 | signoff | Sign-Off - click to Add signature(s)
044fca69-df27-5986-8afb-d71bcff6e9cd | checklist | LM-FOR-50-ITR-303.4 Fire Detection Installation |  | LM-FOR-50-ITR-303.4 Fire Detection Installation
a1596c2a-5d45-5fea-8352-c94c52f08b6b | section | Cabling
d43163db-8f22-5249-9081-91480c3ed8d4 | checkpoint | Latest consented drawings checked & referenced
3489af05-1e7a-5ba7-a45e-4074fffe8913 | textbox | Drawing & Revision #
1b45522f-d8dd-55eb-9f03-723b3a6beceb | tickbox | Area clear, tidy and accessible
4134f3c9-86e9-50fb-a08f-0a350a67c10e | note | Attach Photos/Comments below if any issues & send report to Builder
9ae80a36-2d4e-54c1-a46a-2270b153ec8e | checkpoint | Have all cable supports been installed in the correct position with no obstructions
dd05b8ac-5e35-591c-ba53-1546ab3c9f01 | checkpoint | Have all cables been cable tied to soffit / catenary wire with no sagging or obstructions
f1cc51c1-5ace-589a-b9cd-e2a7d32e0bad | checkpoint | Have all cables been installed for detectors
e498690d-2701-5875-afba-45c850fd5e47 | checkpoint | Have all cables been installed for sprinkler valve sets
182aa0f2-1865-5629-810f-7389c5423658 | checkpoint | Have all cables been installed for magnetic door holders
d82d35a9-5e19-505b-96ba-06c2e146d102 | checkpoint | Have all cables been installed for security fire trips
2a24e8bb-29e0-5023-9a8f-ce2b1078570d | checkpoint | Have all cables been installed for mechanical fire trips
a7b9db13-b98b-5ef5-9f16-37a897216052 | checkpoint | Have all cables been installed for AS 1668 Fan Controls
7785cce1-a604-5189-8a9d-226566584938 | checkpoint | Have the ELV and LV segregation rules been applied as per AS/CAS 009 (including 90 degrees crossovers)
48a40f21-0cd7-58de-9e97-f9fe7aa07773 | checkpoint | Have all cables been installed in the correct position for devices
ef96019f-6f43-5802-b017-28ac674d2115 | checkpoint | Have all cables been joined through for testing purposes
ec30b90e-7ee3-512c-b0ee-d309d137d2bf | section | Cable Feeds
5e531e01-e875-4033-92ee-40219338cadc | checkpoint | Have all cable supports been installed in the correct position with no obstructions
50fb123c-916f-546a-9f79-05b976d719eb | checkpoint | Have all cable feeds been installed in the correct position
a9146f1f-94df-594d-89fa-8117510750cb | checkpoint | Have all cables been tied to cable tray with steel ties with no sagging or obstructions
de05cfd0-93f4-5afe-9e3a-2d6ed7a50015 | checkpoint | Have all cable trays been installed correctly and secured including joiners and bends
37bd51dd-4cd7-5fc5-bff3-96fa0d81631b | checkpoint | Have the modified cable trays been re-galvanized
11b3a826-b908-5473-b2f4-a4da7f1b23f4 | section | Visual Check
3d92684e-b9fd-540d-91ca-14d8649f0c47 | checkpoint | Check that no other services are run with or attached to fire detection cables
849a0bf2-9aee-5c6e-b51d-d949c1684357 | checkpoint | Check that no cables have been damaged
c7074107-d9be-5908-bfe2-d39aa6f19ad7 | checkpoint | Check that all final cable locations are correct and match up with the “For Construction Drawings” and “Reflected Ceiling Plans”
8d76a686-6c75-530c-844e-0daf6b45458b | checkpoint | Have all cable runs, cable trays and penetrations been mark on “As Constructed Drawings” for handover
43a7ec54-bb62-5908-be77-3bc83a24d443 | checkpoint | Have all stickers been installed to fire rated walls and smoke walls for penetrations
144fcaec-399f-590d-bb2b-670302d87a4e | checkpoint | Has photographic evidence been taken and recorded for all penetrations?
d80d130d-72f8-5fc9-872b-1fc379f43b15 | section | Completion
b894fd15-4591-5de3-8256-45a1e534edc3 | checkpoint | Works completed to specification/drawings - Attach photos of work below
17c08620-0641-5aa8-b682-e77d5db03c9f | note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
19db9ac1-7b5a-5a08-861f-66ae374bcd8b | button | Area left clean & tidy | Yes, No
b14b24a8-74f5-589a-a49f-724059ce7686 | tickbox | Leemark Sign-Off
d7b910e2-eb4e-52fc-9651-24c79ef8b414 | tickbox | Builder Sign-Off
dd71b766-5bfd-5126-8e81-631da7396226 | signoff | Sign-Off - click to Add signature(s)
f67d854e-6083-5ad9-83e7-a97cae83ad78 | checklist | LM-FOR-50-ITR-303.7 ASD (Aspirated) installation |  | LM-FOR-50-ITR-303.7 ASD (Aspirated) installation
5ba107c9-f94a-566f-baf5-67fd8dd253df | section | ITR Pre Commissioning Procedures (1)
95c1df9a-4e32-5b01-aa62-05c4d1548126 | checkpoint | Pre Commissioning Procedures
a721100d-feb7-52d6-9a33-dd60ad1c919c | button | Check the location of installation is as per approved shop drawings and manufactures recommendations | Yes, No, N/A
1228415a-6ec5-57b0-b567-077b3622c449 | button | Check the Height of Panel is as per manufactures recommendations and in accordance with the relevant Australian Standards | Yes, No, N/A
a90b3e8d-54e3-5857-923e-091e87520d7b | button | Confirm operation of auto-reset from FIP is wired through GP relay | Yes, No, N/A
e97ea414-b130-530b-98fb-6303810c2527 | button | Check all wiring connections are tight and secure | Yes, No, N/A
9a11b365-e2cd-5fdb-be76-681782321415 | button | Check routing of the conduits are as per approved shop Dwg’s | Yes, No, N/A
068655d9-eb4c-5295-ab40-cfbb564ff45a | button | Check joints are properly glued /sealed and bonded to eliminate any potential air leaks | Yes, No, N/A
192d0645-d4ec-50b0-8ac8-72425b2fd671 | button | Check pipe joints at the inlet ports of the scanner are not glued but firmly fitted into air inlet socket to ensure there is no potential air leaks | Yes, No, N/A
ef0c3400-fa7c-5b97-b8a5-ad0c3c9abe6f | button | Check the sensing holes are drilled as per design | Yes, No, N/A
0e9c5d1a-5704-559e-8289-0cb3a3fc58d4 | button | Confirm the exhaust has been routed back into the sampling space | Yes, No, N/A
64828f37-d819-5f23-a8a5-c7f91a5dff98 | button | Confirm end caps have been installed un-glued to all pipes at a serviceable height and location | Yes, No, N/A
aa43c225-2faf-5fcb-a87d-bf05e6570793 | button | Confirm wiring is complete to Action, Minor Urgent, Fault & Fire relays and monitored via the FIP/SHDCIE. | Yes, No, N/A
cd74642b-3a3c-5279-a533-6c67f42bf91b | section | ITR Pre Commissioning Procedures (2)
af58fde6-eb86-4590-b9a0-561ac12a6fe5 | checkpoint | Pre Commissioning Procedures
006a92b6-5e14-52f3-8e4a-04e0cd8df13e | button | Power up the system, the aspirator starts up and air is flowing out of exhaust port , LCD screen is operational. | Yes, No, N/A
2fdf6551-88bb-544d-8cd8-6fd74e0bb45b | button | Induce smoke into the furthest sampling point from the head end unit | Yes, No, N/A
651463bb-5375-591d-804f-dfd0ab9e8e32 | button | Check that a Fire signal is being transmitted to the FIP within 60s of smoke entering the VESDA pipe | Yes, No, N/A
42fdb065-f267-5759-b060-cb2a56f37f89 | button | Check the correct signals are being transmitted to the FIP via Action, Minor Urgent & Fire Relays correctly. | Yes, No, N/A
2a148fdc-0ee4-50ce-9e22-bbee5d2060cf | button | Remove the power from the VESDA and confirm Fault is received at the FIP | Yes, No, N/A
94616ee1-e4be-5e55-83f1-5da5c317dc56 | button | Check the fire signal is conveyed to the fire Alarm system and BMS, if required | Yes, No, N/A
df0438e5-263c-50d5-92c7-c447fb0e9bff | button | Check the transmission of signals to operate ancillary devices, if required. | Yes, No, N/A
73ec3508-d376-5de6-bc4b-7e079ee3066e | button | Record all baseline data as required. | Yes, No, N/A
4500885f-e2e0-56bf-b4df-ec4f5585071a | checklist | SYS - Sprinkler & Hydrant Hydrostatic Test |  | Sprinkler & Hydrant Hydrostatic Test
92773c79-21d7-53d1-87b7-e42ea3f7d786 | section | Guidelines
37f6445d-78dc-50c9-9d24-ef8faffb8fcf | checkpoint | Guidelines understood - Pass once read
a4c68d39-4aa1-502d-8720-0028fa1b9a7a | note | Guidelines: Fire Sprinkler Systems – 1400kPa or 400kPa above the maximum static pressure for a duration of 2 hours (Check notes on Construction Drawing for nominated test pressure)
2557f4ff-a9c5-5837-b5f0-f6ab3de565fb | note | Fire Hydrant Systems (Low Rise) – 1700kPa or 15 times the design pressure for a duration of 2 hours (Check notes on Construction Drawing for nominated test pressure)
bb560cb1-0dad-5a28-8ad2-0810647c5812 | note | Fire Hydrant Systems (High Rise) – 1050kPa at the highest hydrant in the pressure stage being tested If pressure reading is being taken at the booster, determine the height difference in metres between the top hydrant and the booster and add 10kPa per metre of static pressure to this figure with a minimum test pressure of 1700kPa If in doubt please seek clarification from the Construction Supervisor or the Design Manager
685b5e21-9405-579d-b8f2-96b5b9c79eca | section | Rough In Only OR Rough In & Fit Off Together
9f29aa77-6976-5d3a-adf3-e4d55f0fd7fe | checkpoint | First Sighting - Pass once entered
801dbdfe-c273-5ee5-be62-6f4c647f5001 | textbox | Date
d73faad3-b770-5b06-a32b-3c5d4552a003 | textbox | Time
581682b4-cd9e-5a83-a961-4ca694e0ff1f | textbox | Pressure
fa356fe3-e4cf-529c-a66e-56312dc121ff | button | Photo(s) taken | Yes, No
2777f205-e525-50f1-bdcd-acd3a6bc7245 | button | Leemark Sign-Off - Attach below | Pass, Fail
17eea8ea-5b4c-5487-b428-0837caf89997 | button | Builder Sign-Off - Attach below | Pass, Fail, N/A
b1ca19d8-c57b-5fd0-ba00-fc40f8326b2b | checkpoint | Second Sighting - Pass once entered
7970433a-c86e-5d1e-8dd7-477e8a6b61cb | textbox | Date
da78add1-0ff2-5e7f-9f30-e0c290db91c0 | textbox | Time
89d36721-2f5e-5bc5-a7e4-3c8e1958137c | textbox | Pressure
184d0cea-0cf1-5b85-8e05-6780e9926884 | button | Photo(s) taken | Yes, No
2e12dfd5-1a55-511e-9bb3-a1d363e67b61 | button | Leemark Sign-Off - Attach below | Pass, Fail
5aa044f4-bb22-5442-bf90-7fdf4d7e06bd | button | Builder Sign-Off - Attach below | Pass, Fail, N/A
2c24d488-7f93-5146-bd6c-2217a211c5d9 | section | Fit Off (if required ie if not covered by the above section)
b34488a6-cbcd-5004-90ee-040d52d2049a | checkpoint | Subsequent Sighting - Pass once entered
be264ba9-c1c4-5ad2-84ab-14a07cbb7399 | textbox | Date
a07174b4-eb73-52b7-beac-2388bdeecc6c | textbox | Time
311b1850-7da4-5b6a-bec1-d0c54866f7b7 | textbox | Pressure
2954b052-9a96-55ba-beb0-3f60dba38d95 | button | Photo(s) taken | Yes, No
874dbd26-6c8c-5ae1-8f64-00693fe804c3 | button | Leemark Sign-Off - Attach below | Pass, Fail
f0717548-ff52-5ef4-9efe-57bc95c6d675 | button | Builder Sign-Off - Attach below | Pass, Fail, N/A
d80d130d-72f8-5fc9-872b-1fc379f43b15 | section | Completion
b894fd15-4591-5de3-8256-45a1e534edc3 | checkpoint | Works completed to specification/drawings - Attach photos of work below
fef67b80-09e7-5b11-88c1-1c4d9a2acd7f | note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
8572316f-9f44-5f4d-9ebe-a1aa8f995ebe | button | Area left clean & tidy | Yes, No
c1d2be28-36ca-5022-9cfb-be4d83605ce6 | tickbox | Leemark Sign-Off
f33cc38b-e6aa-5579-b409-283fb1cd80f0 | tickbox | Builder Sign-Off
dd71b766-5bfd-5126-8e81-631da7396226 | signoff | Sign-Off - click to Add signature(s)
58aab166-0042-5dd9-a9cb-6f0b2688f70b | checklist | Water Mist Fire Protection System – AS 4587-1999 |  | Water Mist Fire Protection System – AS 4587-1999
8111ace1-1386-5c1f-8290-3df28e3c8d3f | section | Details
19312081-956e-5b93-9749-6f7ed3256096 | checkpoint | Do the plans accurately illustrate the hazard configuration?
162a5d03-b9fc-5bf1-96a1-45dea5c277a2 | checkpoint | Are all components of the system in compliance with AS4587-1999
ff332214-761e-5fa5-9b11-afbb07d1508c | checkpoint | Check all flow calculations and verify that the containers, piping and operational equipment are installed and sized in accordance with the plans
aeb7c4cc-0294-5858-a67c-d5ef4ec2df41 | checkpoint | Are dimensions of unclosable openings in accordance with the plans?
1a1a53d8-365b-51a1-86b5-c69f90a3d3a5 | checkpoint | Check protected area for openings other than those in Item 4
fd8505ed-2730-545c-b0bb-c61682269b92 | checkpoint | Does the nameplate data on storage containers correlate with the submitted details?
75824d44-16f2-5c62-b4ab-1cfc6f6efb9e | checkpoint | Check quantity and mass of containers
64d1d33f-ec0b-541e-bd60-4ca75267998f | checkpoint | Check protected area volume
6f054bbc-b1b7-56f1-9d26-28713aa082f2 | checkpoint | Check need for and adequate provision of, post-fire ventilation
5fe5bda7-496b-5f70-be61-43a36727dc91 | checkpoint | Physically check the pipework. Are pipe joints sound and is pipework adequately secured?
117e7236-9408-5e0f-86a2-719ccb38aab1 | checkpoint | Ensure that storage containers are disconnected
31c5bbff-1876-5324-aadb-2147f4c799ea | checkpoint | Perform a full functional check of system (by operation of detectors) noting correct auxiliary electrical shutdown function (e.g. .....) doors released, dampers shut, airhandlers shut down, etc. (see Note 1)
fffb1827-4552-5135-bcf6-2a9ad5b87023 | checkpoint | Ensure that any non fire shutdown plant capable of affecting system performance is operating during the test
d45e1cc0-6078-5b38-9303-bf1a0675a34d | checkpoint | Ensure system release(s) operates correctly (see Note 2)
934699dd-60fa-504b-aa9a-1fdeacd76ba8 | checkpoint | Activate each detector head or system in turn by employing heat, products of combustion, etc. Ensure each manual alarm point operates and transmits
53fe48ae-23b4-511b-a269-8a0335f621ac | checkpoint | Ensure that the detection and control equipment complies with AS 1670 and AS 1603.4 with respect to configuration and operation
216a6567-226c-5505-b2d2-d2b1d52b5891 | checkpoint | Ensure that visual and audible alarms operate
9c0c0763-775d-5b77-bb21-30718534622f | checkpoint | Ensure that each alarm registers on CIE and mimic panels, if any
b8462901-c3ec-5ce7-81c7-7e8eb69d577d | checkpoint | Check that air-handling plant shutdown relay is activated
1db8f8c7-91d7-5b57-bb83-b506ab2bbdbb | checkpoint | Where multiple alarms are required for system operation, ensure that first and subsequent level alarms operate, including audible and visual indications, auxiliary equipment, and gas release mechanisms, if installed
bea4777a-83ca-5532-a208-4fe2c2753c57 | checkpoint | Check that directional valves are fitted where required and ensure that they operate correctly
2d9645c8-d91a-5e00-9e2f-ec311b9f90bb | checkpoint | Reset the system and check all manual release devices
8744c688-869e-5e9e-91f0-cfb53b7243ee | checkpoint | Reconnect storage containers. Ensure that all caps, plugs and locking pins are removed and that the system is left in an operable condition (see Note 3)