## Master List Templates
Id | Type | Name | Values | Prompting Name
60f5486b-f744-5d27-b8fb-e1e5f7108955 | checklist | Add Site Diary Checklist |  | Site Diary
bf78f897-fea7-5cd1-8800-293868168998 | checkpoint | Areas of work accessible for the day
e048d81c-b120-5201-90b9-737dc818e2c4 | dropdown | Day | Friday, Saturday, Sunday, Thursday, Tuesday, Wednesday,Monday
8b06ec40-8a3c-5890-8eef-2138d0007662 | textbox | Date
220bbcf8-26f5-50d0-8333-a92a92c45817 | textbox | Year
2ee2d4ff-2e7a-5a32-abbd-16864834758c | textbox | Number of workers on site
f718a78d-8c75-581f-8ecc-f206357c4ca1 | textbox | HSR on site today enter name
67e1eae6-6cc5-54f1-9e71-af2e0d4466a4 | textbox | First Aider on site today enter name
300a822f-3c8d-5eb4-ace2-997e233cf07a | textbox | Injury on site today enter name
01f1b588-929d-53f2-aad3-d4b5cd7ea92b | checkpoint | Work area 1 details entered
47c51389-20da-5ede-8014-b3d862ef3eaa | textbox | Area
be2d3209-4753-5610-ab16-ae8739025b3a | dropdown | Task | Cores, Deck, Footings G/Slab, Framing, Other, Setdown, Stripping, Upstand, Walls,Columns
8e3893b8-ed2f-5026-a09c-93c5cb077f2f | textbox | Comments
08b81b9f-23d8-52c9-a8ca-eac43bb9ea69 | checkpoint-no-value | Work area 2 details entered
c3bf60c1-b562-5b80-a516-8f9ebd4704ed | textbox | Area
4be3a27e-4b3d-586a-b513-ceb15fc40bfe | dropdown | Task | Cores, Deck, Footings G/Slab, Framing, Other, Setdown, Stripping, Upstand, Walls,Columns
c2b720eb-8138-59ab-8725-672f980b9236 | textbox | Comments
d36229fe-bf34-5147-bb14-ad0c6625023d | checkpoint-no-value | Work area 3 details entered
67ba33fd-a2e8-519a-9718-9602c1c22c34 | textbox | Area
d67e8a5c-0701-5122-8469-a3f875979c90 | dropdown | Task | Cores, Deck, Footings G/Slab, Framing, Other, Setdown, Stripping, Upstand, Walls,Columns
e0c6f448-ea66-5571-ab37-d4e5b00d7eba | textbox | Comments
80a68090-6901-508a-bb51-839019e42ad5 | checkpoint-no-value | Work area 4 details entered
a65ca3a0-57ef-5fca-9a21-6c58979e77b1 | textbox | Area
228c593c-8c7b-556a-a358-a302692731ee | dropdown | Task | Cores, Deck, Footings G/Slab, Framing, Other, Setdown, Stripping, Upstand, Walls,Columns
be73872c-40d0-5fe1-95e7-28fc71abd66b | textbox | Comments
104410fe-70a4-5c51-80ba-e83f3c874291 | checkpoint-no-value | Work area 5 details entered
5c62749c-d156-5f1a-a0db-c1bfbf345bbe | textbox | Area
fb2b9525-bedc-5e79-8595-7d9e44168dbe | dropdown | Task | Cores, Deck, Footings G/Slab, Framing, Other, Setdown, Stripping, Upstand, Walls,Columns
0f36562c-85d2-5c15-b10e-0e0351ca42a0 | textbox | Comments
6f677beb-e344-5d16-baa9-7fe0f3ae1253 | checkpoint-no-value | Work area 6 details entered
df45fc36-050d-52a7-b4de-4c3dfd8b7dc1 | textbox | Area
ce639f3d-bbb2-5e33-bfa7-831d0f7f3ce4 | dropdown | Task | Cores, Deck, Footings G/Slab, Framing, Other, Setdown, Stripping, Upstand, Walls,Columns
7a39984c-f43a-5db8-bbb8-67cb3b46d3ad | textbox | Comments
4284857c-6f64-58f3-8927-ba5ab4118ca5 | checkpoint-no-value | Work area 7 details entered
f56b01be-ce67-517e-9201-21fbb9da80c2 | textbox | Area
cd1edc93-5190-52b7-8b91-cd4940a807f6 | dropdown | Task | Cores, Deck, Footings G/Slab, Framing, Other, Setdown, Stripping, Upstand, Walls,Columns
0ce609f8-0e23-570c-84bf-8d4ab1c5a902 | textbox | Other
b9a615da-cbe6-5d4c-be7c-01ad213f34d8 | checkpoint-no-value | Work area 8 details entered
87fec433-1b39-5b0c-85ab-47b3724894e7 | textbox | Area
497f30d6-7d3e-567a-9fde-26ab4d0ca912 | dropdown | Task | Cores, Deck, Footings G/Slab, Framing, Other, Setdown, Stripping, Upstand, Walls,Columns
64afa6dd-5e29-541b-8f7a-b3eefebb69ef | textbox | Comments
7d6b1c3f-bf2b-5380-b63b-7ed9566a0d11 | checkpoint-no-value | Weather conditions entered
e4a9dd83-8a46-5d40-9016-ecdf1143b19f | dropdown | Conditions: | Hot, Overcast, Rain, Showers, Windy,Fine
c4eca12e-6581-575e-a282-008a28f85230 | textbox | Min temp predicted
9f6d3c08-4655-5cb2-a2ec-d500dc6aaf2c | textbox | Max temp predicted
5b3f52a8-b761-5f61-933f-a47148ab9fb7 | checkpoint-no-value | Delays from inclemency
f4baf749-c7b9-5264-82f9-225bad01bac5 | textbox | Total Hours of delay
c7cb66ed-53d5-5a5a-8876-a70cef304006 | dropdown | Conditions: | , Heat, Other trades, Windy,Rain
5b80d7d4-4a1c-5832-8683-847c7af64ab9 | checkpoint-no-value | Delays from Builders or Others
afcd53cc-c4ba-599f-8ce0-c3160cb74e57 | textbox | Total Hours of delay
c19fccf4-46f7-5cda-af3d-ffd8ba800343 | dropdown | Conditions: | Concreter, Crane, Earthworks, Other, PT, Safety, Scaffold, Steel fixer, Union,Builder
df62053a-68f1-5a9a-9162-77035b5d14a0 | checkpoint | Attach Specific site photos for respective day
6127f1dc-4f1e-4792-a980-9c46997559ef | checklist | Additional Tasks - add as required |  | Additional Tasks - add as required
99437fe9-c39f-53b1-9358-61d182ae2111 | checkpoint | Details of additional tasks - comment below
572b08b0-6ae6-5f16-81e4-2c167c64c8af | checklist | Additional Tasks Checklist |  | Additional Tasks Checklist
99437fe9-c39f-53b1-9358-61d182ae2111 | checkpoint | Details of additional tasks - comment below
6cac0869-3cda-508d-b9cb-4651e4731164 | checklist | Daysheets (Labour & Materials) (V.180521) |  | Daysheets (Labour & Materials)
4bce506c-bcdf-576c-b16b-6de3c5e3143d | checkpoint | Daysheet Completed & Ready for Invoicing
931dd1e9-e6f7-5970-96bc-c5fb9280165b | textbox | Date
3bff79c6-0816-52cd-9e1f-63cee682347c | textbox | Project
fadd42ae-e4b2-55ca-840e-a83ee3ddce8b | textbox | Location
a3f6da3f-5df2-56d2-b92e-0f3d0d2589e6 | textbox | Workers Name (Add hours in brackets)
6d361e0f-2263-54e3-b3ca-3bda46ad2f47 | textbox | Material 1 (Quantity & Description)
e983444b-af8c-5726-bee7-c484318a6209 | textbox | Material 2 (Quantity & Description)
d7bdc89c-6dca-5cc2-8bf8-22fc1c0e86b9 | textbox | Material 3 (Quantity & Description)
509caee7-e268-5f5d-ad4b-0812134a7dcd | textbox | Material 4 (Quantity & Description)
6e9d09c8-8a97-5a17-9cdf-0c0915621169 | textbox | Material 5 (Quantity & Description)
c20aadcd-5e8c-5e28-a24b-24f5efd5259f | button | Reviewed by Leemark Supervisor | No,Yes
44ff8f03-db9b-5a6b-ace2-12ab20bcdcb2 | tickbox | Signature of Builder's Supervisor Added
6435f32c-7cd0-5652-bb67-410fc08c8aae | signoff | Signature Added - Click Here
8f1df2a9-920c-50cd-bd21-5f261f2893fd | checklist | Defect / Issue to be rectified |  | ADD new defect / issue to be rectified [RENAME CHECKLIST TO LOCATION & DETAILS OF DEFECT]
1ce33f58-bceb-5bb5-b5a7-61ac5e21fa4d | checkpoint | Upload photo of defect / issue to be rectified. Add comments if necessary.
97acd7e5-f320-523a-9616-f769c9258094 | checkpoint | Has issue been rectified / defect been closed out? Upload photo
bab1d5a9-a3d7-58ff-a01f-4224a18aac6b | note | Only PASS once issue is rectified / defect is closed out
3a7fcaa2-7d4c-58ac-a353-e604d973278a | checklist | Document Attachment ITP (V.220421) |  | Document Attachment ITP (V.220421)
90417bc2-d69e-5f12-91e8-4743f1522568 | checkpoint | Documents/Drawings attached for reference - Pass once attached
8a44cb04-1369-56aa-b24f-13de25fc2559 | checklist | dry fire ITP |  | dry fire ITP
bfeea938-9a7c-596e-8159-bcf005c58f4a | checkpoint | Does the Emergency Lighting system operate manually and automatically via the RFP? RECORD VIDEO OF OPERATION
fb66489c-6b8c-5153-b2af-ef1700f1471c | checkpoint | Have all cables been cable tied to roof trusses / catenary wire with no sagging or obstructions? INSERT PHOTO
46916dd2-eae5-566b-9196-c89e8e07ab3a | checkpoint | Have all Smoke Alarms been installed in bedrooms within 3m of bedhead? INSERT PHOTO
7a5274aa-8390-50db-b3e4-5bcd7293c1ba | checkpoint | Have all cables been installed for sprinkler valve sets and mechanically fixed inside cabinet? INSERT PHOTO
384fdfea-7260-5f52-becb-48be24635b47 | checkpoint | Have all cables been installed for Door Strikes and tested to ensure correct operation on Smoke Detector & Sprinkler Alarm?
e39cefdb-bdb2-57bd-86c0-09e90df5e7bd | checkpoint | Does the main entry strobe operate on Smoke Detector & Sprinkler Alarms? RECORD VIDEO OF OPERATION
5df0f7ad-374c-5d56-b586-f2f1c126fd5d | checkpoint | Do the audible alarms ring independently when the relative SCV is operated for that property? RECORD VIDEO OF OPERATION
8fc93193-32d6-5257-a9ee-d633a1374bcb | checkpoint | If ASE is installed, does the ASE only trigger upon receival of all Sprinkler Alarms and not on Smoke Detection?
4c9bc864-6c96-5e24-a250-a0c7c2008d79 | checkpoint | Does the Heating System shut down on activation of smoke detector or sprinkler and operate manually via RFP? RECORD VIDEO OF OPERATION
be6a84a5-ba95-50ea-a81c-284c410577f2 | checkpoint | Have the Block Plans been installed next to the RFP and match the current zones and detectors installed on site accurately? INSERT PHOTO
e5013e35-e3ed-5ea2-9aef-f280febffb48 | checkpoint | Has all patching and painting been completed or booked in to be completed? INSERT PHOTO
9407048b-d738-5abe-8356-ae33120d2522 | checkpoint | Have the As-Installed been left inside the RFP? INSERT PHOTO
b2f5c4a4-582f-507d-a062-d3e8a728e3a3 | checkpoint | Is there a completed copy of the discharge test in the Emergency Lighting Logbook on top of the RFP, if applicable to project?
dae7fc3f-8472-514a-b395-e8c7b0d8f3ff | checkpoint | Have the newly installed Emergency Lights been labelled, if applicable to project? INSERT PHOTO
cd11f816-1ea0-56ee-b502-27300eb8671d | checkpoint | Is there a FIRE label installed above the strobes? INSERT PHOTO
89c60516-1e1e-53c2-aa65-41f0959f7cb9 | checkpoint | Have the Installers Statements been filled out in the back of the Manual in the RFP? ATTACH PHOTO OF ALL PAGES
0ace1902-99ba-5b45-8dfd-575bcb2391b4 | checklist | Handover ITP (V.200521) |  | Handover ITP (V.200521)
de92f433-8d95-5167-8ab1-a4a100c606b5 | section | Design
3dec0d0c-da0f-5236-9a7f-e890e3b115b2 | checkpoint | Shop Drawings - Pass once completed
8e21ed16-657f-5808-9a2f-13421c82ad58 | note | By: Drawing Office
28b99707-a4b3-587d-9d0a-b305861ce9e4 | note | Verification Criteria
f6b85a84-ae1b-5766-9d5e-90c7c935e409 | note | AS2118.1-1999 Automatic fire sprinkler systems - Part 1: General Requirements
fb3877ea-9760-5cbd-bb00-03f6d16cefc1 | note | AS2118.6-2012 Automatic fire sprinkler systems - Part 6: Combined sprinkler and hydrant systems in multistorey buildings
d077a0d0-f94d-51cd-bc95-e266cf3b51f1 | note | AS2419.1-2005 Fire Hydrant Installations - Part 1: System design, installation and commissioning
211256e5-5e05-5cbb-8454-2e2cdf12c3ca | note | AS2441-2005 Installation of Hosereels
5ddbcbdd-12d6-5883-bf61-1bd90a87116a | note | AS2941-2013 Fixed fire protection installations – Pumpset systems
58eefbad-460d-5c85-b4e9-07ac3e989c0d | note | AS 1670.1-2004 Fire detection, warning, control and intercom systems - System design, installation and commissioning
a4aa7c01-3d8d-5b30-9751-bc34b265b61b | note | AS 1670.4-2015 Fire detection warning control and intercom systems - System design installation and commissioning
5e436985-e0a4-5be1-8e2a-0dd78a6c9701 | note | Project specification (TBC - Once known comment below)
efdb4b77-cd10-53a7-bc5d-86e1505edb60 | note | .. ..
d68be9a8-07f2-5eee-aca9-17543b662a85 | note | Quality Control Method
7a7eadf7-0236-5e3e-b01f-d71ab706495f | button | HOLD POINT - Leemark add signature below | Yes, No, N/A
d3581721-4c25-5383-88fd-0956f24d1e1f | button | Approved by Project Manager | Yes, No, N/A
a87ccb3b-5773-5136-ab38-4c0ffd1b9204 | button | Approved by Fire Services Engineer/Builder | Yes, No, N/A
552d7f8f-0dcf-5220-a750-2122a72ddb15 | note | Records: Aconex
ec658659-0ece-5e4f-b3ae-debf21725a54 | checkpoint | Hydraulic Calculations - Pass once completed
3b732027-3d2d-57a6-a8ba-f40e942ed527 | note | By: Drawing Office
d789e3fb-d86a-5672-aaf2-c26652dd6ebd | note | Verification Criteria
9bd24c06-00df-55c5-9371-e83b6de1ed25 | note | AS2118.1-1999 Automatic fire sprinkler systems - Part 1: General Requirements
9471a8f0-01ed-5473-a879-88901371b10f | note | AS2118.6-2012 Automatic fire sprinkler systems - Part 6: Combined sprinkler and hydrant systems in multistorey buildings
16ce0911-6e4b-5b16-b614-3971656d6f06 | note | AS2419.1-2005 Fire Hydrant Installations - Part 1: System design, installation and commissioning
f5674146-a754-5202-962e-d9cc6e96a323 | note | AS2441-2005 Installation of Hosereels
6a6146a3-65d4-591f-bf20-bd8787a8ab41 | note | AS2941-2013 Fixed fire protection installations – Pumpset systems
c0b4cf60-49f3-5b0c-bad8-7eb37b206ea2 | note | Latest revision FER. (TBC - Once known comment below)
c8073585-e0d6-5387-8e12-80815a83f27b | note | Project specification. (TBC - Once known comment below)
843c58b3-b3d3-5a7c-bd63-53992a052973 | note | Quality Control Method
333fead2-b9db-5d2d-addb-c9040544d004 | button | HOLD POINT - Leemark add signature below | Yes, No, N/A
f660ea01-0d4d-5d04-8362-b2aa3f66e157 | button | Approved by Project Manager | Yes, No, N/A
6cd29afd-07c7-57c1-9ea6-e37174e27763 | button | Approved by Fire Services Engineer/Builder | Yes, No, N/A
6a42ca05-52cd-560c-b588-b0ed59818902 | note | Records: Aconex
3c0cfd31-a39e-5a56-9377-bb58b0b02d85 | checkpoint | Samples - Pass once completed
7a4c57e4-8827-547a-9f87-9d4ab95479e2 | note | By: Drawing Office
65ee3464-7a5d-59fa-90f1-8809f3ac97f9 | note | Verification Criteria: Part C.1 Samples & Details Part C.8 Fire Sprinkler System Part C.9 Fire Hydrant Pipe
742055d2-08d3-5256-a7ec-0c149cac637f | note | Quality Control Method
b7095eb4-2176-57eb-a042-6870088b4122 | button | HOLD POINT - Leemark add signature below | Yes, No, N/A
1d64f07c-422e-5c72-8fd4-aa7e32b8f2ad | button | Approved by Project Manager | Yes, No, N/A
751bf811-12f9-52a1-af17-86cba1ed4909 | button | Approved by Fire Services Engineer/Builder | Yes, No, N/A
f0a98a23-19ab-58f3-9db1-db1f04b98d7d | note | Records: Aconex
04f74ea0-6564-586f-8045-b8ccebf655df | section | Offsite Manufacture
53c41315-29be-50f2-82c5-b5e65d128307 | checkpoint | Pipework Fabrication - Pass once completed
18b0f321-bd67-57aa-a437-f6e21cc57721 | note | By: CWS
e35a2910-2f84-55aa-b9e4-4a161122163e | note | Verification Criteria: C.12 Pipework & Fittings
fe78dcfb-38de-515c-830c-6c3677a93f09 | note | Quality Control Method
b29069a1-5806-5656-957a-89d0c26dafa8 | button | Leemark Inspection Completed | Yes, No, N/A
5f543120-8fbd-506d-a6e3-3e745d2a3d95 | note | Records: CWS/ITR
e8adbc84-b448-5119-bc35-7edd8200d05f | section | Installation
d000a01a-b900-5e2f-8828-c839b516f55f | checkpoint | Sprinkler - Pass once completed
1c56aecc-a6e8-5ee8-a9a7-ef8a0264e2a4 | note | By: Sprinkler Fitters
a37fd250-e671-5161-90aa-ffb57684311d | note | Verification Criteria: Part C.8 Fire Sprinkler System AS2118, 4118
16c3ecd9-9cff-5079-b0cb-fd963329c54b | note | Quality Control Method
b37d257a-b773-56a0-872e-e90b408e5eb9 | button | Leemark Inspection Completed | Yes, No, N/A
2ed5abf4-f895-523e-8a1f-b55a22853a97 | button | Witnessed by Project Manager | Yes, No, N/A
241fe270-051b-509b-b53e-bcd78008c049 | note | Records: Inspection & Test Record, 301/301.1 & 301.2
428b6de5-8f5f-5480-9378-f06255a0b70e | checkpoint | Hydrant & hose Reels - Pass once completed
19230c38-871a-5008-9546-51b901d84191 | note | By: Sprinkler Fitters
50aca357-c828-5c05-b65a-d667bcb5f52e | note | Verification Criteria: Part C.9 Fire Hydrant Pipe & Hose Reel Installations AS2419.1/.2/.3 & 2441
5ff5129d-708f-565f-bf14-47edfe5b4c04 | note | Quality Control Method
a90ebfb4-63f8-56fa-913c-373984ee03aa | button | Leemark Inspection Completed | Yes, No, N/A
ff9469c9-6a09-57e6-8534-faa0e110e069 | button | Witnessed by Project Manager | Yes, No, N/A
4826fd02-592c-5945-95ae-62afc80884ee | note | Records: Inspection & Test Record, 302.2/302.3 & 302.4
e88c102e-d483-5848-b909-1c5a73c18ea6 | checkpoint | Alarms / EWIS - Pass once completed
fa104792-de17-57a5-ae83-ba1d0ffce0c3 | note | By: Fire Alarm Technicians
31d71fa6-c976-59e8-847e-a04cf5cde391 | note | Verification Criteria: Part B.12 Fire Detection & Alarm Installation, Part B.13 Emergency Warning & Intercommunication System AS1670
4698edf5-59e5-5e23-9d92-86dbc7bda5c7 | note | Quality Control Method
e1dcdcbd-46ad-5b23-8749-9f646a89c12e | button | Leemark Inspection Completed | Yes, No, N/A
485d7468-674a-5fea-894d-4834f02a1b71 | button | Witnessed by Project Manager | Yes, No, N/A
d658b17d-2dd9-5c3d-8e63-20f0a1329f6c | note | Records: Inspection & Test Record, 303.1 / 303.2 / 303.3 / 303.4 / 303.5
bdd5cda7-43e6-5934-bc03-37a69b742c8c | section | Commissioning
d83b4ae8-9f84-5c30-82f7-9771d5515513 | checkpoint | Hydrostatic Tests - Pass once completed
0bd86e47-5d8d-5980-ae1d-40c6c9797613 | note | By: Sprinkler Fitters
e33fceaf-6b67-5b77-84ee-e14899539ec1 | note | Verification Criteria: AS2118, 4118, 2419, 2441, 2941
3ab15ca4-7bf5-5cfb-a7dc-d6ec364d4e09 | note | Quality Control Method
370a6403-895b-51e9-86ae-095fbbe28f5f | button | Leemark Inspection Completed | Yes, No, N/A
d70dee45-343a-5f4c-8577-a363bc678c7f | button | Witnessed by Project Manager | Yes, No, N/A
a54bff67-684d-5d19-9295-10d96af0b889 | note | Records: Inspection & Test Record, 401
eba0ec8c-281d-5344-92d7-6e0ab6006a7f | checkpoint | Sprinkler Inspection - Pass once completed
87a429a0-e143-5c8e-9b50-849da90636da | note | By: Fire Safety Victoria
c7aaae11-5559-5256-a13f-0b51a54d2f59 | note | Verification Criteria: AS2118.1, AS2118.6
ebc353e6-4a18-56d1-bfec-3ae52a45bb0c | note | Quality Control Method
32149feb-02d1-5f1d-93f4-84ff3c6a5373 | button | Witnessed by Project Manager | Yes, No, N/A
63fbe6e7-9ee0-5dc3-a900-1d26e41895ce | note | Records: Certificate issued - Attached below as applicable
53e639a5-4269-5cd5-9fde-2ee4fb8e4f61 | checkpoint | Hydrant Inspection - Pass once completed
4e5520e0-8737-5ea4-8831-0f8404823ba2 | note | By: Victorian Hydrant Test & Plumbing
b574b2ab-65af-5054-909d-2c4c074fdeaa | note | Verification Criteria: AS2419, AS2118.6
26ccbada-d706-5ce4-908b-6991163c3e10 | note | Quality Control Method
c15638e3-3311-572f-88c1-bafe2716c186 | button | Witnessed by Project Manager | Yes, No, N/A
465ecdf7-3360-55ba-aa6b-095892e7c9c5 | note | Records: Certificate issued - Attached below as applicable
12ff13c5-c2dd-5e4f-a11c-c03612fee06c | checkpoint | Alarms / EWIS Inspection - Pass once completed
0662f9ec-7cb7-5708-87ad-5d720cbe4f1d | note | By: Fire Safety Victoria
0890b115-7270-5c9f-bf30-f48791ee9f3d | note | Verification Criteria: AS1670
d8877a42-1341-5694-a9b4-23a74d09f4d5 | note | Quality Control Method
06adcd4a-9629-5422-95a1-07cff1f00c03 | button | Witnessed by Project Manager | Yes, No, N/A
902eba8e-4707-5bb9-ad7f-42c00bd7c7ee | note | Records: Certificate issued - Attached below as applicable
d80d130d-72f8-5fc9-872b-1fc379f43b15 | section | Completion
46c52a47-2abf-5d42-b17f-abce14a4e18c | checkpoint | As Installed drawings - Pass once completed
607fdf1d-8c12-5e15-9d63-4f70f007bb5d | note | By: Drawing Office
6c36bd21-564e-507d-afab-4ea75e3fbdde | note | Verification Criteria: AS2118.1, AS2118.6, AS1670
63736753-55a5-502a-acdd-1e7e2b7a5dc4 | note | Quality Control Method
8aaa2b52-7d0c-501b-ba53-8b4641f07720 | button | Document Submitted by Leemark | Yes, No, N/A
67232538-6f08-59c6-a148-8b432945680b | button | Approved by Project Manager | Yes, No, N/A
f9092ec3-8f25-5db2-a647-3d9a9a27050d | button | Approved by Fire Services Engineer/Builder | Yes, No, N/A
a02c682b-12dc-5f37-ac81-95afa517d633 | note | Records: Operation & Maintenance Manual - Attached below as applicable
8ac8aaa8-a7b8-58bb-88b6-eaa9160fb209 | checkpoint | Manuals - Pass once completed
b7066152-a2f3-5428-a732-3a136e51c0dd | note | By: Drawing Office
7e47c988-f492-5d83-bb74-dff9f900fae4 | note | Verification Criteria: As per SOW
e2d81918-4ca4-5303-8550-7e6702ec2935 | note | Quality Control Method
34c275e8-7a02-59bd-a4ca-b4c378160c6e | button | Document Submitted by Leemark | Yes, No, N/A
2d41cd87-85cb-5bdd-9ec5-9100891f0a75 | button | Approved by Project Manager | Yes, No, N/A
d0905132-a5d6-5673-bbc5-f8c2003ea3b7 | button | Approved by Fire Services Engineer/Builder | Yes, No, N/A
3af63e93-ca29-5aa8-9856-a4818fc27076 | note | Records: Operation & Maintenance Manual - Attached below as applicable
4faadc7b-afca-5580-b3f8-339a8a3f38b8 | checkpoint | Test Data - Pass once completed
cb5ecc93-db21-590f-8120-aec4daf10569 | note | By: Site Foreman
b67e3f3f-f859-590b-b8ea-a4b3eb806ebd | note | Verification Criteria: Refer Commissioning part of this plan
d562f040-4326-51b0-8d1a-de482abddb3f | note | Records: Operation & Maintenance Manual - Attached below as applicable
538b9d8e-0ef9-5f45-9694-7089a945d278 | checklist | ITP/R Test Report Gaseous Suppression System (V.240521) |  | ITP/R Test Report Gaseous Suppression System (V.240521)
475eb398-25ac-54a6-b675-e2759d797f02 | section | Installation Testing
d43163db-8f22-5249-9081-91480c3ed8d4 | checkpoint | Latest consented drawings checked & referenced
5b57104a-56ba-51d5-b12e-af6d3a39ab81 | textbox | Drawing & Revision #
12aaa62d-0712-5e8a-a640-edbbf967e0dc | tickbox | Area clear, tidy and accessible
23252166-ad43-598c-8da1-5691b7e8cfc0 | note | Attach Photos/Comments below if any issues & send report to Builder
0e0ef9a1-4ae8-59f8-834f-1c5dfd1c6e07 | checkpoint | Verify correct type, spacing and elevation of installed pipe supports and hangers
3435241f-b220-59d2-aadf-6585efaed6a5 | note | Acceptance Criteria: Installed to Approved Drawings
919ff648-7568-5c5c-a665-f3a3476e5a80 | checkpoint | Installation inspection of pipes and nozzle droppers/risers
542d335f-8de6-539e-a048-28fd509f974b | note | Acceptance Criteria: Installed to Approved Drawings
5cfcef8b-c8fe-5d46-85b0-08fec0117a1c | checkpoint | All dirt traps must be capped and all pops temporarily plugged
1843a944-d0a3-53e9-a4de-9e4003b16833 | note | Acceptance Criteria: Installed to Approved Drawings
cd282dc9-514d-5a83-900f-cf1186bd4b15 | checkpoint | Perform Pneumatic leak test of pipework in accordance with approved Test procedure and SWMS. Gradually apply pressure increments of 100 kPa for 15 minute holds
75c9d4e2-45a2-58b5-aa09-5c915b126a43 | note | Acceptance Criteria: Pressure drop should not exceed 20% of 300 kPa for 10-mins
96a28d2b-22b7-554b-87ac-0856a37d342d | section | Installation of Cylinders, Manifolds, Valves, Actuation, Discharge Hoses & Nozzles
e58c1cb8-1374-5835-840b-8da86fa6efb4 | checkpoint | Cycinders shall be adequately mounted and suitably supported according to approved installation plan
aa22c2ae-93a6-5d24-bc9f-44e5f0be8676 | note | Acceptance Criteria: Installed to Approved Drawings, AS 14520.1-2009 Clause 8.2.3.12a
28e12b97-87e9-5d89-83cc-1d8da6ccaf70 | checkpoint | Discharge manifolds and valves shall be mounted and adequately supported
e8534040-8f74-5e49-959f-e12e987a0479 | note | Acceptance Criteria: Installed to Approved Drawings, AS 14520.1-2009 Clause 6.3.4
188d64f6-4aaf-5da6-9309-91bfdd8dc5a4 | checkpoint | Adequate quantity, correct code and location of discharge nozzles shall be installed according to approved plan
b97526e1-822a-54d6-aed0-3285e90debd4 | note | Acceptance Criteria: Installed to Approved Drawings, AS 14520.1-2009 Clause 6.3.6.1
280ef84f-63e7-59d4-bdbd-d1dfff4cac7a | checkpoint | Detection, actuation, alarm and control systems shall be installed and tested by “DRY FIRE” contractor in accordance to relevant code/standards
39174192-d228-595d-a30d-cd9d126f605e | note | Acceptance Criteria: Installed to Approved Drawings, AS 14520.1-2009 Clause 6.4.1
942c4492-d15e-5429-8426-643951ff4886 | section | Enclosure Integrity Pre-Test Inspection
3384f433-2aa5-559d-ae6c-a4d3fdc3d05c | checkpoint | Client to confirm that all services penetrations and/or openings are sealed prior to the test
6f5c9a97-2e78-51c4-ae8d-3cf28109ef09 | note | Acceptance Criteria: Builder Approval (Click to add signature Sign-Off below as required)
31647873-0f46-5361-9a4b-6cf6c7b4bf06 | checkpoint | Client to confirm that all HVAC fire rated dampers including OPR Damper can be closed prior to the test
aa7eb933-acac-5091-9a4f-b6e4269e891b | note | Acceptance Criteria: Builder Approval (Click to add signature Sign-Off below as required)
9bd69c16-4cb5-58b2-ab71-425f495db3de | section | Enclosure Integrity Test
9416e299-0025-5120-bc92-4d4b65664924 | checkpoint | Perform both pressurization and depressurization fan test of the room and using the software program, confirm that holding time is equal or more than the required 10 minutes
8ce1445d-1196-5a03-b031-0a786432012e | note | Acceptance Criteria: Relief Damper Installed is sufficient
7f15e5c1-b9d6-59ac-9c99-60d676730f4f | checkpoint | Prepare full test report of each enclosure demonstrating the level of compliance achieved
72652afe-e74e-5d90-bd70-a9c9b4affce8 | note | Enclosure PASSED the hold time & venting requirements
18e2a2b7-f51e-5420-90ae-4d1194f2ca02 | section | System Commissioning and Acceptance
e49128bc-9ccb-5eee-983d-d456a42ff3e0 | checkpoint | Prior to start of any test, ensure all extinguishant storage container release mechanism are disabled or removed
a0e7bfe8-c841-553b-af8a-7aea46ce4a73 | note | Acceptance Criteria: Release Mechanism Isolated
123bc64c-f296-5d7b-87bb-93895fed25ec | checkpoint | Verify and confirm compliance to the approved design of distribution piping system, discharge nozzle sizes & orientations, storage containers quantity & locations and warning signs & notices locations
be2e11ae-6ff3-5f4b-b4b8-d07a8dbd058b | note | Acceptance Criteria: Installed to Approved Drawings
e42750be-c24f-5a39-b0ab-6d45bf499a61 | checkpoint | With the operation of fire alarm system, verify and confirm operation of audible & visual alarms, plant shutdown interface, time delay & release mechanism activation/30s time delay / solenoid operated/ audible visual Alarm
fcea09e4-5a0c-5833-a116-97177ea97a74 | note | Acceptance Criteria: 30s time delay, solenoid operated , Audible/visual alarm operated
b218507b-c71d-5c5c-a9c0-2bd49cf325ce | checkpoint | Simulate discharge pressure switch operation and confirm gas released alarm indication at Fire Suppression Panel
1f8c18df-932c-5b59-b8e3-5fa748928795 | note | Acceptance Criteria: Indication at FIP
d18f7a96-94d6-549e-b2e6-caea819a28ee | checkpoint | After completion of system functional test, reset and reconnect all release mechanism onto storage container and return the system to full service condition
a53b1919-079c-5258-b7ce-ff36c88ff5b5 | note | Acceptance Criteria: Builder Approval (Click to add signature Sign-Off below as required)
d80d130d-72f8-5fc9-872b-1fc379f43b15 | section | Completion
b894fd15-4591-5de3-8256-45a1e534edc3 | checkpoint | Works completed to specification/drawings - Attach photos of work below
f4684c11-06d7-5996-beba-eb3b991d6f3c | note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
438736fc-6c03-5609-981a-307ed92d542f | button | Area left clean & tidy | Yes, No
c67616bc-ad4e-5162-a6f0-0c309b2170ed | tickbox | Leemark Sign-Off
e5c9317c-7180-57ff-a410-52bceb7f086f | tickbox | Builder Sign-Off
dd71b766-5bfd-5126-8e81-631da7396226 | signoff | Sign-Off - click to Add signature(s)
1a277d25-b57a-5f05-9b41-219d1b836d8b | checklist | ITP/R Test Report Pre-Action System (V.260521) |  | ITP/R Test Report Pre-Action System (V.260521)
475eb398-25ac-54a6-b675-e2759d797f02 | section | Installation Testing
d43163db-8f22-5249-9081-91480c3ed8d4 | checkpoint | Latest consented drawings checked & referenced
844133e1-871d-52b9-9d9c-32bfa558ff44 | textbox | Drawing & Revision #
c38cc06b-4b78-5dac-ba2c-3f3aad3791fc | tickbox | Area clear, tidy and accessible
bb2d8abc-584e-5a44-aaad-6155d904c901 | note | Attach Photos/Comments below if any issues & send report to Builder
0e0ef9a1-4ae8-59f8-834f-1c5dfd1c6e07 | checkpoint | Verify correct type, spacing and elevation of installed pipe supports and hangers
38886f8a-c065-5528-b142-28785172315f | note | Acceptance Criteria: Installed to Approved Drawings
2e4b0413-c22a-56d1-81a5-6e399396e094 | checkpoint | Installation inspection of trunk mains and range pipes
e1e2f940-7c79-55da-8172-cc614c2d3e6e | note | Acceptance Criteria: Installed to Approved Drawings
5cfcef8b-c8fe-5d46-85b0-08fec0117a1c | checkpoint | All dirt traps must be capped and all pops temporarily plugged
3cf273de-5bd1-5447-ae9c-4eb8eabfe8b1 | note | Acceptance Criteria: Installed to Approved Drawings
3aea4439-fedd-54fa-9f9a-110a14abe8ce | checkpoint | Inspection of installed sprinkler heads & baffle plates and flexible droppers
03208669-ef9f-5f19-941d-06c5d48ce641 | note | Acceptance Criteria: Installed to A.S 2118.1
67db6fa7-5b5c-56c1-bcd5-0f2f383756db | checkpoint | Perform Pneumatic leak test of pipework to ensure no loose joints or open pipe ends
04ad91d3-2786-52c3-9224-de413b86db00 | note | Acceptance Criteria: Refer AS 2118.1-2006 Clause 7.9.4
c257065a-8a9a-55ab-bfdb-80f09ab05810 | checkpoint | Perform Hydrostatic Testing of pipework. Gradually apply pressure increments of 500 kPa for 15 minute holds until test pressure of 1400 kPa or 400 kPa above maximum static working pressure of the system is achieved and hold for 2-hours
462c1fee-beba-50f7-ae5d-6653beee28b6 | note | Acceptance Criteria: Refer AS 2118.1-2006 Clause 7.9.4
499547ef-7f4e-57d1-8adb-c610c59916b7 | section | Installation of Pre-Action Valve Sets & Ancillary Equipment
c8ea29bc-3fc6-55db-a74a-84d073415549 | checkpoint | Installation inspection of pre-action valve sets and ancillary equipment to ensure completeness, correct location, mounting
266bfe91-646f-5a78-9c3f-12dc83cd22c3 | note | Acceptance Criteria: AS 2118.1-1999 Clause 8.1
6ac9bbf9-e586-5484-a3f4-41178942aaa3 | checkpoint | Verify installation of alarm devices (e.g. DBA pressure/flow switch, low pressure switch) and solenoid valve for correct type and rating and proper interface connections to Fire Indicator Panel (FIP)
2969bb73-a1f2-53f4-866f-b3d19633b7da | note | Acceptance Criteria: Refer AS 2118.1-1999 Clause 8.10.1
cac99c78-80ad-5858-82a6-a47f92dc3ff7 | section | System Commissioning
66d4fa6e-1c11-587a-91f1-7e265f42d622 | checkpoint | Perform a trip test on each pre-action valve by opening the alarm test ball valve and check operation of water motor alarm. Confirm operation of DBA pressure switch with correct indication at fire indicator panel
53aa6cf2-4942-5001-bb0e-816e85d86493 | note | Acceptance Criteria: Refer AS 2118.1-2006 Clause 15.4b, DBA -3 mins
99ffa3bf-f86d-54d4-ad59-a13edb135e9e | checkpoint | Initiate single or double interlock release activation and check operation of water motor alarm, DBA pressure switch and correct indication at fire indicator panel
b3b2b578-4e01-5610-8d7e-abfb49faeaca | note | Acceptance Criteria: Refer AS 2118.1-2006 Clause 15.4b, operational confrimation
47f6e164-e977-5c1e-9923-b1dcd96f17c5 | checkpoint | Record cut-in / cut-out pressure of air supply compressor and time to recharge the system pressure
8d13ae0d-2149-5847-9d52-fdbb9108a410 | note | Acceptance Criteria: Refer AS 2118.1-2006 Clause 15.4b, Time to recharge 30 mins
cedba12b-9c6f-5917-af36-91e83d366955 | checkpoint | Reinstate system and ensure valves are secured in its intended position, alarm and monitoring devices are in operational mode and system in ready to operate condition
9f01d373-0f6e-5f02-bc77-1c6ff9035e2c | note | Acceptance Criteria: AS 2118.1-2006Clause 15.6
d80d130d-72f8-5fc9-872b-1fc379f43b15 | section | Completion
b894fd15-4591-5de3-8256-45a1e534edc3 | checkpoint | Works completed to specification/drawings - Attach photos of work below
a2dfd634-dbf3-57c8-9472-610c95428b57 | note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
481ec145-987c-596f-89ad-62c19ee25ddc | button | Area left clean & tidy | Yes, No
5288f8ea-689d-5b0f-bfee-44bc576c23a6 | tickbox | Leemark Sign-Off
beef6ff2-2bfc-54e8-b6c4-9250f968e97e | tickbox | Builder Sign-Off
dd71b766-5bfd-5126-8e81-631da7396226 | signoff | Sign-Off - click to Add signature(s)
f971e054-536f-516e-9712-82947453d737 | checklist | LM-FOR-026 Penetration Installation |  | LM-FOR-026 Penetration Installation
d43163db-8f22-5249-9081-91480c3ed8d4 | checkpoint | Latest consented drawings checked & referenced
81eb179b-f128-5570-8671-d7df13741f98 | textbox | Drawing & Revision #
33c10a2a-7565-55ae-b257-71be0178a1c9 | tickbox | Area clear, tidy and accessible
f57942fe-71cd-533e-873e-fdda4f24dd75 | note | Attach Photos/Comments below if any issues & send report to Builder
5692dc88-991a-5ff6-a500-e7f72aec6c38 | checkpoint | Peno sleeve as per drawings - Please attach photos
f8df8aef-8746-5e56-b21a-fa841050241a | checkpoint | Peno sleeve as per drawings - Pass once completed and photographed
f88f95e3-b7ac-5ce9-9f0c-e32fa4826400 | textbox | Area (State area's worked in)
15a0b65e-81dc-5bbb-a85d-d3df5262e7f5 | dropdown | Substrate type | Concrete, Blockwork, Single layer of Plasterboard, Double layer of Plasterboard, Other (Specified below)
46e1383d-7866-5083-acae-724e7f40905b | textbox | Substrate type - if other (specify here)
469e0eb7-dc72-584a-996a-04b6aec765d6 | dropdown | Penetration type | PvC Pipework, Pex Pipe (HW/CW), Gas Pipe, Copper Pipe, Other (Specified below)
afb4f858-80db-5853-a8d9-44d30bd7b512 | textbox | Penetration type - if other (specify here)
f0da4e0a-ad3f-5f2a-b909-217fd8bae6b8 | dropdown | System Used | TBC w/CONQA, Other (Specified Below)
32bf7186-4238-570d-854c-8495494203bb | textbox | System Used - if other (specify here)
fdef9b94-2484-596b-ac0f-d4a8c9800035 | button | Labelled Attached | Yes, No
99fd04b4-9b31-5a5c-9ced-bbe6e5b63a18 | button | Attach photo(s) when complete | Yes, No
54bab685-4e47-50b9-9871-c2d373f561df | checkpoint | Passive fire elements completed to specification/drawings & Area left clean/tidy
977b57a5-db8c-5d17-99e5-889fa1176689 | note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
084a64d2-23cc-59bf-948d-abee1e1a26f6 | checklist | LM-FOR-30-ITR-301 Sprinkler Installation/Fitoff |  | LM-FOR-30-ITR-301 Sprinkler Installation/Fitoff (V.171121)
6465d6f3-3be2-5499-b503-3c3e618fa07c | section | Sprinkler Rough-In
d43163db-8f22-5249-9081-91480c3ed8d4 | checkpoint | Latest consented drawings checked & referenced
664cb6f6-2306-552e-bf48-ae5351af600a | textbox | Drawing & Revision #
e5c07ca7-84ac-5c90-a48b-f59df54ae693 | tickbox | Area clear, tidy and accessible
9a6be319-4e3c-5ad8-8bff-6ec65b722680 | note | Attach Photos/Comments below if any issues & send report to Builder
908a092b-915c-5c08-b50c-ede1e907f1fb | checkpoint | Supports spacing & fixing as per AS2118
0ce6b1a3-908f-57f4-b480-ef7e2ab4bca0 | checkpoint | Pipework installed as per drawings
9f5be1cb-e20d-521e-ba03-b7cd11733d19 | checkpoint | Concealed space sprinklers installed
db639292-eb82-5cfd-91b6-776ba182f82d | checkpoint | All ends blanked off/plugged for testing
abaffbc0-a165-5a7d-968a-9e1ee9f1b2dd | checkpoint | Pipes left out
b1d15198-6c7c-5c4e-b4b1-d6fe411cb10f | note | Fail=Missing, Pass=Complete
d0d2d4c7-4017-52fb-b22c-113fa803d05b | button | Pipes left out - installed | Yes, No
c016619f-d61c-50f0-af4f-4b00068361fe | section | Sprinkler Fit-Off
a99cdfe5-cca9-41ea-b96f-7eb8282ebe02 | checkpoint | Latest consented drawings checked & referenced
b2a32d07-0e44-5883-b573-8650614c9a55 | textbox | Drawing & Revision #
5079c10d-7a6b-5395-ad4c-661e3f78c553 | tickbox | Area clear, tidy and accessible
656e2bcd-eabc-5451-a318-8c8c20961645 | note | Attach Photos/Comments below if any issues & send report to Builder
f86149be-c970-57fd-975a-1970dbf27b35 | checkpoint | Ceiling grid levelled
d61ada5b-d5ad-556c-afda-15a7b0b6e415 | checkpoint | Sprinklers installed as per drawings
d4116fcb-4c5a-5e06-9763-eeb6318c3f6c | checkpoint | Sprinkler Type & temperature as per drawings
17eac725-bb30-50a9-8f45-34d5f0844ff3 | checkpoint | All escutcheon plates installed
d817b34e-0485-51ac-9c3f-d7acb9574942 | checkpoint | Areas not fitted-off
7e2aa04b-a876-502f-8e9a-f8e4a8c2fe59 | note | Fail=Missing, Pass=Complete
70ca937b-d811-5e52-8c58-3e8709187611 | button | Areas not fitted-off - completed | Yes, No
cbff4ae3-2b4c-528c-a82f-4b4dff05ef2e | checkpoint | Client Sign Off Sheets Complete
bdd1e031-14b5-5238-9027-9fddf2280de3 | checkpoint | Painting carried out
9947fe3a-0d3c-522f-994e-6ac7081bd841 | checkpoint | Pressure Tested (refer ITR 401) - Completed
d80d130d-72f8-5fc9-872b-1fc379f43b15 | section | Completion
b894fd15-4591-5de3-8256-45a1e534edc3 | checkpoint | Works completed to specification/drawings - Attach photos of work below
8fbaaa0a-8c79-5691-835e-7694661b855e | note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
4acbb0b3-01a3-577d-94fb-0c84ac58ba00 | button | Area left clean & tidy | Yes, No
d45072ab-879c-52bb-8bab-d23e9114cac0 | tickbox | Leemark Sign-Off
29eea887-ec22-540d-b7a5-6511d0239e0a | tickbox | Builder Sign-Off
dd71b766-5bfd-5126-8e81-631da7396226 | signoff | Sign-Off - click to Add signature(s)
048e094f-f665-58c0-9816-29c5e263f2b6 | checklist | LM-FOR-30-ITR-301.1 Sprinkler Control Valve (V.171121) |  | LM-FOR-30-ITR-301.1 Sprinkler Control Valve (V.171121)
e8adbc84-b448-5119-bc35-7edd8200d05f | section | Installation
d43163db-8f22-5249-9081-91480c3ed8d4 | checkpoint | Latest consented drawings checked & referenced
031996a9-5d4f-5ceb-a05c-d8365c194211 | textbox | Drawing & Revision #
2327840a-ae01-5bd1-96ad-738c537c5246 | tickbox | Area clear, tidy and accessible
5e5107b3-940d-5e72-bd1d-78ddd02f34da | note | Attach Photos/Comments below if any issues & send report to Builder
d3785afd-be26-556a-8030-d4d52c7c0569 | checkpoint | Supply and Installation pipe works are installed in the correct position and alignment in accordance with the approved drawing/plan
2c03f732-01b0-5eb1-a1f7-51a4c41f25b0 | checkpoint | All supports are completely installed, spaced and bolted down box / assembly secured
fd5662df-1796-5fcf-b393-c5e715bcdaa7 | checkpoint | All roll grooved couplings / flanges are properly tightened
f35d70c8-3be5-5815-a8c4-980cb2f10ce9 | checkpoint | Valve station drain is properly connected to risers drain and building hydraulic drainage
020ced20-c291-5215-ac10-4a1390ec51be | checkpoint | Approved type of Monitored Main Stop Valve is fitted and operational
0acb40dd-f861-597c-a428-a342cf861149 | checkpoint | All specific signage is installed lock shut / lock open including FSV number of M/V’s
396a36da-12c0-540a-8273-786ebdc5d0e3 | checkpoint | Correct size and range of supply and installation pressure gauges with shut-off cocks are fitted
92f8e20c-4a42-5d08-9490-97da44447c0f | checkpoint | Correct type solenoid, flow switch, couplings etc installed
03a5b64c-cd23-4df1-8814-a7c0b7ee4262 | checkpoint | Correct size and range of supply and installation pressure gauges with shut-off cocks are fitted
eb6dee05-be6e-54f8-9543-4d4468a8937d | checkpoint | Confirm GFA on solenoid activation/ flow switch/ MV activation
847800a6-8275-5896-a5f4-84928decccd8 | checkpoint | Control Valve is positioned between 1150mm to 1800mm
d80d130d-72f8-5fc9-872b-1fc379f43b15 | section | Completion
b894fd15-4591-5de3-8256-45a1e534edc3 | checkpoint | Works completed to specification/drawings - Attach photos of work below
a61dbf31-a0c8-5b28-8cce-751e746f97a1 | note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
e5dc7dfb-b9b4-5125-bb46-5f6919da65f8 | button | Area left clean & tidy | Yes, No
33d1eee0-6c9b-5deb-8d0c-ad4f072cd0aa | tickbox | Leemark Sign-Off
985819f1-a936-54b0-b1d2-6b3ac938e0c0 | tickbox | Builder Sign-Off
dd71b766-5bfd-5126-8e81-631da7396226 | signoff | Sign-Off - click to Add signature(s)
bd691993-5177-5a69-887f-870a39c74f96 | checklist | LM-FOR-30-ITR-301.2 Alarm Control Valve (V.171121) |  | LM-FOR-30-ITR-301.2 Alarm Control Valve (V.171121)
e8adbc84-b448-5119-bc35-7edd8200d05f | section | Installation
d43163db-8f22-5249-9081-91480c3ed8d4 | checkpoint | Latest consented drawings checked & referenced
e2f7c154-fda3-5cad-86cd-a57bb1515507 | textbox | Drawing & Revision #
45abe4ce-ae72-53e7-a85d-6fd29f936516 | tickbox | Area clear, tidy and accessible
750da21c-329e-539a-a558-bf05fb7ce134 | note | Attach Photos/Comments below if any issues & send report to Builder
d3785afd-be26-556a-8030-d4d52c7c0569 | checkpoint | Supply and Installation pipe works are installed in the correct position and alignment in accordance with the approved drawing/plan
d3fc9e03-0727-5e20-a5c6-d87330da6161 | checkpoint | All supports are completely installed, spaced and bolted down
fd5662df-1796-5fcf-b393-c5e715bcdaa7 | checkpoint | All roll grooved couplings / flanges are properly tightened
8ec0a757-52bd-53e3-97a0-4a3c61680f43 | checkpoint | Correct size and specification of Alarm Valve is installed in accordance with the approved drawing/plan
020ced20-c291-5215-ac10-4a1390ec51be | checkpoint | Approved type of Monitored Main Stop Valve is fitted and operational
3d160c96-05f0-595d-a38c-5a544398af3c | checkpoint | Correct size of alarm line is installed, adequately supported and alarm gong is properly piped to drain
514df684-2414-5810-9f61-6726dc897609 | checkpoint | Correct size of orifice is fitted and piped to drain when system is with retard chamber
b1c5ba1f-c1bc-5729-9de5-3657f2e2c511 | checkpoint | Main waste & test valve is fitted and piped to drain
96d7ab67-182f-54a9-8ae8-cc85ff8fa282 | checkpoint | Correct type and model of Direct Brigade Alarm device is fitted
dfbe0cb1-770f-5d69-9efa-4fb35da5ce62 | checkpoint | Correct model and range of Pressure Switch is fitted
396a36da-12c0-540a-8273-786ebdc5d0e3 | checkpoint | Correct size and range of supply and installation pressure gauges with shut-off cocks are fitted
6415e286-60d7-5188-bfaf-1fab5bafe75d | checkpoint | All signalling devices (Monitored Stop Valve, DBA, Low Pressure Switch), are wired back to FIP
a44b2c31-0538-5a0e-ab55-3c5f70914026 | checkpoint | Control Valve associated pipe works paint touch-up repair is completed
d80d130d-72f8-5fc9-872b-1fc379f43b15 | section | Completion
b894fd15-4591-5de3-8256-45a1e534edc3 | checkpoint | Works completed to specification/drawings - Attach photos of work below
f84b20c7-dfc2-5955-9a40-f5ede67c0b5c | note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
78b69c8f-adee-5d4b-a693-7550d7ee511a | button | Area left clean & tidy | Yes, No
e940673d-7010-5827-9abd-770524b7880c | tickbox | Leemark Sign-Off
c474c6c4-4d90-5af3-802b-9682d91c97e1 | tickbox | Builder Sign-Off
dd71b766-5bfd-5126-8e81-631da7396226 | signoff | Sign-Off - click to Add signature(s)
88192c5b-0a9c-5bc6-b8d0-9a394b0722df | checklist | LM-FOR-33-ITR-401 Sprinkler & Hydrant hydrostatic test (V.171121) |  | LM-FOR-33-ITR-401 Sprinkler & Hydrant hydrostatic test (V.171121)
92773c79-21d7-53d1-87b7-e42ea3f7d786 | section | Guidelines
37f6445d-78dc-50c9-9d24-ef8faffb8fcf | checkpoint | Guidelines understood - Pass once read
7675f4a0-6f97-5ff3-8625-7be43d797ab1 | note | Guidelines: Fire Sprinkler Systems – –AS:2118.1 2017- 1600kPa or 400kPa above the maximum static pressure for a duration of 2 hours (Check notes on Construction Drawing for nominated test pressure)
7fee6fd4-9e1e-5f6c-b207-dee603acb662 | note | Fire Hydrant Systems (Low Rise) – 1700kPa or 15 times the design pressure for a duration of 2 hours (Check notes on Construction Drawing for nominated test pressure)
9f17401b-a3a7-5199-b88c-7abab99c1fc7 | note | Fire Hydrant Systems (High Rise) – 1050kPa at the highest hydrant in the pressure stage being tested If pressure reading is being taken at the booster, determine the height difference in metres between the top hydrant and the booster and add 10kPa per metre of static pressure to this figure with a minimum test pressure of 1700kPa If in doubt please seek clarification from the Construction Supervisor or the Design Manager
685b5e21-9405-579d-b8f2-96b5b9c79eca | section | Rough In Only OR Rough In & Fit Off Together
9f29aa77-6976-5d3a-adf3-e4d55f0fd7fe | checkpoint | First Sighting - Pass once entered
e17bdab2-119b-5951-9321-805d6dada841 | textbox | Date
352032bf-57ec-565f-bea0-6ee87938a765 | textbox | Time
08ba1a84-3609-5cbf-b4b7-5e66901a8453 | textbox | Pressure
1975a0a3-87ee-5f43-8395-0515fa7874f2 | button | Photo(s) taken | Yes, No
3c7ae15f-4045-5fd3-b1fd-82deceafc178 | button | Leemark Sign-Off - Attach below | Pass, Fail
0332dac3-cc52-526b-bf89-867d71728029 | button | Builder Sign-Off - Attach below | Pass, Fail, N/A
b1ca19d8-c57b-5fd0-ba00-fc40f8326b2b | checkpoint | Second Sighting - Pass once entered
82278996-59d9-5ca6-905a-71de12925bcc | textbox | Date
d894402c-1a77-5d80-abb7-9620bac740ee | textbox | Time
147160b8-0c3f-5b54-9eff-b001657cebb8 | textbox | Pressure
972fa139-c80f-5e94-8b85-3ef6bbb3ef04 | button | Photo(s) taken | Yes, No
1ae255c5-42f6-50bf-9eb0-70f07abf6eb7 | button | Leemark Sign-Off - Attach below | Pass, Fail
475eca55-fef3-5c3c-a01d-2f3d44aa38b1 | button | Builder Sign-Off - Attach below | Pass, Fail, N/A
2c24d488-7f93-5146-bd6c-2217a211c5d9 | section | Fit Off (if required ie if not covered by the above section)
b34488a6-cbcd-5004-90ee-040d52d2049a | checkpoint | Subsequent Sighting - Pass once entered
696b7229-e3fe-5604-bc09-3adac5e1fdb1 | textbox | Date
4aa79aee-e590-5ca8-9834-c28867c51f10 | textbox | Time
fbfd4ae1-fd5b-5d71-a30f-5ef5bd2f3f93 | textbox | Pressure
11aaeafe-2f85-5301-9cde-5d05b6d1dd20 | button | Photo(s) taken | Yes, No
abed6a55-2d4c-5fbc-bfe3-e32d296f3bff | button | Leemark Sign-Off - Attach below | Pass, Fail
3559c9bb-1644-546a-abf5-241c8c6aefce | button | Builder Sign-Off - Attach below | Pass, Fail, N/A
d80d130d-72f8-5fc9-872b-1fc379f43b15 | section | Completion
b894fd15-4591-5de3-8256-45a1e534edc3 | checkpoint | Works completed to specification/drawings - Attach photos of work below
a5dd776f-2387-52dc-a461-81cb3dd933c7 | note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
b3e83d4c-c71c-5612-820f-cf48420163d5 | button | Area left clean & tidy | Yes, No
424fad44-3d81-5f49-80c6-ea791f5e8a65 | tickbox | Leemark Sign-Off
1e0fa119-f3c6-5230-b0ca-1fa77c64297a | tickbox | Builder Sign-Off
dd71b766-5bfd-5126-8e81-631da7396226 | signoff | Sign-Off - click to Add signature(s)
1d9a6b85-b314-57e1-b893-51e07313d19b | checklist | LM-FOR-40-ITR-302.1 Fire Pump Installation (V.171121) |  | LM-FOR-40-ITR-302.1 Fire Pump Installation (V.171121)
e8adbc84-b448-5119-bc35-7edd8200d05f | section | Installation
d43163db-8f22-5249-9081-91480c3ed8d4 | checkpoint | Latest consented drawings checked & referenced
b48b8dfb-18b9-5d36-99f1-b113e04822cc | textbox | Drawing & Revision #
16b53e60-297e-5ce7-ba84-3cc387b36ffc | tickbox | Area clear, tidy and accessible
e759b49e-c464-540e-a6d1-ad78fdcf9b9d | note | Attach Photos/Comments below if any issues & send report to Builder
088de84c-7237-5409-a42f-feb36c8f8ecb | checkpoint | Pump installation arrangement including suction and discharge pipe works are in accordance with the approved drawing/plan
b5fbfde4-0c74-542c-b58d-694809739674 | checkpoint | Pump clearance is 1000 mm on all four sides and 600 mm between pumps
8f2e10e8-9575-5ab8-8165-b25201777363 | checkpoint | Concrete plinth/foundation height is minimum 150 mm from FFL and 150 mm wider on all four sides of pump base
edac107a-efde-5e62-9af3-dfed2596c240 | checkpoint | Pump base is sitting squarely and bolted down Vibration mounts are properly anchored on plinth or inertia plinth
01a764f3-2f59-5626-9bcc-616056b7c845 | checkpoint | Pump suction and discharge pipework are completely installed and connected Supports are adequately provided
38f23645-ec05-57bb-861d-135b6dc7d167 | checkpoint | Control panels installed and bolted down, MFB have clear access around pump controller 1000mm Arc
ec285001-c249-5b2a-8e24-a47bd2c5c20a | checkpoint | Suction isolation valve installed is OS & Y type
566dde6f-9a61-5df3-8a1a-eece6a730b20 | checkpoint | Non-return valve is installed and located upstream of the isolation valve in pump discharge line
a0d82dfa-4bc5-53dc-8529-d43d2ab74294 | checkpoint | Pump circulation-relief valve for electric driven pump is installed and piped to drain or tank return line
a900469f-df76-51a7-9216-e212268a75b9 | checkpoint | Heat exchanger cooling water harness for diesel driven pump is installed and piped to drain or tank return line
40149c62-d8a8-5112-ad80-b67530f230a1 | checkpoint | Pressure gauge with gauge cock is installed min 2Ø downstream of discharge flange or reducer
201a2fc1-191f-5904-b0ff-fc4256a3501a | checkpoint | Pressure reductions installed on manifold x2 for each stage with M/V’s and Annubar for each stage
e908e4fa-140d-54c0-be7e-53b7dc4af6be | checkpoint | Exhaust connected to pump and installed to approved discharge location
5dbf94f6-eb2a-5556-8a79-42892c8c95c9 | checkpoint | Full tanks have been filled with Diesel; Electric Pumps AND Controls ready for energisation
d80d130d-72f8-5fc9-872b-1fc379f43b15 | section | Completion
b894fd15-4591-5de3-8256-45a1e534edc3 | checkpoint | Works completed to specification/drawings - Attach photos of work below
a6d2f41e-83fb-5041-ae58-4b76ba8d0123 | note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
cbf386ce-b5ae-5340-86ac-7bd996228d8e | button | Area left clean & tidy | Yes, No
9e2e6ec7-0c50-518e-a288-93b43c315a60 | tickbox | Leemark Sign-Off
50d546b1-47ad-5a0f-8423-a26eb4a1591f | tickbox | Builder Sign-Off
dd71b766-5bfd-5126-8e81-631da7396226 | signoff | Sign-Off - click to Add signature(s)
eb3fcee0-101f-5039-8a5d-5cfb1ef373dd | checklist | LM-FOR-40-ITR-302.2 Hydrant Installation (V.171121) |  | LM-FOR-40-ITR-302.2 Hydrant Installation (V.171121)
e8adbc84-b448-5119-bc35-7edd8200d05f | section | Installation
d43163db-8f22-5249-9081-91480c3ed8d4 | checkpoint | Latest consented drawings checked & referenced
ff1ebb66-c0fb-5128-814a-3cfcdc572d5b | textbox | Drawing & Revision #
473a3de3-0a52-51e1-8ff7-4d9181d66715 | tickbox | Area clear, tidy and accessible
0a6ed5e4-4e14-56c8-9e3e-dbb2d9774d87 | note | Attach Photos/Comments below if any issues & send report to Builder
59f9cfca-ea88-5bc2-81a1-299d5b94c2ce | textbox | Hydrant No.
3ad39dfa-233e-508c-b2af-4b1a5c953960 | checkpoint | Hydrant supply pipe works completely installed of correct size, position, elevation, alignment and adequately supported in accordance with approved drawing/plan
06646595-6c37-5aae-b53d-227d691d117a | checkpoint | Hydrostatic pressure testing of installed supply pipe works completed and accepted
6dd48c80-a7e0-5e34-afe3-6e37361dbe02 | checkpoint | Hydrant valves and associated pipes and fittings used are in accordance with the approved specifications and applicable codes/standards
870639f6-6e97-58a9-b081-c3224a30ec67 | checkpoint | Fire Hydrant and associated fire water main isolation valves locations are in accordance with the approved drawing/plan
9f51d2d1-c512-5015-bb7f-82d665b55dfc | checkpoint | Hydrants stand pipe is adequately supported and bolted down. Concrete surround block provided for external hydrant
62596d7c-83a4-5c3b-af45-020d35e5ff07 | checkpoint | Hydrant valve is between 750 to 1200 mm from finish floor/grade level
32192ebb-9b3e-5ee2-acfd-1d35310b4022 | checkpoint | Valve outlet is facing away from the wall and not more than 35O below its horizontal axis. Minimum 300 mm clearance around the valve outlet
1fef2f25-8b2d-5a27-89c4-1942ce6fc623 | checkpoint | Minimum 1000 mm clear space in front of valve outlet is provided
019bc049-244c-53ba-999c-b2517ef64ae3 | checkpoint | Valve handwheel clearance is minimum 100 mm clear of any obstruction at fully open
d80d130d-72f8-5fc9-872b-1fc379f43b15 | section | Completion
b894fd15-4591-5de3-8256-45a1e534edc3 | checkpoint | Works completed to specification/drawings - Attach photos of work below
858b3ff8-679c-5786-8b32-66545b1fea39 | note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
079dfc80-fd79-542f-90ea-e8ae8c171c92 | button | Area left clean & tidy | Yes, No
bf639abd-2775-54de-8db7-18893848f770 | tickbox | Leemark Sign-Off
638bbcec-15bc-5265-b1ff-c808567c14bb | tickbox | Builder Sign-Off
dd71b766-5bfd-5126-8e81-631da7396226 | signoff | Sign-Off - click to Add signature(s)
16e4cc4f-b64f-585e-9f62-d63041a9c5e9 | checklist | LM-FOR-40-ITR-302.3 Hose Reel Installation (V.171121) |  | LM-FOR-40-ITR-302.3 Hose Reel Installation (V.171121)
e8adbc84-b448-5119-bc35-7edd8200d05f | section | Installation
d43163db-8f22-5249-9081-91480c3ed8d4 | checkpoint | Latest consented drawings checked & referenced
766be16c-1765-5808-8442-f66c82ed0bb6 | textbox | Drawing & Revision #
51f6f79f-60d5-530a-bdf7-e6c78a3fe0ca | tickbox | Area clear, tidy and accessible
7fd7a9f0-e9d7-566b-b2d2-a290311647e6 | note | Attach Photos/Comments below if any issues & send report to Builder
2d644428-615c-50ae-8e00-475a211edbdc | textbox | Hose Reel No.
0a0ba801-62d8-5411-8fd2-e62b89ec489a | checkpoint | Hose Reel supply pipe works completely installed of correct size, position, elevation, alignment and adequately supported in accordance with approved drawing/plans
9a560a4c-13d4-5f50-8c39-47261e5490df | checkpoint | Hydrostatic pressure testing of installed pipe works completed and accepted
019a9076-e1ad-5356-adf7-563652796e3d | checkpoint | Hose Reel and associated valves, pipes and fitting used are in accordance with the approved specifications and applicable codes/standards
68e507bf-ead5-560b-a688-7603bb25521f | checkpoint | Hose Reel located along normal path of travel to nearest exit and readily accessible
eb9f5050-c8de-532d-9dc5-da6b70ff4a7a | checkpoint | Verify and confirm hose length to be 36-metres or 40-meters
45451fa0-1bf7-53f4-b8ed-6b06940972f8 | checkpoint | Hose reel spindle is 1400 mm minimum to 2400 mm maximum above floor level. Stop valve is 1000 + 100 mm above floor level
a1e04f8e-49bc-56f2-ac27-9b0ad786e687 | checkpoint | Minimum radial clearance of 100 mm between the reel rim and cabinet/cavity to the sides, above and below
94b42990-a21a-5f54-8bb2-a971b1a32857 | checkpoint | Minimum 100 mm clearance around the stop valve handwheel/handle
7ad936be-f917-5485-bca1-b98389e38723 | checkpoint | Any defects found on the hose reel assembly have been corrected
d80d130d-72f8-5fc9-872b-1fc379f43b15 | section | Completion
b894fd15-4591-5de3-8256-45a1e534edc3 | checkpoint | Works completed to specification/drawings - Attach photos of work below
31b8cde2-6ffb-562f-a516-c692545293a3 | note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
a3fce89e-560b-5838-887a-e67bb388b8f7 | button | Area left clean & tidy | Yes, No
d6fde23e-3e6a-524f-98d4-3feba888f302 | tickbox | Leemark Sign-Off
cba21e20-7011-51cc-976a-dc376da6b6db | tickbox | Builder Sign-Off
dd71b766-5bfd-5126-8e81-631da7396226 | signoff | Sign-Off - click to Add signature(s)
d5df36a4-5d0c-5a08-8ecc-82d8c9b5263b | checklist | LM-FOR-40-ITR-302.4 Tank Installation (V.171121) |  | LM-FOR-40-ITR-302.4 Tank Installation (V.171121)
e8adbc84-b448-5119-bc35-7edd8200d05f | section | Installation
d43163db-8f22-5249-9081-91480c3ed8d4 | checkpoint | Latest consented drawings checked & referenced
6253daff-8279-5e3e-9f5d-1ad793106a26 | textbox | Drawing & Revision #
0538600c-205a-5631-9916-dd0e97e1b081 | tickbox | Area clear, tidy and accessible
3d22d99b-f930-535a-8fd2-1734bfc8b751 | note | Attach Photos/Comments below if any issues & send report to Builder
fd3c03e9-fc9a-5a78-9d70-10f7a48db3a8 | checkpoint | Tank installation/construction is completed including associated pipe works in accordance with the approved drawing/plan
39198f89-8b94-5dce-9d1a-e8c9c5d50920 | checkpoint | Tank is free from dents, buckling, cracks, and internal is clean and free of any debris and construction materials
1d16e36f-f44c-54d7-9d9d-ffe52085a008 | checkpoint | Tank internal liner (if provided) is complete and properly bonded to tank wall/shell
8cd4155e-ef4f-5846-8b78-34a58067c6f9 | checkpoint | Tank quick infill line including associated infill valve and isolation valve installed and adequately supported
d80b7b8b-af10-50bc-b571-884c1f5277b8 | checkpoint | Tank suction isolation valve is fitted in the correct position and operational in accordance with the approved drawing/plan
0a825d98-eb7f-5f1d-af42-a304a6dbad6b | checkpoint | Tank suction vortex inhibitor is fitted in the correct position and elevation in accordance with the approved drawing/plan
5812f02d-de35-5c01-b99d-30c3acd9fc37 | checkpoint | Tank overflow is fitted in the correct position, elevation and properly piped to drain Adequate drain available
c9b6905d-5eb3-5b7b-a8fc-8585fbea4849 | checkpoint | Tank drain/sludge isolation valve is fitted and blank off
989ad281-8267-525f-99fe-cbcfb81b1cd1 | checkpoint | Tank external water level indicator is fitted and operational
1f0fb308-8ece-5553-98d5-c95bdbf13241 | checkpoint | Tank internal and external access ladders are fitted & secured
5b3e6fc0-2162-593c-b068-78802c90d062 | checkpoint | Tank access hatch is fitted and provided with lockable cover
2ecb7980-f135-5426-bb2d-9334db848cab | checkpoint | Ball float for infill pilot line is fixed tightly, close to the manhole and away from the discharge path of tank infill
59469748-c96a-5fdc-ade7-8862fbc201cf | checkpoint | Tank is located with minimum of 600 mm clearance around tank perimeter and roof line
d80d130d-72f8-5fc9-872b-1fc379f43b15 | section | Completion
b894fd15-4591-5de3-8256-45a1e534edc3 | checkpoint | Works completed to specification/drawings - Attach photos of work below
fcfbbed9-a2b1-5cf8-8636-996504019419 | note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
aee91bbb-6e94-504a-9ba6-ef60610a59c5 | button | Area left clean & tidy | Yes, No
1872cca3-5dbc-5a60-8279-c20c2c6af89a | tickbox | Leemark Sign-Off
d87d144e-86ad-5e1e-9f26-777b524e2c6d | tickbox | Builder Sign-Off
dd71b766-5bfd-5126-8e81-631da7396226 | signoff | Sign-Off - click to Add signature(s)
a10f1b6c-559f-5254-acff-dc82d4c06081 | checklist | LM-FOR-40-ITR-302.5 Booster Assembly (V.171121) |  | LM-FOR-40-ITR-302.5 Booster Assembly (V.171121)
e8adbc84-b448-5119-bc35-7edd8200d05f | section | Installation
d43163db-8f22-5249-9081-91480c3ed8d4 | checkpoint | Latest consented drawings checked & referenced
0666fe68-39d4-5b87-9319-5964f619469d | textbox | Drawing & Revision #
74afbd17-185b-5a38-910f-e1a22eb73de0 | tickbox | Area clear, tidy and accessible
33518840-c967-513d-891c-d6f8a147efae | note | Attach Photos/Comments below if any issues & send report to Builder
02330769-6dc6-56ab-abee-4c0c7f30c5a2 | checkpoint | All pipework are installed in the correct position and alignment in accordance with the approved drawing/plan
aa9af366-5ef8-5499-b32b-bfeabd0bbea3 | checkpoint | All pipework have been pressure tested and accepted in accordance to approved pressure testing procedure
726e5cc5-80bb-5e9b-a416-d061faecc85f | checkpoint | Fire Brigade Booster is located within sight of the main entrance to the building
49217c89-1ea9-51b9-a67e-a30c75031e08 | checkpoint | Concrete plinth provided for the booster location and hard stand for fire brigade pumping appliance
61a42766-6df9-5712-9344-ff5c15123e63 | checkpoint | Feed Hydrant is located within 8 metres from fire brigade appliance hard stand
281e6307-2396-5dd0-bfd7-37210533bc0a | checkpoint | Fire water storage tank suction point (Storz) is located within 4 metres from fire brigade appliance hard stand
b63456b9-9fdf-5eac-b80b-25eab8b6594e | checkpoint | Fire water storage tank suction point (Storz) is located within 10 metres from fire brigade booster inlet connection
42aab1ba-eb65-5840-8436-517c6a0f7946 | checkpoint | Centre distance between feed hydrant and booster inlet connection is 450 mm minimum and 5 m maximum
0d493d1c-a6ea-5a1b-9e30-357e76e04117 | checkpoint | The height of Feed Hydrant Outlet and Booster Inlet Connection is minimum 750 mm and maximum 1200 mm from FFL
93f6c0ce-d88a-5025-9fce-0e142eead985 | checkpoint | Valves face minimum 150-mm from door and valve handles are 100-mm from cabinet sides
a65cceaa-58ba-53c7-a0f0-a3b3f7f7b3b4 | checkpoint | The number of feed hydrant outlet installed is equal to number of fire brigade booster assembly inlets
ee65e64e-5dfb-5516-ada4-59fab3844e8c | checkpoint | The required number of fire brigade booster inlets installed is suitable for the system requirement or minimum of 2 inlets
dcc370b8-0c61-5341-8bb9-f98a73fa294b | checkpoint | Full flow non-return valve of correct size is installed in the proper location
e25ef715-9194-53ea-8a9f-c560ccb14a2b | checkpoint | Approved type of cabinet enclosure is installed as required
d80d130d-72f8-5fc9-872b-1fc379f43b15 | section | Completion
b894fd15-4591-5de3-8256-45a1e534edc3 | checkpoint | Works completed to specification/drawings - Attach photos of work below
1c30f14f-2dde-5c2c-a7a6-8c871001a199 | note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
22588b54-61ed-503a-9509-5021d518cfb9 | button | Area left clean & tidy | Yes, No
ff034178-d8b7-56b5-ac3e-a1bc3cb0d558 | tickbox | Leemark Sign-Off
651828ff-b004-5725-bf5b-bdc6ef6cc3ed | tickbox | Builder Sign-Off
dd71b766-5bfd-5126-8e81-631da7396226 | signoff | Sign-Off - click to Add signature(s)
6b522396-2fff-58b3-a65e-f10748f518d6 | checklist | LM-FOR-50 ITR 303.7 ASD (Aspirated) Installation (V.171121) |  | LM-FOR-50 ITR 303.7 ASD (Aspirated) Installation (V.171121)
f438efa3-e1ae-57f1-a2c2-5d28b2b87130 | section | Pre-commissioning Procedures
043a59d9-20e3-5bf3-9785-4631f0ba841d | checkpoint | Check the location of installation is as per approved shop drawings and manufactures recommendations
03d74146-47e0-51d0-a621-1a77c0e4b314 | checkpoint | Check the Height of Panel is as per manufacturer's recommendations and in accordance with the relevant Australian Standards
ab880840-eedd-5a29-b413-1761c4b80a97 | checkpoint | Confirm operation of auto-reset from FIP is wired through GP relay
9a3d0395-71af-5fe0-b930-7d5ce3b035bd | checkpoint | Check all wiring connections are tight and secure
3db095a8-e7e5-5f29-9787-f072f299daff | checkpoint | Check routing of the conduits are as per approved shop Dwg’s
ea990434-baba-5511-a4bc-a3483bfb1ddd | checkpoint | Check joints are properly glued /sealed and bonded to eliminate any potential air leaks
2222636b-c705-526a-8a7f-610a48c84514 | checkpoint | Check pipe joints at the inlet ports of the scanner are not glued but firmly fitted into air inlet socket
b0a4fad3-2ece-52a8-aec2-a5d0aa84584f | checkpoint | Check the sensing holes are drilled as per design
3c009ef3-dd00-5a3f-9b0d-c2a1bd5a9824 | checkpoint | Confirm the exhaust has been routed back into the sampling space
632db992-6d68-5598-8b64-5c7f1d98080a | checkpoint | Confirm end caps have been installed un-glued to all pipes at a serviceable height
16e26e87-191f-5e7a-86b2-f6ab0719d962 | checkpoint | Confirm wiring is complete to Action, Minor Urgent, Fault & Fire relays and monitored via the FIP.
bdd5cda7-43e6-5934-bc03-37a69b742c8c | section | Commissioning
127bd386-46de-5864-8bef-0750195b55d3 | checkpoint | Power up the system, the aspirator starts up and air is flowing out of exhaust port , LCD screen is operational.
69b54bf2-dc5c-5435-be9a-a910ef3c656a | checkpoint | Induce smoke into the furthest sampling point from the head end unit
c4efa3ee-f2dc-52d2-ae21-5aa2e6ff4488 | checkpoint | Check that a Fire signal is being transmitted to the FIP within 60s of smoke entering the VESDA pipe
deaa64da-ae81-53c7-b4ed-a8343839670d | checkpoint | Check the correct signals are being transmitted to the FIP via Action, Minor Urgent & Fire Relays correctly.
df4c7153-17c9-5565-97e6-1249b4608be7 | checkpoint | Remove the power from the VESDA and confirm Fault is received at the FIP
06cb9c56-e38c-5c93-bf9d-0caefa0c8e83 | checkpoint | Check the fire signal is conveyed to the fire Alarm system and BMS, if required
ce813563-8336-597e-9e40-a16b2b779709 | checkpoint | Check the transmission of signals to operate ancillary devices, if required.
6ed90022-de9c-5452-9730-7faff9e18bcd | checkpoint | Record all baseline data as required
a85bd0bc-9e55-5cc3-8eea-e51142530c2a | checklist | LM-FOR-50-ITR- 303.5 Fire Detection Fit Off (V160421) |  | LM-FOR-50-ITR- 303.5 Fire Detection Fit Off (V160421)
11ea1445-3c9d-5c50-9466-57b90f1ad9ec | section | Fit-Off
d43163db-8f22-5249-9081-91480c3ed8d4 | checkpoint | Latest consented drawings checked & referenced
39415713-177b-5290-bb66-3662c6dead3a | textbox | Drawing & Revision #
0f585856-8ce5-5a68-9a8e-5a56787bb72d | tickbox | Area clear, tidy and accessible
50797ca4-5008-59ee-b0ed-6d71cae27a0b | note | Attach Photos/Comments below if any issues & send report to Builder
d2aa0f2e-43f6-531a-a774-441d8c7d5b0c | checkpoint | Have all devices been installed in the correct position with no obstructions
7849beb6-b62b-56d7-8bdb-e34ef1d29a87 | checkpoint | Have all detectors been installed in the correct position and addressed
0a27b38e-4a4b-5422-aeda-ebb518ba0022 | checkpoint | Have all input/output modules been installed in the correct position and addressed, with all enclosures sealed
0b00d4e3-f653-5293-a0c8-12c57a4ccbbe | checkpoint | Have all magnetic door holders been installed correctly
25b3ee31-4380-5497-98c2-84ec231124a4 | checkpoint | Have all input/output devices been installed and addressed for security fire trips
48d381f9-eb27-5d96-bbfe-8a8da3ed02cc | checkpoint | Have all input/output devices been installed and addressed for mechanical fire trips
376ff4bf-42c5-59ae-aec8-1c0c54773056 | checkpoint | Have all input/output devices been installed and addressed for AS 1668 Fan Controls
d37751de-aecb-5290-9542-7c0a9afe9799 | checkpoint | Have the ELV and LV segregation rules been applied as per AS/CAS 009 (including 90 degrees crossovers) – Double check to make sure no other trades have been in after fire works
c1003bbd-6a75-56c3-b9d5-c3b1d211f0c7 | checkpoint | Have all cables and conduits been installed in the correct position for devices
6b59f6dc-3f60-599c-8a5a-6af5e10ee3fd | checkpoint | Have all devices been terminated for testing purposes
ec30b90e-7ee3-512c-b0ee-d309d137d2bf | section | Cable Feeds
5312575f-67ec-51e1-b91b-9d9965176552 | checkpoint | Have all cable feeds been connected to the first device
daad72c8-62e2-5ce3-b6e1-c487f697af88 | checkpoint | Have all cable feeds been connected to the last device
e243cc04-4750-5916-99bf-48d2e0581a61 | checkpoint | Have cable feeds been connected at the panel
11b3a826-b908-5473-b2f4-a4da7f1b23f4 | section | Visual Check
3d92684e-b9fd-540d-91ca-14d8649f0c47 | checkpoint | Check that no other services are run with or attached to fire detection cables
849a0bf2-9aee-5c6e-b51d-d949c1684357 | checkpoint | Check that no cables have been damaged
c7074107-d9be-5908-bfe2-d39aa6f19ad7 | checkpoint | Check that all final cable locations are correct and match up with the “For Construction Drawings” and “Reflected Ceiling Plans”
12fedbea-0cf1-5f72-bf6a-a716357aa06c | checkpoint | Check that all address tags and labels are clear and readable
730b71db-d281-5daa-b636-6470c0180bc8 | checkpoint | Have devices and address been noted on “As Constructed Drawings” for handover
43a7ec54-bb62-5908-be77-3bc83a24d443 | checkpoint | Have all stickers been installed to fire rated walls and smoke walls for penetrations
144fcaec-399f-590d-bb2b-670302d87a4e | checkpoint | Has photographic evidence been taken and recorded for all penetrations?
d80d130d-72f8-5fc9-872b-1fc379f43b15 | section | Completion
b894fd15-4591-5de3-8256-45a1e534edc3 | checkpoint | Works completed to specification/drawings - Attach photos of work below
8e85bcca-d32b-52a1-b941-06fe7608e201 | note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
b065cc30-99fe-5cec-8827-d1a6b6fdad5a | button | Area left clean & tidy | Yes, No
22d35957-8f31-59cf-bb04-93e0fc0046c5 | tickbox | Leemark Sign-Off
9a355fb2-181a-5d47-bf26-426e0030bca8 | tickbox | Builder Sign-Off
dd71b766-5bfd-5126-8e81-631da7396226 | signoff | Sign-Off - click to Add signature(s)
6dd3d15d-d07b-5cde-9603-82d7e92084da | checklist | LM-FOR-50-ITR-303.1 Fire Panel Installation (V.171121) |  | LM-FOR-50-ITR-303.1 Fire Panel Installation (V.171121)
907e5889-d4f6-5070-8f08-309d964bd6f3 | section | Fire Indicator Panel
d43163db-8f22-5249-9081-91480c3ed8d4 | checkpoint | Latest consented drawings checked & referenced
595d8463-6ddf-502d-a2e7-6db763ee9ecf | textbox | Drawing & Revision #
ba90e81a-a458-51b7-a627-a051c1499b87 | tickbox | Area clear, tidy and accessible
d0bcabb5-5a9c-5c94-8e2a-957f94610040 | note | Attach Photos/Comments below if any issues & send report to Builder
b2321c59-c4ab-5204-9f78-925a10f24437 | checkpoint | Are visual indicators and controls not less than 750 mm from the floor
8d9420f8-3f4a-52bb-bdee-e37e86968544 | checkpoint | Are visual indicators and controls not more than 1850 mm from the floor
f3414b2e-0611-5d3e-9aa6-a71d36094086 | checkpoint | Connected to Brigade - Is the fire indicator panel clearly visible and readily accessible within the designated building entry point or the fire control room
fe2377a1-3943-57e2-9c4c-5a62fc52b9fc | checkpoint | Not Connected to Brigade - Is the fire indicator panel in a secure location and clearly visible and readily accessible to authorized personnel
8778cc5a-77c4-534d-b2b8-78002ad04a20 | section | Accessibility
b93d4820-97ae-59f3-854d-2f2d38652b82 | checkpoint | Is the fire indicator panel obscured by a door (if No, continue to CLEARANCE)
603a7921-9d56-5fd1-834d-a1bbf9d9090b | checkpoint | Is the door marked in a contrasting colour to the general colour scheme with the words “FIRE PANEL” in letters not less than 50mm high
6b200959-ed86-545f-893a-fe58a320bfb7 | checkpoint | Is the door absent of locks
09d7dc5b-fcb7-5c6c-b5e4-177e55cc4984 | checkpoint | Where the door reduces the CIE sounder sound level below the CIE requirement, means are provided to give the required sound level outside the covering door
5d17514e-94f8-53c9-9617-916f99c012b4 | checkpoint | A minimum clearance is maintained from the enclosure as shown
00b38fe1-76e5-5bb7-9e80-36cd52f57442 | section | Power sources
9a9de1ef-07c7-57e4-a9f2-4a335f4e5ed0 | checkpoint | Is the battery enclosure located such that the batteries are readily accessible for inspection
3dd2c6ae-db7f-5bbb-a4c6-245bdd6d0b51 | checkpoint | Are the connecting leads to the battery clearly labelled to reduce the possibility of reverse connections to the battery
dc9739e5-17ee-51bd-8761-52ccef9a06a6 | checkpoint | The battery is not be tapped for intermediate voltages
6202645d-663b-5604-8467-362363fa59d9 | checkpoint | All connections are made using suitable connectors
2519d09b-5217-5412-9e48-c50fa10b6235 | section | Sub-Indicator Panels
8c5d1c3c-3915-54b2-8798-6cfcc3a10f35 | checkpoint | The SIP shall only serve areas on one level of a building unless - Pass once below considered
224df418-8b6d-553d-baf8-9cb5360e069d | button | (a) The SIP serves the entire building | Yes, No, N/A
0272eb84-3d08-59e8-85c2-761de48cb115 | button | (b) All zones connected to the SIP are readily accessible without leaving the area served by the SIP; or | Yes, No, N/A
e70bfc1f-e1e7-5226-af72-fb49dae25657 | button | (c) The location of each zone in alarm at the SIP can be identified at the designated building entry point | Yes, No, N/A
7a431d19-71be-5f7d-86be-133adb1f1794 | button | Where the SIP serves the entire building, it shall be installed in accordance with the requirements for an FIP | Yes, No, N/A
223c9c09-dae4-5fa1-a547-f8b11a312b82 | button | If the SIP serves a specific area, is it located at the main point of entry into that area | Yes, No, N/A
2423cd6a-ced2-52e0-9dce-335ce826af4a | section | Wiring
bbf5f778-c421-5bbc-b8d4-c1512f178773 | checkpoint | The extra low voltage wiring of the fire detection and alarm system is be kept separate and distinct from all other systems
5155e46d-ede8-583f-a8b8-11b412557c82 | checkpoint | The extra low voltage wiring of the fire detection and alarm system is installed in accordance with the requirements of AS/ACIF S009
51be89ab-4777-5453-bb75-8652f1759edd | checkpoint | Other wiring is installed in accordance with the electrical safety requirements of AS/NZS
c95c3c84-0a8d-552c-b50c-6d3b7fb0e33d | checkpoint | Externally energized circuits at voltages in excess of extra low voltage, except the power source for CIE, do not enter any CIE enclosure
d80d130d-72f8-5fc9-872b-1fc379f43b15 | section | Completion
b894fd15-4591-5de3-8256-45a1e534edc3 | checkpoint | Works completed to specification/drawings - Attach photos of work below
5901b22b-0656-59ce-8788-baaa6da739e5 | note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
c58eddf1-bfdd-54cd-9460-cc7c3994576c | button | Area left clean & tidy | Yes, No
6328d84b-6f97-51f0-a4f4-dd50f85fee3e | tickbox | Leemark Sign-Off
7458a519-16f3-56e5-a483-53f8c643bb47 | tickbox | Builder Sign-Off
dd71b766-5bfd-5126-8e81-631da7396226 | signoff | Sign-Off - click to Add signature(s)
da686d6f-057c-520e-81b6-46dda9467055 | checklist | LM-FOR-50-ITR-303.2 Ewis Installation (V.171121) |  | LM-FOR-50-ITR-303.2 Ewis Installation (V.171121)
a1596c2a-5d45-5fea-8352-c94c52f08b6b | section | Cabling
d43163db-8f22-5249-9081-91480c3ed8d4 | checkpoint | Latest consented drawings checked & referenced
d28138c0-dcd7-5eb8-9b80-c3c61cc1a6e9 | textbox | Drawing & Revision #
a50b7f47-7216-5fc6-8bec-765457be82be | tickbox | Area clear, tidy and accessible
3c45c1a6-2d5c-5691-b6c8-8235b84d3911 | note | Attach Photos/Comments below if any issues & send report to Builder
9ae80a36-2d4e-54c1-a46a-2270b153ec8e | checkpoint | Have all cable supports been installed in the correct position with no obstructions
dd05b8ac-5e35-591c-ba53-1546ab3c9f01 | checkpoint | Have all cables been cable tied to soffit / catenary wire with no sagging or obstructions
576269da-5339-5bd6-8d11-bd6c9fad8bde | checkpoint | Have all cables been installed for speakers and horns
b983e950-b9a4-54e2-9968-d7007648de8b | checkpoint | Have all cables been installed for warden intercom points
32d23c76-d73f-5725-b9b7-1a0069b09a43 | checkpoint | Have all cables been installed for emergency call points
d12335ee-1558-537f-a0ac-e43c85b928ef | checkpoint | Have all cables been installed for strobes
489271ce-8c44-5dd2-8849-71672f2419d9 | checkpoint | Have all cables been installed for background music inputs
7b5002de-2316-53a9-bebf-5feac5a1a764 | checkpoint | Have all cables been installed for microphone inputs
7785cce1-a604-5189-8a9d-226566584938 | checkpoint | Have the ELV and LV segregation rules been applied as per AS/CAS 009 (including 90 degrees crossovers)
48a40f21-0cd7-58de-9e97-f9fe7aa07773 | checkpoint | Have all cables been installed in the correct position for devices
944335ec-5d96-54bc-a05c-fae87484f55b | checkpoint | Have all cables been joined through for testing purposes or fitted with end of line devices
ec30b90e-7ee3-512c-b0ee-d309d137d2bf | section | Cable Feeds
e1ebfc71-fc7f-4eb2-9eb0-517d2ee95f7b | checkpoint | Have all cable supports been installed in the correct position with no obstructions
50fb123c-916f-546a-9f79-05b976d719eb | checkpoint | Have all cable feeds been installed in the correct position
a9146f1f-94df-594d-89fa-8117510750cb | checkpoint | Have all cables been tied to cable tray with steel ties with no sagging or obstructions
de05cfd0-93f4-5afe-9e3a-2d6ed7a50015 | checkpoint | Have all cable trays been installed correctly and secured including joiners and bends
37bd51dd-4cd7-5fc5-bff3-96fa0d81631b | checkpoint | Have the modified cable trays been re-galvanized
11b3a826-b908-5473-b2f4-a4da7f1b23f4 | section | Visual Check
d2c93664-6131-5454-9f1d-51eec9232fd2 | checkpoint | Check that no other services are run with or attached to occupant/emergency warning cables
849a0bf2-9aee-5c6e-b51d-d949c1684357 | checkpoint | Check that no cables have been damaged
06d26023-9d83-52e2-a647-4fef39e94ed3 | checkpoint | Check that all final cable locations are correct and match up with the “For Construction Drawings” and “Reflected Ceiling Plans”
8d76a686-6c75-530c-844e-0daf6b45458b | checkpoint | Have all cable runs, cable trays and penetrations been mark on “As Constructed Drawings” for handover
43a7ec54-bb62-5908-be77-3bc83a24d443 | checkpoint | Have all stickers been installed to fire rated walls and smoke walls for penetrations
b41d9cc1-5fe2-5955-9af8-f7b4eeb59fe6 | checkpoint | Has photographic evidence been taken and recorded for all penetrations
d80d130d-72f8-5fc9-872b-1fc379f43b15 | section | Completion
b894fd15-4591-5de3-8256-45a1e534edc3 | checkpoint | Works completed to specification/drawings - Attach photos of work below
96e752c0-7d61-5c12-8964-f4a5e16d8d5b | note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
f3c39177-ccfe-5676-ac36-aa50e75572b9 | button | Area left clean & tidy | Yes, No
cbbac449-61e7-556c-a5a9-b42c715f1682 | tickbox | Leemark Sign-Off
6ec1091d-8235-5143-affd-ca28f9430d14 | tickbox | Builder Sign-Off
dd71b766-5bfd-5126-8e81-631da7396226 | signoff | Sign-Off - click to Add signature(s)
1eee7017-f159-5b27-a3ea-e45191d1603d | checklist | LM-FOR-50-ITR-303.3 Ewis Installation Fit Off (V.171121) |  | LM-FOR-50-ITR-303.3 Ewis Installation Fit Off (V.171121)
1603ca4e-b1fc-5389-a8d3-ea92f6a40b0d | section | EWIS Fit-Off
d43163db-8f22-5249-9081-91480c3ed8d4 | checkpoint | Latest consented drawings checked & referenced
25a2aaa8-437d-5000-8552-2b947c58a481 | textbox | Drawing & Revision #
5b1bca4a-957c-51da-9295-ef805fa35a55 | tickbox | Area clear, tidy and accessible
9874e39f-e7e0-51f8-a474-bd2e9fb63a17 | note | Attach Photos/Comments below if any issues & send report to Builder
d2aa0f2e-43f6-531a-a774-441d8c7d5b0c | checkpoint | Have all devices been installed in the correct position with no obstructions
49454916-dea8-5435-9c54-d3793e3e3880 | checkpoint | Have all speakers / horns been installed in the correct location
8d97f643-5fa6-5d93-b000-ab1b709f3ed2 | checkpoint | Have all warden intercom points been installed in the correct location
1156b0a2-bbaa-5ea9-9a27-df75c1972106 | checkpoint | Have all emergency call points been installed in the correct location
8aad9d8f-484a-54f2-95cc-dc7f0b25f183 | checkpoint | Have all strobes been installed in the correct location
c8fd860e-f16b-5059-a3ef-427095de55c1 | checkpoint | Have all background music points been installed in the correct location
d338d7dd-107d-50c0-8d81-c2244cef04c3 | checkpoint | Have all microphone points been installed in the correct location
d90bbf6d-30e1-520c-981c-fdd1d78ab0ff | checkpoint | Have the ELV and LV segregation rules been applied as per AS/CAS 009 (including 90 degrees crossovers) – Double check to make sure no other trades have been in after warning system works
c1003bbd-6a75-56c3-b9d5-c3b1d211f0c7 | checkpoint | Have all cables and conduits been installed in the correct position for devices
6b59f6dc-3f60-599c-8a5a-6af5e10ee3fd | checkpoint | Have all devices been terminated for testing purposes
ec30b90e-7ee3-512c-b0ee-d309d137d2bf | section | Cable Feeds
6c6c5aba-aa62-5851-a7e1-afb729a0e67d | checkpoint | Have all cable supports been connected to the first device
7108a3c5-6748-54e7-b97d-b9fb83890383 | checkpoint | Have all end of lines been fitted and measured
7314b1f3-cb17-5760-84ea-7f6e7620ed65 | checkpoint | Have cables feeds been connected at the panel
11b3a826-b908-5473-b2f4-a4da7f1b23f4 | section | Visual Check
57ec8c66-0fd8-5ebd-9ce2-594ae0f23d7e | checkpoint | Check that no other services are run with or attached to occupant/emergency warning cables or devices
512764d8-a9cd-58a4-ae76-7f62f8ee5bf5 | checkpoint | Check that no cables or devices have been damaged
b050a0a7-1d6c-59df-9dd9-081a9dbf747e | checkpoint | Check that all final device locations are correct and match up with the “For Construction Drawings” and “Reflected Ceiling Plans”
719283c7-1c69-556c-a110-0b13c0c30c98 | checkpoint | Have devices and readings been noted on “As Constructed Drawings” for handover
43a7ec54-bb62-5908-be77-3bc83a24d443 | checkpoint | Have all stickers been installed to fire rated walls and smoke walls for penetrations
b41d9cc1-5fe2-5955-9af8-f7b4eeb59fe6 | checkpoint | Has photographic evidence been taken and recorded for all penetrations
d80d130d-72f8-5fc9-872b-1fc379f43b15 | section | Completion
b894fd15-4591-5de3-8256-45a1e534edc3 | checkpoint | Works completed to specification/drawings - Attach photos of work below
1a9359da-4a24-52a6-9118-f7b27ba0df20 | note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
62a3d1f8-1ae3-556a-8728-a010318e4f2f | button | Area left clean & tidy | Yes, No
e1eedff4-ea64-509b-861c-5e6665d5b6cc | tickbox | Leemark Sign-Off
6e85ff60-b7fe-5cb0-8952-325112afe672 | tickbox | Builder Sign-Off
dd71b766-5bfd-5126-8e81-631da7396226 | signoff | Sign-Off - click to Add signature(s)
a78f5419-1472-5e3e-9c7f-fab726f8991d | checklist | LM-FOR-50-ITR-303.4 Fire Detection Installation (V.171121) |  | LM-FOR-50-ITR-303.4 Fire Detection Installation (V.171121)
a1596c2a-5d45-5fea-8352-c94c52f08b6b | section | Cabling
d43163db-8f22-5249-9081-91480c3ed8d4 | checkpoint | Latest consented drawings checked & referenced
2454c99f-a05e-55f2-8932-8b30caa6e6cf | textbox | Drawing & Revision #
81480ff7-5a43-5c1e-a1c6-610f3bcb08d9 | tickbox | Area clear, tidy and accessible
ee9dad85-64f7-5435-bdf1-f9ee71f21cea | note | Attach Photos/Comments below if any issues & send report to Builder
9ae80a36-2d4e-54c1-a46a-2270b153ec8e | checkpoint | Have all cable supports been installed in the correct position with no obstructions
dd05b8ac-5e35-591c-ba53-1546ab3c9f01 | checkpoint | Have all cables been cable tied to soffit / catenary wire with no sagging or obstructions
f1cc51c1-5ace-589a-b9cd-e2a7d32e0bad | checkpoint | Have all cables been installed for detectors
e498690d-2701-5875-afba-45c850fd5e47 | checkpoint | Have all cables been installed for sprinkler valve sets
182aa0f2-1865-5629-810f-7389c5423658 | checkpoint | Have all cables been installed for magnetic door holders
d82d35a9-5e19-505b-96ba-06c2e146d102 | checkpoint | Have all cables been installed for security fire trips
2a24e8bb-29e0-5023-9a8f-ce2b1078570d | checkpoint | Have all cables been installed for mechanical fire trips
a7b9db13-b98b-5ef5-9f16-37a897216052 | checkpoint | Have all cables been installed for AS 1668 Fan Controls
7785cce1-a604-5189-8a9d-226566584938 | checkpoint | Have the ELV and LV segregation rules been applied as per AS/CAS 009 (including 90 degrees crossovers)
48a40f21-0cd7-58de-9e97-f9fe7aa07773 | checkpoint | Have all cables been installed in the correct position for devices
ef96019f-6f43-5802-b017-28ac674d2115 | checkpoint | Have all cables been joined through for testing purposes
ec30b90e-7ee3-512c-b0ee-d309d137d2bf | section | Cable Feeds
e6b9dcea-049f-4ab2-b9ba-f8562dd52e47 | checkpoint | Have all cable supports been installed in the correct position with no obstructions
50fb123c-916f-546a-9f79-05b976d719eb | checkpoint | Have all cable feeds been installed in the correct position
a9146f1f-94df-594d-89fa-8117510750cb | checkpoint | Have all cables been tied to cable tray with steel ties with no sagging or obstructions
de05cfd0-93f4-5afe-9e3a-2d6ed7a50015 | checkpoint | Have all cable trays been installed correctly and secured including joiners and bends
37bd51dd-4cd7-5fc5-bff3-96fa0d81631b | checkpoint | Have the modified cable trays been re-galvanized
11b3a826-b908-5473-b2f4-a4da7f1b23f4 | section | Visual Check
3d92684e-b9fd-540d-91ca-14d8649f0c47 | checkpoint | Check that no other services are run with or attached to fire detection cables
849a0bf2-9aee-5c6e-b51d-d949c1684357 | checkpoint | Check that no cables have been damaged
c7074107-d9be-5908-bfe2-d39aa6f19ad7 | checkpoint | Check that all final cable locations are correct and match up with the “For Construction Drawings” and “Reflected Ceiling Plans”
8d76a686-6c75-530c-844e-0daf6b45458b | checkpoint | Have all cable runs, cable trays and penetrations been mark on “As Constructed Drawings” for handover
43a7ec54-bb62-5908-be77-3bc83a24d443 | checkpoint | Have all stickers been installed to fire rated walls and smoke walls for penetrations
144fcaec-399f-590d-bb2b-670302d87a4e | checkpoint | Has photographic evidence been taken and recorded for all penetrations?
d80d130d-72f8-5fc9-872b-1fc379f43b15 | section | Completion
b894fd15-4591-5de3-8256-45a1e534edc3 | checkpoint | Works completed to specification/drawings - Attach photos of work below
97ab2ab4-b75a-5a37-8f4a-372407891f76 | note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
1c0b7aa3-57c3-50c4-9e41-cb4e26907d28 | button | Area left clean & tidy | Yes, No
f4075a03-647a-50c8-b9a3-09b1be46627f | tickbox | Leemark Sign-Off
4ac5444e-733e-549d-ba67-ce6e190dde39 | tickbox | Builder Sign-Off
dd71b766-5bfd-5126-8e81-631da7396226 | signoff | Sign-Off - click to Add signature(s)
86fd7cdf-eb03-59ff-a8fb-9cbb6063cc31 | checklist | LM-FOR-50-ITR-303.6 F.E Installation |  | LM-FOR-50-ITR-303.6 F.E Installation
e7581576-5a10-5963-90b0-44587360e1f6 | section | Inspection
af574a82-b1c1-544f-8842-f6b972f7214f | checkpoint | Check that the extinguisher is conspicuous, readily accessible and in its assigned location in accordance with the approved plan.
b8e2834e-1fbf-5da6-85fa-65a1b72c2c5a | checkpoint | Check that the extinguisher is mounted at the appropriate height in accordance with Figure 3.2.
3ecbf633-88fb-5c61-b47c-f767055bca36 | checkpoint | Check that the anti-tamper device is intact. And that the service tag or label is firmly attached.
ee359504-7b77-53f5-b334-359db05bbab6 | checkpoint | Check that the extinguisher is clean and the operating instructions are legible.
94509bba-18e5-5a1c-8916-351d6871723f | checkpoint | Check that the extinguisher, including any attachments, is not damaged.
5fe8d71c-7a6f-57af-8a1f-66928e1c4f7c | checkpoint | Check that the hose is securely fitted, the nozzle is securely attached, the assembly is free from obstruction, and the hose shows no cracking or other signs of damage or deterioration.
7f17a98a-03e9-5ad1-9a19-55a95b9affdd | checkpoint | Check that the appropriate discharge nozzle is fitted and is not blocked or damaged.
4a98c80d-17f6-5cf1-860c-d4106d1ca02a | checkpoint | Where fitted, check that the pressure indicator is legible, and registering within the operable range.
302afa07-b49d-5426-a8d7-701dfa657548 | checkpoint | Check that the appropriate support bracket is securely attached to wall or other suitable feature.
d80d130d-72f8-5fc9-872b-1fc379f43b15 | section | Completion
b894fd15-4591-5de3-8256-45a1e534edc3 | checkpoint | Works completed to specification/drawings - Attach photos of work below
e9293cc4-ea92-5d10-894f-769075d2bba2 | note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
de0c0b7c-9580-5deb-a42c-8186d99d18b4 | button | Area left clean & tidy | Yes, No
6206a3ec-e6ed-551a-b606-384aa14e7e2f | tickbox | Leemark Sign-Off
54c752ce-77c9-5870-98c8-90c35ee82def | tickbox | Builder Sign-Off
dd71b766-5bfd-5126-8e81-631da7396226 | signoff | Sign-Off - click to Add signature(s)
82f0de4b-33d6-50f5-a02f-a39f0f2afb9a | checklist | LM-FOR-50-ITR-304.1 Pre Action Systems |  | LM-FOR-50-ITR-304.1 Pre Action Systems
ee31263b-c940-56f7-b47d-1229cee49670 | section | 1. ITR Pre-commissioning Procedures
01ce076d-be9e-50ef-ba51-b81185d7790e | checkpoint | 1.1 Verify correct type, spacing and elevation of installed pipe supports and hangers.
c972b997-d6ea-5eab-9d4b-26e56a0de382 | checkpoint | 1.2 Installation inspection of trunk mains and range pipes
636529c9-2385-5760-9c05-b95e8b13763a | checkpoint | 1.3 All dirt traps must be capped, and all pops temporarily plugged
bc80cbcd-d86a-5323-8c4d-3b101db567b1 | checkpoint | 1.4 Inspection of installed sprinkler heads & baffle plates and flexible droppers
d47d3622-2ce3-5929-8fd4-8171d3a4dbcd | checkpoint | 1.5 Installation inspection of pre-action valve sets and ancillary equipment to ensure completeness, correct location, mounting
d4be5e2a-36b6-5b46-b39e-f31dc90cf6b9 | checkpoint | 1.6 Verify installation of alarm devices (e.g., DBA pressure/flow switch, low pressure switch) and solenoid valve for correct type and rating and proper interface connections to Fire Indicator Panel (FIP).
1c0d3a02-c6d3-555d-856b-b061ea0ce8a0 | section | 2. ITR Commissioning
6b988e29-b396-55cd-9df6-4a0870644f39 | checkpoint | 2.1 Perform Pneumatic leak test of pipework to ensure no loose joints or open pipe ends
87a646b2-02de-5d85-b6f2-319640733007 | checkpoint | 2.3 Perform Hydrostatic Testing of pipework. Gradually apply pressure increments of 500 kPa for 15-minute holds until test pressure of 1600 kPa or 400 kPa above maximum static working pressure of the system is achieved and hold for 2-hours.
a7f7dddc-fba8-5e27-bc5e-6177b49ae392 | checkpoint | 2.4 Perform a trip test on each pre-action valve by opening the alarm test ball valve and check operation of water motor alarm. Confirm operation of DBA pressure switch with correct indication at fire indicator panel.
be736b31-9738-552c-9d18-b95933f8b743 | checkpoint | 2.5 Initiate single or double interlock release activation and check operation of water motor alarm, DBA pressure switch and correct indication at fire indicator panel.
9083cd38-6e4f-5a9b-86ba-7c0e7e0515f0 | checkpoint | 2.6 Record cut-in / cut-out pressure of air supply compressor and time to recharge the system pressure
73d27ea2-422f-5264-88a1-6ec7a9263302 | checkpoint | 2.7 Reinstate system and ensure valves are secured in its intended position, alarm and monitoring devices are in operational mode and system in ready to operate condition
6f36c1e5-335f-583c-b903-f8449d527bbd | checkpoint | Final Inspection Builder
5266e169-163a-5d87-8ed0-ace697240f42 | textbox | Checked By:
666b44aa-93e7-5542-af33-5d6f7646c2a2 | textbox | Signature:
f27ce135-4a6d-5dcb-aa93-e6fd21a0e303 | textbox | Date:
0529b5d1-c9af-520a-9376-5244d2663164 | checkpoint | Final Inspection (Leemark)
7c5179d5-5ce4-5359-b236-08833430dd68 | textbox | Checked By:
e33feda4-cfa6-5043-92f7-fd182bc90e4f | textbox | Signature:
9e80f159-47f9-50e6-9689-f1dc5e9bf88f | textbox | Date:
4e9cac88-8c7f-5591-8b16-d57ff5a1ab7b | checklist | LM-FOR-50-ITR-304.2 N2 Blast System |  | LM-FOR-50-ITR-304.2 N2 Blast System
ee31263b-c940-56f7-b47d-1229cee49670 | section | 1. ITR Pre-commissioning Procedures
dbbaac5b-7f4c-54a2-8eb3-b681cc4deff3 | checkpoint | 1.1 Verify unit is fixed into position using the anchor points
9005f2ff-7779-5704-9ecb-c5a8324a65f0 | checkpoint | 1.2 Verify all connections are complete to unit and compressor/s
f9940ce4-63b5-5e97-8a6e-9c66f127460c | checkpoint | 1.3 Check for leaks – Listen for leaks and spray with soapy water around connections.
4c942258-d0ee-5d8d-84f9-60aedfcf57b9 | checkpoint | 1.4 All power is connected and energised
49aea0b3-b7cb-513a-9f7c-de5d60e00a25 | checkpoint | 1.5 Set Air maintenance devices on Pre Action Valves to 18psi
1c0d3a02-c6d3-555d-856b-b061ea0ce8a0 | section | 2. ITR Commissioning
bac2540a-b5ab-53cd-a064-33908ba106a8 | checkpoint | 2.1 Power is on the unit by making sure the touchscreen has turned on and the start and stop button is “Red” and the icon reads “Status: Off”
71b505ab-e913-5b7e-89ac-dd02538d013c | checkpoint | 2.3 Make sure the outlet ball valve is valve off.
31ed6023-0cb6-5cf9-8054-f2675e68f54f | checkpoint | 2.4 Skip this step if this is a FPS-1650, otherwise, slowly open the Air Inlet valve and allow pressure to build up to the internal regulator after the filters. Make sure pressure reaches 120 PSIG. Listen and feel for any major leaks.
9bb3d5b4-9e96-5405-8acb-da6069681635 | checkpoint | 2.5 "On the home screen of the touchscreen, press and hold the power button for 2 seconds until it turns “Green” and the icon reads “Status: Running”. Air will rushing through the system and N2 will start filling the tank"
b0a45251-c2fc-52e5-94b1-d8889a85197f | checkpoint | 2.6 Once the internal tank pressure reaches 70 PSIG, the system will go into standby mode at the end of the cycle.
b7e83c0c-9b77-5d47-ab74-91c9b609be01 | checkpoint | 2.7 "After the 5 minutes with the pressure maintained, slowly open the nitrogen outlet valve to the “Air Maintenance Device” and monitor for any leaks. The nitrogen generator will automatically run, and shutoff as needed based on the internal storage tank pressure."
6f36c1e5-335f-583c-b903-f8449d527bbd | checkpoint | Final Inspection Builder
7953e6bf-13bb-5fba-abbe-b401865220c1 | textbox | Checked By:
5b0e242e-dcc3-5bc6-9798-6f1b0dcccfd3 | textbox | Signature:
ebf75578-39ce-52dd-821f-49bf149ced97 | textbox | Date:
0529b5d1-c9af-520a-9376-5244d2663164 | checkpoint | Final Inspection (Leemark)
beee132c-cec7-59ca-a525-72a6762a5206 | textbox | Checked By:
3f3a0a1b-9ba1-5cdf-b9b1-7fb83d4e8255 | textbox | Signature:
9ca9fe95-6b2d-57a1-8ead-2431e291ab2c | textbox | Date:
b834ad48-9d73-5c19-81c5-6d8df0f2892e | checklist | wet fire ITP |  | wet fire ITP
3b7d5130-bcd6-51a0-a616-f5d19b0eab02 | checkpoint | Are all sprinklers installed clear of obstructions as per AS2118.4(2012) Clause 4.4.3.2?
0dc94443-7037-5042-8aac-b1fbfd82b839 | checkpoint | Have sprinkler spares been left in cabinet including a sprinkler key, if new install? INSERT PHOTO
ef8dad67-8cfc-538a-b262-3120e94e35b2 | checkpoint | Have the valves been labelled inside the SCV? INSERT PHOTO
a1ff9dd4-8b0f-5e0a-9623-712a96aec59e | checkpoint | Has the Sprinkler Block Plan been laminated and stuck on to the inside of the SCV cabinet? INSERT PHOTO
984ac465-68a9-549f-be72-38a5ced08692 | checkpoint | Has the Water Tapping been connected to the SCV? INSERT PHOTO OF PRESSURE GAUGE
b387c8ad-939f-5bed-a4af-191af9a9ecc3 | checkpoint | Has the Water Tapping Cage been installed? INSERT PHOTO
ab925ca3-1b47-5d66-bf18-9ed3669dfaa7 | checkpoint | Has a Flow Test been conducted and recorded?
33c7775f-1d61-5bef-a1f4-b00d0da3fa70 | checkpoint | Has the remote test valve been installed as per our shop drawing and labelled? INSERT PHOTO
c239e722-5c13-554d-8c2d-550d9d88d270 | checkpoint | Have sprinklers been installed with guards if exposed? INSERT PHOTO
68158a71-cea7-5af3-87f2-484fd6034d3d | checkpoint | Has a Hydrostatic test record been completed and recorded? 1200kPA min 2 Hours INSERT PHOTO OF PRESSURE GAUGE
521f7f96-7450-532c-bba8-73c8e80f091e | checkpoint | Do the As-Installed conditions on site reflect the Shop Drawings