## Table 1
Inspection and Test Plan - VSD 2 Delivery and Installation ITP Reference Number 561482-ITP-002.2
SECTION 1 – GENERAL DETAILS
Project Name: | DCC11014 Water Pump Station Renewals - SILVERSTREAM | [14 empty] | Inspection Key Use in sections 3, 4 and |  |  | Responsibilities Use in sections 3, 4 and 5.
Project Number: | 561482 | [14 empty] | A Action |  |  | Role Key |  |  | Name |  |  |  |  | Signature/ Initial
Customer: | Dunedin City Council | [14 empty] | B Report by Breach |  |  | CM Construction Manager |  |  | Stephen Vorgers
Contract Number: | DCC11014-WPS002 | [14 empty] | C Check |  |  | CR Cust. Representative |  |  | Joff Riley / Mark Todd
Area/ Sub-System: | VSD Delivery and Installation - SILVERSTREAM | [8 empty] | Lot ID Number: | N/A |  |  |  |  | D Dimension Inspection |  |  | IP Inspection Personnel |  |  | Hamish Watson
[16 empty] | E Examine |  |  | MC Material Controller
ITP Number: | 561482-ITP-002.2 | [8 empty] | Version: | DRAFT |  |  |  |  | H Hold Point |  |  | OP Operations Manager
ITP Description: | VSD2 Delivery and Installation | [14 empty] | I Inspection |  |  | PM Project Manager |  |  | Matt Paterson
Discipline: | VSD's | [14 empty] | M Monitor on Random Basis |  |  | PS Project Supervisor
Specification: | C11014 Water Pump Station Renewals Specification 12581908 | [14 empty] | O Operation |  |  | QE Quality Engineer
[16 empty] | R Review |  |  | QM QA Manager
Drawings: | Construction Issue Drawings as issued by GHD - Silverstream Pump Station Project Ref: 12581908-GHD-PS-SS-DRG-GN Drawings: G0001, M0001 through M0004 & P0001 | [14 empty] | S Subcontractor |  |  | SP Supervisor |  |  | Hamish Watson
[16 empty] | V Visual Verification |  |  | ST Superintendent
Prepared By: (Name) | Hamish Watson / Matt Paterson | [8 empty] | Date: | 2024-10-12 |  |  |  |  | W Witness Point |  |  | SV Surveyor
Quality Specified: | None - As per Specification requirements | [17 empty] | WS Welding Supervisor
SECTION 2 – SIGNATURES – CLOSE-OUT & APPROVAL
ITP Close-Out by Downer |  |  | Name: |  |  |  | Hamish Watson | [7 empty] | Signature: | [6 empty] | Date:
Downer Approval |  |  | Name: |  |  |  | Matt Paterson/Stephen Vorgers | [7 empty] | Signature: | [6 empty] | Date:
Customer Approval |  |  | Name: |  |  |  | Joff Riley / Bruce Buxton | [7 empty] | Signature: | [6 empty] | Date:
DG-QA-TP018 Internal Use Only © Downer. All Rights Reserved | [22 empty] | Page 1 of 5 Version: 1.2 Warning: Printed documents are UNCONTROLLED
SECTION 3 – RECEIVING INSPECTIONS Insert additional or delete unused rows as required. Include reference to specification.
Item No. |  | Activity/ Task Description |  | Inspection Point: Quality Control Activity |  |  |  |  | Acceptance Criteria |  |  |  | Verifying Document |  |  |  | Frequency |  |  | Inspection Type (Visual, other) |  |  |  |  | Inspection
[25 empty] | Key |  |  |  | By (Role Key)
3.1 |  | Inspection of VSD prior to delivery to site |  | Check overall condition of packaging, noting any obvious signs of damage, Check rating of drives is correct. |  |  |  |  | Visual check and report any defects or areas of concern | [7 empty] | Once |  |  | Visual + Photograph |  |  |  |  | C |  |  |  | IP/B
3.2 |  | Delivery of VSD to Site |  | Check and verify that correct VSD are delivered and that drives are undamaged |  |  |  |  | VSD are damage free |  |  |  | VSD Delivery documents |  |  |  | Once |  |  | Visual |  |  |  |  | C |  |  |  | IP
SECTION 4 – IN-PROCESS INSPECTIONS Insert additional or delete unused rows as required. Include reference to specification.
4.1 |  | On-site assembly of mounting Frame |  |  | materials for frame delivered to site |  |  | Correct materials on site, protective coatings correct. |  |  |  | Delivery Docket for Materials |  |  |  |  | Once |  |  | Visual |  |  |  | I |  |  |  | IP
4.2 |  | Assembly and mounting of Frame |  |  | Frame Built and bolted to Ground. |  |  | Frame built and Securely attached to ground, minimal flex/ movement when force applied. |  |  |  | N/a |  |  |  |  | Once |  |  | Visual + Photograph |  |  |  | I |  |  |  | IP
4.3 |  | Mounting of VSD to Frame |  |  | VSD Mounted to frame |  |  | VSD Mounted satisfactorily, bolts tight, washers and spring washers present, S/S bolts and fixings used. |  |  |  | VSD Inspection Sheets. |  |  |  |  | Once |  |  | Visual + Photograph |  |  |  | I |  |  |  | IP
4.4 |  | Installation of supply cables to VSD |  |  | Cables installed, not terminated into VSDs or switchboard |  |  | Correct Cables installed, suitable for full load plus 20 percent of VSD, insulation resistance acceptable |  |  |  | VSD Cable Test Sheets. |  |  |  |  | Once |  |  | Visual + Inspection |  |  |  | I |  |  |  | IP
4.5 |  | Installation of Output Cables From VSD to Motors |  |  | Cables installed, not terminated at motors or VSD |  |  | Correct Cables installed, suitable for full load of motor plus 20 percent, insulation resistance acceptable |  |  |  | VSD Cable Test Sheets. |  |  |  |  | Once |  |  | Visual + Inspection |  |  |  | I |  |  |  | IP
4.6 |  | Termination of cabling to VSD |  |  | Cables terminated into VSD |  |  | Correct Cables installed, terminals tightened to correct torque, cables prepared correctly. cable earths and screens fit off correctly. |  |  |  | VSD Cable Test Sheets. |  |  |  |  | Once |  |  | Visual + Inspection |  |  |  | I |  |  |  | IP
4.7 |  | Termination of cabling to Switchboard |  |  | Cables fit off at Switchboard. |  |  | Correct Cables installed, terminals tightened to correct torque, cables prepared correctly. cable earths and screens fit off correctly. |  |  |  | VSD Cable Test Sheets. |  |  |  |  | Once |  |  | Visual + Inspection |  |  |  | I |  |  |  | IP
4.8 |  | Verification of motors electrically |  |  | Cables installed, not terminated into motor |  |  | Correct motors installed. insulation resistance verified, winding configuration confirmed against nameplate. |  |  |  | VSD Cable Test Sheets. |  |  |  |  | Once |  |  | Visual + Inspection |  |  |  | I |  |  |  | IP
4.9 |  | Termination of cabling to Motor |  |  | Cables fit off at Motor |  |  | Cables Lugged off correctly, terminals tightened to correct torque |  |  |  | Motor Inspection Sheets |  |  |  |  | Once |  |  | Visual + Photograph |  |  |  | I |  |  |  | IP
SECTION 5 – FINAL INSPECTION AND HANDOVER Insert additional or delete unused rows as required. Include reference to specification.
5.1 | VSD |  |  |  |  | VSD Energised and set up, motor nameplate data entered, protections set, Labels attached |  |  | VSD parameters set correctly, inputs set up as per drawings. analog i/o set correctly and verified to plc |  |  |  |  | VSD ITR Document |  |  |  | Once |  |  | Visual + Document |  |  |  |  | I |  |  | IP
5.2 | Motors |  |  |  |  | Assembled and in position, inspection carried out and approved |  |  | Motors Tested, rotation direction confirmed, pumps operating as intended. |  |  |  |  | Motor inspection Sheet |  |  |  | Once |  |  | Visual + Document |  |  |  |  | I |  |  | IP
SECTION 6 – COMMENTS
[9 empty] | Customer Release Granted: |  |  |  |  | ☐ Yes |  |  |  | ☐ No |  |  | Date:
Certificate Number: