## Table 1
Inspection and Test Plan - Wet Well Wall Penetration 2 ITP Reference Number 561482-ITP-003.2
SECTION 1 – GENERAL DETAILS
Project Name: | DCC11014 Water Pump Station Renewals - SILVERSTREAM | [14 empty] | Inspection Key Use in sections 3, 4 and |  |  | Responsibilities Use in sections 3, 4 and 5.
Project Number: | 561482 | [14 empty] | A Action |  |  | Role Key |  |  | Name |  |  |  |  | Signature/ Initial
Customer: | Dunedin City Council | [14 empty] | B Report by Breach |  |  | CM Construction Manager |  |  | Stephen Vorgers
Contract Number: | DCC11014-WPS002 | [14 empty] | C Check |  |  | CR Cust. Representative |  |  | Joff Riley / Mark Todd
Area/ Sub-System: | Wet Wall Penetration Preparation - SILVERSTREAM | [8 empty] | Lot ID Number: | N/A |  |  |  |  | D Dimension Inspection |  |  | IP Inspection Personnel |  |  | Jason Bell
[16 empty] | E Examine |  |  | MC Material Controller
ITP Number: | 561482-ITP-003.2 | [8 empty] | Version: | DRAFT |  |  |  |  | H Hold Point |  |  | OP Operations Manager
ITP Description: | Wet Well Wall breakout and preparation - Inspection Test Plan | [14 empty] | I Inspection |  |  | PM Project Manager |  |  | Matt Paterson
Discipline: | Wet Well Wall breakout & preparation Pump 2 Penetration | [14 empty] | M Monitor on Random Basis |  |  | PS Project Supervisor
Specification: | C11014 Water Pump Station Renewals Specification 12581908 | [14 empty] | O Operation |  |  | QE Quality Engineer
[16 empty] | R Review |  |  | QM QA Manager
Drawings: | Construction Issue Drawings as issued by GHD - Silverstream Pump Station Project Ref: 12581908-GHD-PS-SS-DRG-GN Drawings: G0001, M0001 through M0004 & P0001 | [14 empty] | S Subcontractor |  |  | SP Supervisor |  |  | Bruce Allan
[16 empty] | V Visual Verification |  |  | ST Superintendent
Prepared By: (Name) | Matt Paterson | [8 empty] | Date: | 2024-10-12 |  |  |  |  | W Witness Point |  |  | SV Surveyor
Quality Specified: | None - As per Specification | [17 empty] | WS Welding Supervisor
SECTION 2 – SIGNATURES – CLOSE-OUT & APPROVAL
ITP Close-Out by Downer |  |  | Name: |  |  |  | Matt Paterson/Jason Bell | [7 empty] | Signature: | [6 empty] | Date:
Downer Approval |  |  | Name: |  |  |  | Matt Paterson/Stephen Vorgers | [7 empty] | Signature: | [6 empty] | Date:
Customer Approval |  |  | Name: |  |  |  | Joff Riley / Mark Todd | [7 empty] | Signature: | [6 empty] | Date:
DG-QA-TP018 Internal Use Only © Downer. All Rights Reserved | [22 empty] | Page 1 of 5 Version: 1.2 Warning: Printed documents are UNCONTROLLED
SECTION 3 – RECEIVING INSPECTIONS Insert additional or delete unused rows as required. Include reference to specification.
Item No. |  | Activity/ Task Description |  | Inspection Point: Quality Control Activity |  |  |  |  | Acceptance Criteria |  |  |  | Verifying Document |  |  |  | Frequency |  |  | Inspection Type (Visual, other) |  |  |  |  | Inspection
[25 empty] | Key |  |  |  | By (Role Key)
3.1 |  | Masonry drill bits 18mm |  | Verify correct quantity & type |  |  |  |  | Compatable with the drill unit |  |  |  | Manufacturers Technical data & Physical fitment |  |  |  | Once |  |  | Visual + Photographs |  |  |  |  | Inspection |  |  |  | IP
3.2 |  | Reinforcing Bar |  | Verify correct quantity & size/diameter has been delivered to site |  |  |  |  | Quantities correct. Dimensions correct. |  |  |  | Drawing M0003 |  |  |  | Once |  |  | Visual + Photographs |  |  |  |  | Inspection |  |  |  | IP
3.3 |  | Hilti RE-500 Chemical Anchor |  | Verify correct product is deivered. Check expiratrion date. |  |  |  |  | Quantities correct. Within expiration date |  |  |  | HILTI Product Calculator APP. Delivery Docket |  |  |  | Once |  |  | Visual + Photographs |  |  |  |  | Inspection |  |  |  | IP
3.4 |  | Grout (Sika MonoTop 438R) |  | Verify correct product is deivered. Check expiratrion date. |  |  |  |  | Quantities correct. Within expiration date |  |  |  | Delivery Docket |  |  |  | Once |  |  | Written/Submission |  |  |  |  | Inspection |  |  |  | IP
SECTION 4 – IN-PROCESS INSPECTIONS Insert additional or delete unused rows as required. Include reference to specification.
4.1 |  | Mark out penetration on both sides (wet & dry sides) using existing pipe as reference |  |  | Check and verify dimensains against drawings |  |  | Approval from Engineer |  |  |  | Drawing M0003 |  |  |  |  | once |  |  | Document + Visual + Photograph + Engineer site Inspection |  |  |  | V |  |  |  | CR
4.2 |  | Proceed with breakout. Hammer drill |  |  | Monitor work and progress report any issues |  |  | Approval to proceed from item 4.1 |  |  |  | As per drawings listed dimensions & measurements |  |  |  |  | once |  |  | Visual & Document |  |  |  | I |  |  |  | IP
4.3 |  | Pre pour inspection |  |  | Engineer Inspection |  |  | Dimensioin & Surface sheck. As per Drawing M0003 and notes. Approval to proceed via NTC. Correct profile achieved with 5mm roughness and any loose material removed |  |  |  | NTC or other written confirmation |  |  |  |  | once |  |  | Document |  |  |  | H |  |  |  | CR
4.4 |  | Procurement of Reinforcing bar, starters & trimmers |  |  | Check measurents and vereify correct fitment |  |  | As detailed on Drawings & specifications |  |  |  | Drawing M0003 |  |  |  |  | once |  |  | Document + Visual |  |  |  | I |  |  |  | IP
4.5 |  | Installation of Reinforcing bar, starters & trimmers |  |  | Drill holes around perimeter to receive reinforcing bar. Check for correct diameter & corret embedment |  |  | As detailed on Drawings |  |  |  | Drawing M0003 |  |  |  |  | once |  |  | Visual + Photographs |  |  |  | I |  |  |  | IP
4.6 |  | Install pipe spool with puddle flange to be cast within wall |  |  | Check that orientation is correct and is in alignment with pump assembly |  |  | As detailed on Drawings M0003 and drawing notes |  |  |  | Drawing M0001 Drawing M0002 Drawing M0003 Drawing M0004 |  |  |  |  | once |  |  | Visual + Photographs |  |  |  | I |  |  |  | IP
4.7 |  | Hilti RE500. Chemical Anchor reinforcing bar, starters & trimmers into position |  |  | Observe Manufacturers instructions. Monitor curing times and temparatures. Use manufacturers calculator to determine product volumes. Sequence the installion to avoid obstruction |  |  | As detailed on Drawings and completion of item 4.6 |  |  |  | Drawing M0003 |  |  |  |  | once |  |  | Visual + Photographs |  |  |  | I |  |  |  | IP
4.8 |  | Chemically treat perimeter using product HYDROTITE CJ1020 |  |  | Observe Manufacturers instructiuons & Health and safety requirements |  |  | As detailed on Drawings and completion of item 4.7 |  |  |  | Drawing M0003 |  |  |  |  | once |  |  | Visual + Photographs |  |  |  | H |  |  |  | IP
SECTION 5 – FINAL INSPECTION AND HANDOVER Insert additional or delete unused rows as required. Include reference to specification.
5.1 | Final dimensional check |  |  |  |  | At completion of all items on this ITP |  |  | Dimensions match the measurements shown on drawings |  |  |  |  | Drawing M0003 |  |  |  | once |  |  | Visual + Photograph + Mark-up drawing |  |  |  |  | H |  |  | CR
SECTION 6 – COMMENTS
[9 empty] | Customer Release Granted: |  |  |  |  | ☐ Yes |  |  |  | ☐ No |  |  | Date:
Certificate Number: