## Table 1
Inspection and Test Plan - Grout Pour - Penetration 2 ITP Reference Number 561482-ITP007.2
SECTION 1 – GENERAL DETAILS
Project Name: | DCC11014 Water Pump Station Renewals - SILVERSTREAM | [15 empty] | Inspection Key Use in sections 3, 4 and |  |  | Responsibilities Use in sections 3, 4 and 5.
Project Number: | 561482 | [15 empty] | A Action |  |  | Role Key |  |  | Name |  |  |  |  | Signature/ Initial
Customer: | Dunedin City Council | [15 empty] | B Report by Breach |  |  | CM Construction Manager |  |  | Stephen Vorgers
Contract Number: | DCC11014-WPS002 | [15 empty] | C Check |  |  | CR Cust. Representative |  |  | Joff Riley / Mark Todd
Area/ Sub-System: | Grout Pour - SILVERSTREAM | [10 empty] | Lot ID Number: | N/A |  |  |  | D Dimension Inspection |  |  | IP Inspection Personnel |  |  | Jason Bell
[17 empty] | E Examine |  |  | MC Material Controller
ITP Number: | 561482-ITP007.2 | [10 empty] | Version: | V1 |  |  |  | H Hold Point |  |  | OP Operations Manager
ITP Description: | Wet Well Wall grout pour Penetration 2 - Inspection Test Plan | [15 empty] | I Inspection |  |  | PM Project Manager |  |  | Matt Paterson
Discipline: | Wet Well Wall grout pour | [15 empty] | M Monitor on Random Basis |  |  | PS Project Supervisor
Specification: | C11014 Water Pump Station Renewals Specification 12581908 | [15 empty] | O Operation |  |  | QE Quality Engineer
[17 empty] | R Review |  |  | QM QA Manager
Drawings: | Construction Issue Drawings as issued by GHD - Silverstream Pump Station Project Ref: 12581908-GHD-PS-SS-DRG-GN Drawings: G0001, M0001 through M0004 & P0001 | [15 empty] | S Subcontractor |  |  | SP Supervisor |  |  | Bruce Allan
[17 empty] | V Visual Verification |  |  | ST Superintendent
Prepared By: (Name) | Matt Paterson | [10 empty] | Date: | 2024-12-16 |  |  |  | W Witness Point |  |  | SV Surveyor
Quality Specified: | None - As per Specification | [18 empty] | WS Welding Supervisor
SECTION 2 – SIGNATURES – CLOSE-OUT & APPROVAL
ITP Close-Out by Downer |  |  |  | Name: |  |  |  | Matt Paterson/Jason Bell | [7 empty] | Signature: | [6 empty] | Date:
Downer Approval |  |  |  | Name: |  |  |  | Matt Paterson/Stephen Vorgers | [7 empty] | Signature: | [6 empty] | Date:
Customer Approval |  |  |  | Name: |  |  |  | Joff Riley / Mark Todd | [7 empty] | Signature: | [6 empty] | Date:
DG-QA-TP018 Internal Use Only © Downer. All Rights Reserved | [23 empty] | Page 1 of 4 Version: 1.2 Warning: Printed documents are UNCONTROLLED
SECTION 3 – RECEIVING INSPECTIONS Insert additional or delete unused rows as required. Include reference to specification.
Item No. |  |  | Activity/ Task Description |  | Inspection Point: Quality Control Activity |  |  |  |  | Acceptance Criteria |  |  |  |  | Verifying Document |  |  | Frequency |  |  | Inspection Type (Visual, other) |  |  |  |  | Inspection
[26 empty] | Key |  |  |  | By (Role Key)
3.1 |  |  | Grout - SIKA MonoTop- 438R |  | Calculate Quantity |  |  |  |  | Correct volume to be calculated |  |  |  |  | Product Datasheet |  |  | Once |  |  | Written |  |  |  |  | R |  |  |  | CR
3.2 |  |  | Installed Reinforcing |  | Measure and check |  |  |  |  | Matches Design Drawings |  |  |  |  | Drawing M0003 |  |  | Once |  |  | Visual + Photographs |  |  |  |  | V |  |  |  | IP
3.3 |  |  | Spool/Puddle Flange |  | Measure and check |  |  |  |  | Pipework is straight and parrallel to structure & pump |  |  |  |  | As per drawing M0001 & M0002 |  |  | Once |  |  | Visual + Photographs |  |  |  |  | V |  |  |  | IP
SECTION 4 – IN-PROCESS INSPECTIONS Insert additional or delete unused rows as required. Include reference to specification.
4.1 |  |  | Boxing of penertation |  |  | Measure & Check. Ensure perimeter of boxing and pipe penetration is sealed to stop grout spill. |  |  | Matches Design Drawings by dinension and configuration |  |  |  |  | Drawing M0003 |  |  |  | Once |  |  | Visual + Inspection HOLD POINT |  |  |  | H |  |  |  | CR
4.2 |  |  | Mixing of Grout |  |  | Ensure product is on hand & plenty of clean fresh water is readily available |  |  | As per manufacturers instructions/guidelines |  |  |  |  | Product technical instruction sheets or certificate (if delivered) |  |  |  | once |  |  | Document |  |  |  | I |  |  |  | IP
4.3 |  |  | Casting of wall penetration |  |  | Monitor the consistency and quality of the grout fill |  |  | As per manufacturers instructions/guidelines |  |  |  |  | Product technical instructions |  |  |  | once |  |  | Dodument + Visual |  |  |  | I |  |  |  | IP
4.4 |  |  | Vibrate |  |  | Vibrate to remove entrained air. Ensure all air is removed |  |  | Grout Placer Approval |  |  |  |  | This ITP |  |  |  | once |  |  | Visual + Photographs + Short video |  |  |  | I |  |  |  | IP
4.5 |  |  | Monitor curing process |  |  | Monitor curing inspectiong the boxing and areas of potential grout leakage. |  |  | No evident shrinkage or deformation. Repotr any issues to Engineer |  |  |  |  | As per drawings allowing 7 days curing time. Boxing can be removed after 72 hours |  |  |  | once |  |  | Visual |  |  |  | I |  |  |  | IP
SECTION 5 – FINAL INSPECTION AND HANDOVER Insert additional or delete unused rows as required. Include reference to specification.
5.1 |  | Remove boxing |  |  |  |  | At completion of all items on this ITP |  |  |  | Time period as indicated on programme |  |  |  |  | This ITP |  |  | once |  |  | Visual + Photograph |  |  |  |  | I |  |  | IP
SECTION 6 – COMMENTS
[11 empty] | Customer Release Granted: |  |  |  |  | ☐ Yes |  |  | ☐ No |  |  | Date:
Certificate Number: