## Table 1
Inspection and Test Plan - Pump 2 Operational test/check ITP Reference Number 561482-ITP-009.2
SECTION 1 – GENERAL DETAILS
Project Name: | DCC11014 Water Pump Station Renewals - SILVERSTREAM | [14 empty] | Inspection Key Use in sections 3, 4 and |  |  |  | Responsibilities Use in sections 3, 4 and 5.
Project Number: | 561482 | [14 empty] | A Action |  |  |  | Role Key |  |  | Name |  |  |  |  | Signature/ Initial
Customer: | Dunedin City Council | [14 empty] | B Report by Breach |  |  |  | CM Construction Manager |  |  | Stephen Vorgers
Contract Number: | DCC11014 - WPS002 | [14 empty] | C Check |  |  |  | CR Cust. Representative |  |  | Joff Riley Mark Todd
Area/ Sub-System: | Pump 2 Operational test/check | [8 empty] | Lot ID Number: | N/A |  |  |  |  | D Dimension Inspection |  |  |  | IP Inspection Personnel |  |  | Bruce Allan
[16 empty] | E Examine |  |  |  | MC Material Controller
ITP Number: | 561482-ITP-009.2 | [8 empty] | Version: | DRAFT |  |  |  |  | H Hold Point |  |  |  | OP Operations Manager
ITP Description: | To test and check the operation of Pump 2 and associated valves/pipework | [14 empty] | I Inspection |  |  |  | PM Project Manager |  |  | Matt Paterson
Discipline: | Operational testing | [14 empty] | M Monitor on Random Basis |  |  |  | PS Project Supervisor |  |  | Aaron Sutherland
Specification: | C11014 Water Pump Station Renewals Specification 12581908 | [14 empty] | O Operation |  |  |  | QE Quality Engineer |  |  | Bruce Buxton
[16 empty] | R Review |  |  |  | QM QA Manager
Drawings: | Construction Issue Drawings as issued by GHD - Silverstream Pump Station Project Ref: 12581908-GHD-PS-MG-DRG-GN Drawings: G0001, M0001 through M0004, & P0001 | [14 empty] | S Subcontractor |  |  |  | SP Supervisor |  |  | Bruce Allan
[16 empty] | V Visual Verification |  |  |  | ST Superintendent
Prepared By: (Name) | Matt Paterson | [8 empty] | Date: | 2024-10-12 |  |  |  |  | W Witness Point |  |  |  | SV Surveyor
Quality Specified: | As Per Specification - Section 4.6 Acceptance Testing, Disinfection & Commissioning | [18 empty] | WS Welding Supervisor
SECTION 2 – SIGNATURES – CLOSE-OUT & APPROVAL
ITP Close-Out by Downer |  |  | Name: |  |  |  | Bruce Allan | [7 empty] | Signature: | [7 empty] | Date:
Downer Approval |  |  | Name: |  |  |  | Matt Paterson/Stephen Vorgers | [7 empty] | Signature: |  | Matt Paterson | [5 empty] | Date:
Customer Approval |  |  | Name: |  |  |  | Joff Riley / Bruce Buxton | [7 empty] | Signature: | [7 empty] | Date:
DG-QA-TP018 Internal Use Only © Downer. All Rights Reserved | [23 empty] | Page 1 of 6 Version: 1.2 Warning: Printed documents are UNCONTROLLED
SECTION 3 – RECEIVING INSPECTIONS Insert additional or delete unused rows as required. Include reference to specification.
Item No. |  | Activity/ Task Description |  | Inspection Point: Quality Control Activity |  |  |  |  | Acceptance Criteria |  |  |  | Verifying Document |  |  |  |  | Frequency |  |  | Inspection Type (Visual, other) |  |  |  |  | Inspection
[26 empty] | Key |  |  |  | By (Role Key)
3.1 |  | Fill Wet Well |  | Pressure testing between suction and discharge isolation valves |  |  |  |  | Completion of 561482- ITP-008 |  |  |  | This ITP |  |  |  |  | once |  |  | Visual |  |  |  |  | Inspection |  |  |  | IP
SECTION 4 – IN-PROCESS INSPECTIONS Insert additional or delete unused rows as required. Include reference to specification.
4.1 |  | Filling of pipeline |  |  | Remove Entrained air |  |  | Bleed until water visible |  |  |  | None | [5 empty] | once |  |  | Visual |  |  |  | Inspection |  |  |  | IP
4.2 |  | Visual Check over of Pump 2 and motor |  |  | Look for any visible leaking |  |  | All pipework connections tight All Cable & Terminations secure |  |  |  | This ITP | [5 empty] | once |  |  | Visual |  |  |  | Inspection |  |  |  | IP
4.3 |  | Bump Start Pump 2 |  |  | Check for correct pump rotation direction |  |  | Rotation direction is correct |  |  |  | Pump build sheet literature | [5 empty] | once |  |  | Visual |  |  |  | Inspection |  |  |  | IP
4.4 |  | Pressure testing between suction and diacharge isolation valves - Pump 2 |  |  | VSD Energised, water in pump pipelines |  |  | No visible leaking as per Item 4.2 |  |  |  | To meet Specification requirements and not to exceed pump manufacturers maximum pressure (Pump flanges 16Bar, Seal max pressure 30Bar) | [5 empty] | once |  |  | Visual |  |  |  | Inspection |  |  |  | IP
SECTION 5 – FINAL INSPECTION AND HANDOVER Insert additional or delete unused rows as required. Include reference to specification.
5.1 | Pump 2 rotation direction |  |  |  |  | Pump rotation direction as per manufacturers technical information |  |  | Pump rotation direction is correct and matched the technicxal information |  |  |  |  | This ITP |  |  |  |  | Once |  |  | Record on ITP |  |  |  |  | Inspection |  |  | IP
5.2 | Pump 2 pressure test pass |  |  |  |  | Record Guage pressure |  |  | Pass - no pressure loss or visible weaping |  |  |  |  | This ITP & Specified Pressure testing document |  |  |  |  | Once |  |  | Visual / Photo |  |  |  |  | Inspection |  |  | IP
SECTION 6 – COMMENTS
[9 empty] | Customer Release Granted: |  |  |  |  | ☐ Yes |  |  |  |  | ☐ No |  |  | Date:
Certificate Number: