## Project Checklist Templates
Id | Type | Name | Values | Prompting Name
cf776114-6195-4b72-8b9f-d7eda9ea622b | checklist | 561482-ITP-005.2 - Pump. Motor Shaft Alignment - Pump 2 | itp | 561482-ITP-005.2 - Pump. Motor Shaft Alignment - Pump 2
fcc3f6cd-2b16-4e25-bc3e-893ac9d39f7e | section | SECTION 3 – RECEIVING INSPECTIONS
f61d0b52-8290-45db-b526-aa984c9aac2c | checkpoint | 3.1 - Align pump and motor shafts and install coupling - Pump & Motor Assembly 2
c5a3a016-2274-570a-96a9-ba71a6ae5570 | note | Inspection Point: Quality Control Activity - Downer to engage a specialist to laser align motor and pump shafts to within 0.025mm
59baec02-0980-5010-b49e-605b142d1167 | note | Acceptance Criteria - Completion of the assebmly to pump and motor 2 including mounting to the plinth.
28111e01-4316-54b3-984d-97481b10fdaf | note | Verifying Document - Downer 561482-ITP-004.2
9d92e142-6604-5aa8-a7db-e634ab48a789 | note | Frequency - once
1a5f6b5f-055f-5d6c-a408-1118d8f213ce | note | Inspection Type (Visual, other) - Visual + Photograph + document provided by specialist
871f1cd6-d632-553f-9804-ebd26f922835 | note | Inspection: Key - QE
60f59dae-d7d7-54b2-938c-4d112adfd516 | note | Inspection: By - D / E
3cbb84b7-b719-41fa-b238-d8f1e137fa4f | section | SECTION 4 – IN-PROCESS INSPECTIONS
fdd805d9-ded6-44ad-b93e-9e87fe8fe8bf | checkpoint | 4.1 - Align pump and motor shafts and install coupling - Pump & Motor Assembly 2
ae231f52-a04f-5b7e-9889-29c1a4474882 | note | Inspection Point: Quality Control Activity - Engage Engineering Specialist to adjust and align motor and pump shafts using laser alignment
952d1da7-e92b-5596-a722-ef2e38cddc38 | note | Acceptance Criteria - Pump and motor shafts are aligned to the specified tolerances on X-Y-Z axis to tolerance of 0.025mm
ccc041ca-1276-5cdc-a876-d241ce505348 | note | Verifying Document - Report provided by Engineering Specialist - Wallace Murray Electrical
3429c640-387f-5ee0-ae24-6d0fe9ffc625 | note | Frequency - once
7354e46c-1d82-5a44-93ea-01831f6d6900 | note | Inspection Type (Visual, other) - Visual + Photograph + document provided by specialist
a873ccd8-a74e-57f6-be90-9eda4d6bb923 | note | Inspection: Key - QE
4ee02c9f-98c1-5c25-9afd-b0d78eabe0e5 | note | Inspection: By - D / E
c22ef4f9-f701-4489-92b0-203b90616733 | checkpoint | 4.2 - Install drive coupling to Pump 2
179b174f-5e40-52b7-b508-33086056c1f0 | note | Inspection Point: Quality Control Activity - Completion of the nstallation of shaft drive coupling - Pump 2
27b4aaeb-206a-56f2-b360-6a5b186f6013 | note | Acceptance Criteria - Completion of Item 4.1
d8726d32-37c5-58ce-a808-a6f4a82f0fbb | note | Verifying Document - Report provided by Engineering Specialist - Wallace Murray Electrical
7cfe7920-7033-5cf7-916f-55e70c12374f | note | Frequency - Once
f7e651f8-e8de-5359-8cfe-30e52cb25726 | note | Inspection Type (Visual, other) - Visual + Photograph
2d226274-4de7-58f7-9497-d4dfa47a7c22 | note | Inspection: Key - A / I
40955d40-9cfd-50d2-a2c6-9fba1a0f6f41 | note | Inspection: By - IP
2406cc7d-0e69-46d4-932f-1cddfa5fef51 | section | SECTION 5 – FINAL INSPECTION AND HANDOVER
fe412602-90a4-4c76-a340-e52b69b48c6c | checkpoint | 5.1 - Pump 2 & Motor assembly
fe5a81b2-6c82-5edb-8f4b-2676532cf0ae | note | Inspection Point: Quality Control Activity - Final inspection & check. Rotate motor/pump assembly by hand to esnure smooth operation
57963e0f-f27e-58c0-997e-be393c0d7b34 | note | Acceptance Criteria - Pump/Motor assembly completed and laser alignemt completed and verified. Drive coupling installed
f716c40d-6178-5f9f-8aff-65a0daeaa04d | note | Verifying Document - As per methodology, Shaft lignment verification & Manufacturers Instructions.
e53402b0-f5f7-51bc-bad9-752d5f2ef0b1 | note | ○ Detailed report provided from specialist - Wallace Murray Electrical
ccacc0f0-da82-55a3-830b-1e63289f86ee | note | Frequency - once
7dc2feea-9690-575c-9a93-20dfe0fd9b77 | note | Inspection Type (Visual, other) - Visual + Document
62f8e1c7-6cfa-552c-9880-fe7f9eda7570 | note | Inspection: Key - I
324b6e40-59c6-5417-bf45-87fa8893b203 | note | Inspection: By - IP
5cd85ed7-0b91-401b-ba45-152d4961880c | checklist | 561482-ITP-005.3 - Pump. Motor Shaft Alignment - Pump 3 | itp | 561482-ITP-005.3 - Pump. Motor Shaft Alignment - Pump 3
7a375857-cb6f-4a86-bc78-9ada83fa342e | section | SECTION 3 – RECEIVING INSPECTIONS
27dcceae-aa2b-44d5-bf16-e8750fb5da12 | checkpoint | 3.1 - Align pump and motor shafts and install coupling - Pump & Motor Assembly 3
5893dcb7-823b-53fc-90e2-ed7a5049ae76 | note | Inspection Point: Quality Control Activity - Downer to engage a specialist to laser align motor and pump shafts to within 0.025mm
e8a59a0c-671f-5815-a53c-33d98c03186a | note | Acceptance Criteria - Completion of the assebmly to pump and motor 3 including mounting to the plinth.
ebc75702-0c4e-51f6-8cd0-3d64d3a49a50 | note | Verifying Document - Downer 561482-ITP-004.3
048512a9-5467-5cea-9c36-dc4c7e61963d | note | Frequency - once
24c92551-7f22-59b3-bcd8-ca507cffe7b2 | note | Inspection Type (Visual, other) - Visual + Photograph + document provided by specialist
f240bc3c-0205-58f6-bdcd-cdd62bc343a7 | note | Inspection: Key - QE
0e5b566a-8dcf-566f-b4bf-f36f3d1683ac | note | Inspection: By - D / E
371e6ee1-41e8-4751-8542-a125f745120c | section | SECTION 4 – IN-PROCESS INSPECTIONS
ae2aa987-58d0-4046-b92d-6a5e58daa4b2 | checkpoint | 4.1 - Align pump and motor shafts and install coupling - Pump & Motor Assembly 3
94f927e1-e24c-5f8b-adf4-ae53f8a22775 | note | Inspection Point: Quality Control Activity - Engage Engineering Specialist to adjust and align motor and pump shafts using laser alignment
c82bbd30-5e21-5029-a5be-3213fccd4832 | note | Acceptance Criteria - Pump and motor shafts are aligned to the specified tolerances on X-Y-Z axis to tolerance of 0.025mm
a7370b22-f297-55ab-a381-a68958038191 | note | Verifying Document - Report provided by Engineering Specialist - Wallace Murray Electrical
15b723b7-2f2d-51db-839c-de7c4b08fbf6 | note | Frequency - once
f22e0acb-e13e-5790-84c2-32cc3ec37fb5 | note | Inspection Type (Visual, other) - Visual + Photograph + document provided by specialist
9de4197e-aa94-520d-9013-03e47bde7aba | note | Inspection: Key - QE
5d2bbc37-6777-5175-a06f-e6aa9b336feb | note | Inspection: By - D / E
bd4a6dde-2312-4ad4-bf2a-7ee9dc86c756 | checkpoint | 4.2 - Install drive coupling to Pump 3
3e8086cd-ab5c-51d1-8d0d-0544ae8a2dc6 | note | Inspection Point: Quality Control Activity - Completion of the nstallation of shaft drive coupling - Pump 3
5f622266-cffb-5738-9a52-1fa00d38ab68 | note | Acceptance Criteria - Completion of Item 4.1
8bc8a698-46e6-5b26-a66b-2f4abd61db60 | note | Verifying Document - Report provided by Engineering Specialist - Wallace Murray Electrical
8c21c70e-7d8b-53a4-a808-4edf4490f52a | note | Frequency - Once
b14c57e7-6cd2-5c06-a2a3-18014ea77fe3 | note | Inspection Type (Visual, other) - Visual + Photograph
03aef200-c098-56f9-a677-caca5d3ba887 | note | Inspection: Key - A / I
01abb95a-5825-5a44-83bf-c9335708ef24 | note | Inspection: By - IP
84de3274-b806-4364-bf27-9eb2f3010bb9 | section | SECTION 5 – FINAL INSPECTION AND HANDOVER
e5ffc516-3461-4033-8375-11c79c4253c7 | checkpoint | 5.1 - Pump 3 & Motor assembly
5a8b6fa7-6d32-56cc-8715-eaacd1625404 | note | Inspection Point: Quality Control Activity - Final inspection & check. Rotate motor/pump assembly by hand to esnure smooth operation
030e7ebd-e0e8-532a-9826-454b82d22c03 | note | Acceptance Criteria - Pump/Motor assembly completed and laser alignemt completed and verified. Drive coupling installed
44504101-c5f3-585f-a1ec-50900f8ab3b2 | note | Verifying Document - As per methodology, Shaft lignment verification & Manufacturers Instructions.
a87b5f7e-2cad-56f0-9241-bb9b5c787630 | note | ○ Detailed report provided from specialist - Wallace Murray Electrical
3f381d50-90a2-5d54-a32e-26d9cf34891b | note | Frequency - once
3dde77c1-afad-50eb-81b4-0835e4e5d12a | note | Inspection Type (Visual, other) - Visual + Document
9a9a70e3-975a-50d1-badd-29fd03d6a9e0 | note | Inspection: Key - I
40b63d3d-0ebf-5ddd-95e4-24814ffca5df | note | Inspection: By - IP
b8eff675-8b3a-47b5-b0db-e9ef0bd8c878 | checklist | 561482-ITP-006.1 - Pipe & Fitting Installation Pump 1 | itp | 561482-ITP-006.1 - Pipe & Fitting Installation Pump 1
d8606108-ebfb-423c-8430-5a2335d9b85c | section | SECTION 3 – RECEIVING INSPECTIONS
e9765e7b-4e31-4d23-bf9b-1f5a05af5352 | checkpoint | 3.1 - Stainless Steel Pipe components
67672620-43ef-5a3f-8b7d-6e1b4a5ef88c | note | Inspection Point: Quality Control Activity - Obtain the mill certificates for the materials used - 316L Stainless Steel
79d47014-2ca7-5cfa-be4a-c9b9927e0b2f | note | Acceptance Criteria - Documents from the supplier/Manufacturer
6bae09bf-4975-5f73-81b0-f7b6195cf537 | note | Verifying Document - Mill Certificates & Welding certificates
82d24078-91c9-50e8-841c-0600d5f5171c | note | Frequency - Once
abc8b964-d056-53d2-b016-c466a5fc5291 | note | Inspection Type (Visual, other) - Documentation
31145320-c8a3-5798-b5e8-bf64eab9acc7 | note | Inspection: Key - C
6dd768ad-70dd-5a61-9fa0-00a1e643b3a9 | note | Inspection: By - IP
b9fa7e86-aee2-4b55-aaaf-845611b82a1e | checkpoint | 3.2 - Stainless Steel Pipe components
aa78ee3e-9b8c-5a94-a55a-150d28caf04d | note | Inspection Point: Quality Control Activity - Take delivery of components from Supplier. Verify all components have been delivered
d25722c5-8e9b-50d8-b5f8-228e72e77e11 | note | Acceptance Criteria - Quantities as shown on the drawings
f0467330-f29e-5459-bbf5-2d1ad12bfd48 | note | Verifying Document - Drawing M0001
3dd1fee4-1dd6-5528-ac44-c83da3e5dc13 | note | ○ Drawing M0002
8ec8dab6-b2a2-5f41-84c5-68158f351b6e | note | ○ Drawing M0003
a3cf5de5-668d-5c90-b8ea-bda32360f224 | note | ○ Drawing M0004
ab38019e-37f1-554a-90b0-d0a88e6f55eb | note | Frequency - Once
2411d3f4-a043-54a5-966b-9e758c53a73f | note | Inspection Type (Visual, other) - Visual
7421e0bc-2d56-52e6-ad11-29b4885464bb | note | Inspection: Key - C
57263c10-8b0a-51e8-8566-03d959482438 | note | Inspection: By - IP
1e3b5505-301b-4a29-85ef-378048a4b6a0 | checkpoint | 3.3 - Stainless Steel Pipe components
fa5912f0-d69d-551d-8b73-a37aca1d6dbb | note | Inspection Point: Quality Control Activity - Take delivery of components from Supplier. Verify all components have been manufactured to the correct dimensions
a9a59311-7f10-56a6-8875-854aef1ed8d3 | note | Acceptance Criteria - Dimensions & orientation as shown on the drawings
a0ff312a-3346-52c0-9ffe-d23e37b9d0fe | note | Verifying Document - Drawing M0001
e6a50a71-93d6-5954-99b7-09be0ae25ab1 | note | ○ Drawing M0002
9f0fc32b-8cc1-5494-884c-114d84cca37a | note | ○ Drawing M0003
4fd0c703-4d9d-5683-8c7e-c575907027d4 | note | ○ Drawing M0004
90a4b2b3-04ef-541a-b28c-2eac602fbb63 | note | Frequency - Once
0c169dde-f5be-5f3b-ac8f-56758c46aea1 | note | Inspection Type (Visual, other) - Visual Dimension Inspection
b2cc7987-ffec-5e07-94e0-60d289f6ca07 | note | Inspection: Key - D
c0ad7035-c3e3-565f-898f-896a4d3dfc12 | note | Inspection: By - IP
de3fe68f-67fd-439f-bdd2-e67a9354e14e | checkpoint | 3.4 - Valves & Ancillaries (Blanking Flange)
3da76aee-349f-548a-935d-80884f6213bb | note | Inspection Point: Quality Control Activity - Check and verify that the Manufacturer & Type is approved for use by the client
1a35a80a-1ef0-5d1d-bc01-b392a4b9541a | note | Acceptance Criteria - Must be on the Approved Products list
c33a1f54-b26f-5d32-9c9c-c67b0c06c647 | note | Verifying Document - Specification - Approved Materials list
8fef2806-344c-56dd-833b-aa1310066493 | note | Frequency - Once
f8e07a5d-c12b-5d6d-ae15-5e2a5da97d69 | note | Inspection Type (Visual, other) - Visual
6b14be53-cca0-5163-bcb9-a5d93530105e | note | Inspection: Key - C
645c18ec-fa19-5d8c-b789-1095999dc6e9 | note | Inspection: By - IP
a73108ff-003f-4c10-bbfe-df23cf36fc34 | checkpoint | 3.5 - Dress Sets (gaskets & fasteners)
05147020-0c68-5762-93af-258dfaf1b51f | note | Inspection Point: Quality Control Activity - Check and verify that the dress sets are compatible with the flanges and the gasket material is correct. Check correct quantities/sizes/flange patterns etc
14efc88d-e2aa-5377-a626-67d7737f40b5 | note | Acceptance Criteria - Must be on the Approved Products list
696fb468-eeb1-5f60-b200-57347879e2c8 | note | Verifying Document - Specification - Approved Materials list
704a5f48-6ecd-5973-a1b3-9322a2f9552d | note | Frequency - Once
cc791cf9-1b96-5040-bf34-90c121eb497c | note | Inspection Type (Visual, other) - Visual
fc8bae6f-d177-5a8a-8b7f-374f11e64fc7 | note | Inspection: Key - C
5975537e-aae6-5b8c-b387-a1d2f291baa9 | note | Inspection: By - IP
ca555757-2216-49b6-ada2-259186b44f79 | section | SECTION 4 – IN-PROCESS INSPECTIONS
234ce304-6996-47d8-997d-dafd6c7f0803 | checkpoint | 4.1 - Fasten Wet Well side/pick-up to spool (cast in wall) Item # 1
d9ca77c5-f64a-539a-9fe0-28f36b7cfa87 | note | Inspection Point: Quality Control Activity - Install gasket, bolts & nuts and tighten. Torque fasteners
70ecac8f-b2b8-58a1-a13c-d42bdb992f79 | note | Acceptance Criteria - Use diametrically opposed touque sequence
94c12448-4346-5a89-b860-bcc54a177aa2 | note | Verifying Document - As per WSA-109 Australiann Water Standards Guidelines - 80N.m
5caa2650-7916-5f43-a0b4-4918b4e20503 | note | Frequency - Each flange
030df472-58b0-53dd-82b7-14d4fcc69cf5 | note | Inspection Type (Visual, other) - Record & attach to ITP
8784db47-019a-52ed-9b2d-dde375ebc6ec | note | Inspection: Key - Inspection
a32c9cde-52ee-5438-8c43-a11b9f4c3746 | note | Inspection: By - IP
cd3c3b76-a124-443f-bd7a-f241674c00c6 | checkpoint | 4.2 - Fasten Dry Well side from spool (cast in wall) Item # 2
ddda5591-02d7-5b21-bb7a-5c46fb966a8a | note | Inspection Point: Quality Control Activity - Install gasket, bolts & nuts and tighten. Torque fasteners to relevant water standards
d55462eb-3c5a-587a-89d1-56750fb7120f | note | Acceptance Criteria - Use diametrically opposed touque sequence
ac3d693e-57fa-561e-98f7-1f9e12038f1b | note | Verifying Document - As per WSA-109 Australiann Water Standards Guidelines - 80N.m
71fc488d-23d0-5ea2-9c76-172ea8453304 | note | Frequency - Each Flange
5864a802-cce4-569f-a8fc-8a1542b3c03d | note | Inspection Type (Visual, other) - Record & attach to ITP
2b56a0bd-da85-51c1-8053-a98ab741d001 | note | Inspection: Key - Inspection
0920fd53-3c16-53a4-9085-1ac43130254b | note | Inspection: By - IP
aefae2ae-bff1-4069-90b3-ba748ce0dbee | checkpoint | 4.3 - Blanking Flange150mm (suction side)
c28c4bd3-0700-55f6-81d8-e8868952bbd6 | note | Inspection Point: Quality Control Activity - Install gasket, bolts & nuts and tighten. Torque fasteners to relevant water standards
bdb3082e-1fa6-5440-b97f-b6d80f08a2dc | note | Acceptance Criteria - Use diametrically opposed touque sequence
26dc2a55-4ea6-55da-90c4-8a5df5cc2564 | note | Verifying Document - As per WSA-109 Australian Water Standards Guidelines - 80N.m
fe50b6d0-badf-5848-ab72-868ace4ef695 | note | Frequency - Each Side of Valve
eb043b32-75c3-556a-931d-deb608a867bc | note | Inspection Type (Visual, other) - Record & attach to ITP
fdacc0d6-5f18-58c5-bf4e-5b780132abc9 | note | Inspection: Key - Inspection
cb133296-8ba9-56ba-9367-e97629a0e40d | note | Inspection: By - IP
874ae99a-8535-440d-8a6e-be877dcd371b | checkpoint | 4.3 - Blanking Flange150mm (Discharge side)
1ad00f9d-520f-50ea-bd68-6c273e456590 | note | Inspection Point: Quality Control Activity - Install gasket, bolts & nuts and tighten. Torque fasteners to relevant water standards
79556b7e-21ca-5610-95ae-03b0ba7a7b5d | note | Acceptance Criteria - Use diametrically opposed touque sequence
c131d0cb-7c77-57bf-ac0c-a3fb5713784c | note | Verifying Document - As per WSA-109 Australian Water Standards Guidelines - 80N.m
a6e4dc1d-cea6-57b6-b8a5-e7e9271b29f5 | note | Frequency - Each Side of Valve
811bea7d-2158-515d-959f-2c0f00aa9212 | note | Inspection Type (Visual, other) - Record & attach to ITP
beae2312-2df3-5242-9531-4917116f3ea3 | note | Inspection: Key - Inspection
a65a3fa0-4638-587b-95c1-70b08cb1478c | note | Inspection: By - IP
a0be18aa-0a41-472c-bf1b-87273405f569 | section | SECTION 5 – FINAL INSPECTION AND HANDOVER
7af52dfa-a61c-4d58-b3bc-5f3b3f0e0f7a | checkpoint | 5.1 - Final inspection to installed pipework
b4ca4837-155d-54c0-b11e-346e8acaebca | note | Inspection Point: Quality Control Activity - At completion of pipework
befff066-16e5-5cac-b4ac-5abf0f3723ce | note | Acceptance Criteria - Flanges are straight and bolts tightened all threads sealed and leak free
1d877c3b-4812-5e5e-81f4-95eeb14450b0 | note | Verifying Document - As per drawings
41278976-0f33-56d1-af3f-c4abf6517896 | note | Frequency - once
9edb0b65-5090-59bb-bf56-95b053c7da62 | note | Inspection Type (Visual, other) - Visual
c142ee9e-93e7-595f-aff9-0fdb87fabdf0 | note | Inspection: Key - I
500f23bd-15ff-54fa-8a1d-c8e3f432f5bc | note | Inspection: By - IP
ecdf23f9-2dce-4a64-ad57-ff520af84341 | checklist | 561482-ITP-006.2 - Pipe & Fitting Installation Pump 2 | itp | 561482-ITP-006.2 - Pipe & Fitting Installation Pump 2
b9880f77-e1c8-44ce-94c2-cebf2646204e | section | SECTION 3 – RECEIVING INSPECTIONS
96911d34-4328-4c52-b275-d0ad6c03d911 | checkpoint | 3.1 - Stainless Steel Pipe components
1ca77c7c-bf6c-55eb-814f-8e84200ea91d | note | Inspection Point: Quality Control Activity - Obtain the mill certificates for the materials used - 316L Stainless Steel
69e0455c-9c4e-511b-9431-44cd9ca76673 | note | Acceptance Criteria - Documents from the supplier/Manufacturer
0c2734df-b74d-51a2-a2a8-47ca3e96b553 | note | Verifying Document - Mill Certificates & Welding certificates
4b4df5a7-4df7-5703-b323-e1792e8435a9 | note | Frequency - Once
d99316f8-7912-52d3-814a-2a6e34b79d3e | note | Inspection Type (Visual, other) - Documentation
2d915948-4443-5143-b2a5-23b4b2c140d9 | note | Inspection: Key - C
e83ac92d-6b01-51ad-b656-c79f916796e1 | note | Inspection: By - IP
0281de9e-c1b8-4367-a651-282796551903 | checkpoint | 3.2 - Stainless Steel Pipe components
2e6501e2-6581-5988-bbbf-179e959e88d8 | note | Inspection Point: Quality Control Activity - Take delivery of components from Supplier. Verify all components have been delivered
92f4b7dc-d94e-5b88-9fd3-0181d796c402 | note | Acceptance Criteria - Quantities as shown on the drawings
67ccecd8-69d4-5df3-b076-dd0b8756b050 | note | Verifying Document - Drawing M0001
fddb0806-6092-508c-a395-4f5f75f8a155 | note | ○ Drawing M0002
8886385b-ad13-534e-9f39-7bafa5bfb056 | note | ○ Drawing M0003
fdf90a21-824a-5768-804c-e8c947cc4506 | note | ○ Drawing M0004
a1c7d928-3df6-55c4-bf05-db7f4404cf1e | note | Frequency - Once
8737336a-050d-5d21-8472-3671a54b1483 | note | Inspection Type (Visual, other) - Visual
7f53d69c-1c3e-515e-a4bf-a524fd8be644 | note | Inspection: Key - C
9ef1e997-e97d-5121-8ee2-98162dbff7f3 | note | Inspection: By - IP
2309c2ea-68be-44a9-8302-9c0606e25188 | checkpoint | 3.3 - Stainless Steel Pipe components
8d83767a-1648-56f4-a597-8ed6f8380a5f | note | Inspection Point: Quality Control Activity - Take delivery of components from Supplier. Verify all components have been manufactured to the correct dimensions
d14e2a9d-e65c-5b0a-be71-b807bd957027 | note | Acceptance Criteria - Dimensions & orientation as shown on the drawings
5bd07c60-fd46-5908-a55e-e92a2de589f3 | note | Verifying Document - Drawing M0001
436245b2-1d0c-57e1-8aec-4d5df3700fbe | note | ○ Drawing M0002
bcd8cdf7-ce9a-5ced-a1fd-3d370fe812bd | note | ○ Drawing M0003
5670afc3-34a9-597c-a0c0-15579afe5cf6 | note | ○ Drawing M0004
963a9be0-a0bc-5343-866e-36a95c9ff1fe | note | Frequency - Once
29b42713-3f21-59e5-a8dc-1ad7caa31c58 | note | Inspection Type (Visual, other) - Visual Dimension Inspection
5f7f2485-615b-53e4-81ce-dc94987ea330 | note | Inspection: Key - D
6621146e-afb0-502c-914d-eb37ea737e30 | note | Inspection: By - IP
3e16f3e6-42cf-4b22-b499-3a42452d0401 | checkpoint | 3.4 - Valves & Ancillaries
8aeaac1c-c901-5d40-b14c-e5b74e5bf42f | note | Inspection Point: Quality Control Activity - Check and verify that the Manufacturer & Type is approved for use by the client
f8bc6db5-14d7-5676-a47c-93751f390838 | note | Acceptance Criteria - Must be on the Approved Products list
ba85bc8c-ab3d-5d6b-91be-8991911237fa | note | Verifying Document - Specification - Approved Materials list
5b8cddff-db5e-5747-b6da-49cd73a7f5d0 | note | Frequency - Once
255c6152-10a0-5f43-a880-947037fd0f83 | note | Inspection Type (Visual, other) - Visual
6b42a257-4535-554f-95a8-85aec352cf41 | note | Inspection: Key - C
0e9615cd-a0ad-5264-9721-d32136f41f66 | note | Inspection: By - IP
1d305302-a30a-4912-8f5b-bdc71feca59d | checkpoint | 3.5 - Dress Sets (gaskets & fasteners)
bfef5849-5b28-5637-b5c1-68f423af4355 | note | Inspection Point: Quality Control Activity - Check and verify that the dress sets are compatible with the flanges and the gasket material is correct. Check correct quantities/sizes/flange patterns etc
c477352d-5940-5742-9d6a-578b6a5b3fd4 | note | Acceptance Criteria - Must be on the Approved Products list
76e0c7a9-e1eb-5689-8f13-129a4114756f | note | Verifying Document - Specification - Approved Materials list
1ba82a15-4e16-5321-8bc0-1a7aececfe25 | note | Frequency - Once
700bbfed-cca6-581a-ab04-5880857b1c3c | note | Inspection Type (Visual, other) - Visual
4d91a056-9d58-5ee8-a927-07c6185935cd | note | Inspection: Key - C
5a1da9fb-833a-5d04-b36f-deb01cec82f8 | note | Inspection: By - IP
58018d37-34f5-4cb8-a119-6deab1f412f6 | section | SECTION 4 – IN-PROCESS INSPECTIONS
d6747565-bff8-4321-9945-002f3452ecc2 | checkpoint | 4.1 - Fasten Wet Well side/pick-up to spool (cast in wall) Item # 1
5611d823-2f7c-5390-952b-3c7fc5cf5b01 | note | Inspection Point: Quality Control Activity - Install gasket, bolts & nuts and tighten. Torque fasteners
aa1a8fee-607f-56dd-baff-db3175e363ae | note | Acceptance Criteria - Use diametrically opposed touque sequence
556e4882-147a-55f5-83a1-cadeb808f0d9 | note | Verifying Document - As per WSA-109 Australiann Water Standards Guidelines - 80N.m
e053d352-c643-5343-8643-18016b447bdb | note | Frequency - Each flange
19aa908e-1457-5deb-9ea0-a0c48c48a269 | note | Inspection Type (Visual, other) - Record & attach to ITP
93dfc4c7-5e24-5a72-85bb-89787013cdaf | note | Inspection: Key - Inspection
c5ebfab9-ede5-55ca-81e8-3afb7eaa6255 | note | Inspection: By - IP
30328ebf-df38-4bc4-bab4-3fb159ddcac2 | checkpoint | 4.2 - Fasten Dry Well side from spool (cast in wall) Item # 2
dfdb7daf-640d-5971-bbb8-6b4bcc687b55 | note | Inspection Point: Quality Control Activity - Install gasket, bolts & nuts and tighten. Torque fasteners to relevant water standards
86d43d3e-2599-5f34-bebe-d4fd71178f8a | note | Acceptance Criteria - Use diametrically opposed touque sequence
aa492383-856f-5268-a57f-9b17ac58e4a8 | note | Verifying Document - As per WSA-109 Australiann Water Standards Guidelines - 80N.m
2989b14d-b129-5dda-9547-c7b2b0af22dc | note | Frequency - Each Flange
8848765d-a6ad-55a7-ba42-a1d70e0d71d5 | note | Inspection Type (Visual, other) - Record & attach to ITP
c17377b7-550e-5d1e-bd77-37ea4e61c759 | note | Inspection: Key - Inspection
13376683-82cb-5b62-864d-6f732344d5e9 | note | Inspection: By - IP
33bf0813-5649-4ba1-8e50-021015259516 | checkpoint | 4.3 - Isolation Valve 150mm Item # 3 (suction side)
c88d13e6-fd25-5b51-bf35-b70cc7887658 | note | Inspection Point: Quality Control Activity - Install gasket, bolts & nuts and tighten. Torque fasteners to relevant water standards
1e7defdd-25e1-511f-b5c4-1905fa029fdb | note | Acceptance Criteria - Use diametrically opposed touque sequence
04526a9e-aa93-59e6-ae75-fddb7971917d | note | Verifying Document - As per WSA-109 Australiann Water Standards Guidelines - 80N.m
a86685e2-0e0d-59dc-9111-76bf2205c013 | note | Frequency - Each Side of Valve
b59f6f92-8a7f-5eba-885b-4b52e7237e5d | note | Inspection Type (Visual, other) - Record & attach to ITP
7d321e87-18d8-5f40-9d7b-4e322c9b0a15 | note | Inspection: Key - Inspection
8990b10f-32bf-5d62-b05b-0b82ccb0801b | note | Inspection: By - IP
9b7e863b-cd0a-4ff3-9a74-515c0d40b176 | checkpoint | 4.4 - 150mm Dismantling joint (suction side) Item#4
a48d90ae-82fe-5233-bd66-4e686e72b2f4 | note | Inspection Point: Quality Control Activity - Torque fasteners to relevant water standards
4d90d7c6-8895-5bf4-b85a-7713f7e39b4d | note | Acceptance Criteria - Use diametrically opposed touque sequence and manufactruers instructions
781a06a1-af8b-52f2-9f00-56c477bd1909 | note | Verifying Document - As per WSA-109 Australiann Water Standards Guidelines - 80N.m
806b0b2a-8c4b-5dea-9ff6-3b790343bfe6 | note | Frequency - Once
36382eac-9dc8-5927-a4af-78d217505a4a | note | Inspection Type (Visual, other) - Record & attach to ITP
0e627b03-c207-598f-8225-09442e1336c8 | note | Inspection: Key - Inspection
3353e402-eab8-5b45-9851-42fb90356b25 | note | Inspection: By - IP
5a83b1c1-8876-4250-b65d-ee9da2f35050 | checkpoint | 4.5 - 150mm Flange Adaptor Spool. Item # 5
81e50aae-8f77-5470-ab6f-2a2e2c196333 | note | Inspection Point: Quality Control Activity - Install gasket, bolts & nuts and tighten. Torque fasteners to relevant water standards
a573a8d7-c9f8-559a-b18a-5425d20f41af | note | Acceptance Criteria - Use diametrically opposed touque sequence
62c6d8b6-bc93-59ff-a168-5315908b8647 | note | Verifying Document - As per WSA-109 Australiann Water Standards Guidelines - 80N.m
158f44a9-84f9-54a5-97bf-ddbe4bbad44e | note | Frequency - Once
517a35cf-6616-5926-8e05-eefea773b971 | note | Inspection Type (Visual, other) - Record & attach to ITP
e17b08cb-08a8-55ca-a9ff-c9f07c1f56eb | note | Inspection: Key - Inspection
d2a7b2e0-5fb1-5c4e-9c72-7b700b1e0fb3 | note | Inspection: By - IP
941b9736-617f-4385-9d4c-b0e6817f37bb | checkpoint | 4.6 - 100mm to150mm Sweeping Flange Adaptor Spool. Item # 6
d1fa2a07-1b60-5dd7-abd8-1453ff6e4a2b | note | Inspection Point: Quality Control Activity - Install gasket, bolts & nuts and tighten. Torque fasteners to relevant water standards
f2980767-a659-51ce-8079-9ea2c13ec066 | note | Acceptance Criteria - Use diametrically opposed touque sequence
3fe7d66c-b900-5128-b854-560c3479e413 | note | Verifying Document - As per WSA-109 Australiann Water Standards Guidelines - 80N.m
fe919e49-f083-58ee-b72b-91c0ec7641bc | note | Frequency - Once
f724fd6c-4264-5f2a-868d-cdbfe8de81c9 | note | Inspection Type (Visual, other) - Record & attach to ITP
ba7960e7-bd71-5bb6-8c43-e06007ddde1d | note | Inspection: Key - Inspection
5bbb5043-b9a1-56cf-8a78-1b6a60f82e6c | note | Inspection: By - IP
7d28013e-08a6-451c-8899-0b1a746cc8b2 | checkpoint | 4.7 - 150mm swing check valve. Item # 7
68fedaf9-1c93-52f8-8494-ccc105f996b2 | note | Inspection Point: Quality Control Activity - Install gasket, bolts & nuts and tighten. Torque fasteners to relevant water standards
a8f688d7-93aa-5b6e-9469-075f65178db8 | note | Acceptance Criteria - Use diametrically opposed touque sequence
c8ba7434-f511-5c49-a37a-36db29a00022 | note | Verifying Document - As per WSA-109 Australiann Water Standards Guidelines - 80N.m
7e666594-265e-5bcd-8c1c-ff2ed6d9a15f | note | Frequency - Each Side of Valve
60a5f616-5575-5f5f-8058-6dd7fe19633b | note | Inspection Type (Visual, other) - Record & attach to ITP
55107423-76a6-5897-9ffa-3b7f2ea4af32 | note | Inspection: Key - Inspection
560b2abf-8eca-5c0d-be4a-5d1a01e19563 | note | Inspection: By - IP
f8549c83-313d-436d-be67-c3d451d64d8c | checkpoint | 4.8 - 150mm Sweeping Spool (discharge). Item # 8
ca7cab1a-1b5c-55b8-87aa-0799bf9b2293 | note | Inspection Point: Quality Control Activity - Install gasket, bolts & nuts and tighten. Torque fasteners to relevant water standards
0cfd491f-0e90-5dfd-b0ad-e030e97ae621 | note | Acceptance Criteria - Use diametrically opposed touque sequence
02bdc93c-e0a7-5f8b-9487-5848d26917fa | note | Verifying Document - As per WSA-109 Australiann Water Standards Guidelines - 80N.m
64389bfd-f807-583c-82fb-0871e8d1c01b | note | Frequency - Once
c36c7b08-aceb-56df-b0bb-ebbcbe9ecdab | note | Inspection Type (Visual, other) - Record & attach to ITP
7702735e-619c-5592-8720-626b24c70212 | note | Inspection: Key - Inspection
0406c148-cce0-510e-bca8-296a55d02692 | note | Inspection: By - IP
b7716a82-861b-438e-8787-925137762fb9 | checkpoint | 4.9 - 150mm Dismantling joint (discharge side) Item#4
decf3ce8-edf3-5a76-80e1-3da848e0fe8d | note | Inspection Point: Quality Control Activity - Torque fasteners to relevant water standards
d626b6c0-483e-541b-bf86-ff7391bc3819 | note | Acceptance Criteria - Use diametrically opposed touque sequence and manufactruers instructions
301e77bc-f1bc-5d5d-b87d-0452a23b6372 | note | Verifying Document - As per WSA-109 Australiann Water Standards Guidelines - 80N.m
3563dc44-029b-5290-a2c1-b2236befd340 | note | Frequency - Once
381d90d5-95a8-5f72-8a27-8bc534da706e | note | Inspection Type (Visual, other) - Record & attach to ITP
18aac799-0742-5ab4-9a34-0bdb3e479e09 | note | Inspection: Key - Inspection
0cace3a1-a025-5494-b9f0-5733503b2d35 | note | Inspection: By - IP
3603ab52-fe18-476c-94e5-0424786ca1f4 | checkpoint | 4.10 - Isolation Valve 150mm Item # 3 (discharge side)
613fd92e-aae0-5759-bd40-e3eacfbd46c8 | note | Inspection Point: Quality Control Activity - Install gasket, bolts & nuts and tighten. Torque fasteners to relevant water standards
6f79b1de-5e89-5d8c-9f88-1a06b6589cfa | note | Acceptance Criteria - Use diametrically opposed touque sequence
88a2feda-4480-54d3-a5ff-de3ee216cde3 | note | Verifying Document - As per WSA-109 Australiann Water Standards Guidelines - 80N.m
cb284ec9-8031-5b30-80b9-36a15b0d402c | note | Frequency - Each Side of Valve
43721e36-87af-55a4-a053-bc15ca9b818b | note | Inspection Type (Visual, other) - Record & attach to ITP
a8f8d25f-7be5-5f2f-add1-81c17ff56564 | note | Inspection: Key - Inspection
0cd9f547-d66a-5629-a5eb-75060ed5a389 | note | Inspection: By - IP
11901f3e-bad4-476f-9353-5bd85eb6d399 | checkpoint | 4.11 - Pipework bracketing installed and is secure.
fdbb4115-1f02-5f6c-87ec-78431e7f23f4 | note | Inspection Point: Quality Control Activity - At completion of pipework
bd4766f0-a879-5893-a35e-edffc4a7584f | note | Acceptance Criteria - Pipework complete and installed. Adjustable brackets
6d6cf4a5-3422-519f-881a-ea13227d7b6e | note | Verifying Document - As indicated on the drawings
39f4cd8a-f3a7-5bca-bd6a-922163e9c699 | note | Frequency - once
827754bb-ba28-5e8d-963f-6bf3d621ec9b | note | Inspection Type (Visual, other) - Visual
fa247592-bcc4-5d5e-ac1b-340d18aa614a | note | Inspection: Key - I
3b2fc194-2ffe-5380-9d62-14f093c87b43 | note | Inspection: By - IP
82f82659-7981-4ab8-9106-de9eef390547 | section | SECTION 5 – FINAL INSPECTION AND HANDOVER
b15fce3b-9ae2-4f16-a2d4-09d96b0acff5 | checkpoint | 5.1 - Final inspection to installed pipework
56eb81d5-3d61-5517-b44f-e1a39cacc9a6 | note | Inspection Point: Quality Control Activity - At completion of pipework
1a1dd471-95ec-598c-9a5e-751b709eb234 | note | Acceptance Criteria - Flanges are straight and bolts tightened all threads sealed and leak free
7ef4cf0e-89f7-5e4c-8816-011089a43493 | note | Verifying Document - As per drawings
de0e872c-0b95-5304-85cf-38246875cb19 | note | Frequency - once
9ad6143d-254a-5120-9d01-878b06c1852d | note | Inspection Type (Visual, other) - Visual
7a864cc4-8d05-5475-9940-1b6353fa7adc | note | Inspection: Key - I
c9892299-d337-56f1-a9c3-e5cc795b04ee | note | Inspection: By - IP
559938ce-47b6-4e93-a7d5-54028306e682 | checkpoint | 5.2 - Instrumentation. e.g. Pressure transducers and sensors are fitted correctly - No Damage
e471ec81-aedb-518f-8302-a91804279c2d | note | Inspection Point: Quality Control Activity - At completion of pipework
e1ed3373-38a8-50a9-be8e-493c8a0d7736 | note | Acceptance Criteria - Pipework is installed and correct fittings installed to accept the instrumentation
fe28191c-66e5-5205-bcfd-b87735094642 | note | Verifying Document - As per drawing schematics
3a726664-27a0-521c-a989-123ba74f2a6e | note | Frequency - once
2456b281-b35e-5116-b2b6-401fe6351b81 | note | Inspection Type (Visual, other) - Visual
82a9c429-392e-5900-9b8f-3043d16a7bb3 | note | Inspection: Key - I
832f2628-66df-5624-9099-3ece0f4f20df | note | Inspection: By - IP
92a84c7a-489c-41af-bd0e-ad686a4146a1 | checkpoint | 5.3 - Pipework bracketing installed and is secure.
3e3a7bda-df45-5036-992c-7de32f2f4cfa | note | Inspection Point: Quality Control Activity - At completion of pipework
f38349a3-375a-5916-a563-1712c62d9bae | note | Acceptance Criteria - Pipework complete and installed
d5475874-c751-5ed5-957d-af6419b79c28 | note | Verifying Document - As per drawings
94649beb-7e6c-58f0-94b6-e4b1edaa5356 | note | Frequency - once
36576e85-e91d-5db6-9caf-b33940f329af | note | Inspection Type (Visual, other) - Visual
5552ad98-941f-5916-8eb3-84151c5b5f44 | note | Inspection: Key - I
c5e393ae-714d-5506-9f78-bd60eaac0efb | note | Inspection: By - IP
cfb97827-fd38-4581-bc10-2e87e551ab85 | checklist | 561482-ITP-006.3 - Pipe & Fitting Installation Pump 3 | itp | 561482-ITP-006.3 - Pipe & Fitting Installation Pump 3
b42c6ac3-9255-4690-9283-4b31fb8454ac | section | SECTION 3 – RECEIVING INSPECTIONS
d0fede74-778d-4039-9331-52d1cdd65e22 | checkpoint | 3.1 - Stainless Steel Pipe components
c5261988-f054-51c9-8b4c-04b4e3670aee | note | Inspection Point: Quality Control Activity - Obtain the mill certificates for the materials used - 316L Stainless Steel
90992016-0cb2-58dd-aac0-205155fb4a76 | note | Acceptance Criteria - Documents from the supplier/Manufacturer
612e0151-a290-52ff-803f-03f5025bfbc4 | note | Verifying Document - Mill Certificates & Welding certificates
303e51ca-5fc0-5d2c-b83b-2b56eaf237e1 | note | Frequency - Once
a49bcd6a-a74f-5ffc-bdbb-c2a6950ae3fc | note | Inspection Type (Visual, other) - Documentation
79d45f11-90d8-54a2-8f8b-5a9b302c8d6e | note | Inspection: Key - C
c42324be-2eb0-5ca4-b956-62d44bff93f7 | note | Inspection: By - IP
8a9744e4-c18e-413a-aa00-1e123e2da9b4 | checkpoint | 3.2 - Stainless Steel Pipe components
93e85615-459e-59ba-b9a9-67ff7ff2230a | note | Inspection Point: Quality Control Activity - Take delivery of components from Supplier. Verify all components have been delivered
74c2a989-78f2-52aa-aa61-7824b3283fd3 | note | Acceptance Criteria - Quantities as shown on the drawings
c80fee4e-2aa0-5b6a-8e70-75f208f1f132 | note | Verifying Document - Drawing M0001
4d455161-f3a4-5d85-b6ae-46a0f4a3b725 | note | ○ Drawing M0002
122b0d82-d4b1-5114-833f-04df1be2aca2 | note | ○ Drawing M0003
98cfc088-855b-5608-a4e5-11caa6460a8b | note | ○ Drawing M0004
96b552a5-f253-5f49-816f-80ac78fccb3a | note | Frequency - Once
ab978ea9-71c3-5c1d-bdb3-b85cc676c1d3 | note | Inspection Type (Visual, other) - Visual
56a7278b-8b07-5c55-ace3-7851639b12a4 | note | Inspection: Key - C
cf9e8a08-cd79-512c-8d7b-4493f8616352 | note | Inspection: By - IP
ccaf9a83-66b6-4782-a28e-ca7e65417faa | checkpoint | 3.3 - Stainless Steel Pipe components
1f1d2f1e-050b-5b7b-83b5-2dc8b7e34179 | note | Inspection Point: Quality Control Activity - Take delivery of components from Supplier. Verify all components have been manufactured to the correct dimensions
17818ac9-ebc8-5160-abc6-55ad05762a60 | note | Acceptance Criteria - Dimensions & orientation as shown on the drawings
711ab90d-75c1-5152-a09a-f6b7c75da0a6 | note | Verifying Document - Drawing M0001
8261307c-0f5b-5458-92c6-f7350a95895c | note | ○ Drawing M0002
e96ae188-664f-5016-aa7a-85cdcc5486f1 | note | ○ Drawing M0003
a33b8f79-b4bf-5779-b809-59a232eaae00 | note | ○ Drawing M0004
80482a50-0812-50ac-923e-d8cba19197ba | note | Frequency - Once
5432dcd7-2792-5b10-b041-823a3fb7d994 | note | Inspection Type (Visual, other) - Visual Dimension Inspection
1f7a3f41-27e5-5d8e-abf2-2d80e1644422 | note | Inspection: Key - D
82869995-fb43-5875-825a-bc7c7419e6f1 | note | Inspection: By - IP
46dda6c9-eda8-4598-94a5-de7b19142f97 | checkpoint | 3.4 - Valves & Ancillaries
0e35853f-36d9-5eb3-be60-a18c65ca4cb3 | note | Inspection Point: Quality Control Activity - Check and verify that the Manufacturer & Type is approved for use by the client
96b1d56b-7663-5304-97b5-ee7039382770 | note | Acceptance Criteria - Must be on the Approved Products list
796279dc-466b-5071-8d06-f1398902b3e9 | note | Verifying Document - Specification - Approved Materials list
bb1e9ae0-5fed-5657-833a-77e67aa19c45 | note | Frequency - Once
7b3d49b5-4630-5e2f-8a4b-a9537db863f3 | note | Inspection Type (Visual, other) - Visual
caa595ac-254a-568e-9dc9-2b148a9e66c7 | note | Inspection: Key - C
4aa88059-8c23-561c-9487-e9f2c3accdde | note | Inspection: By - IP
2de45f86-3031-446a-b7a7-762599ae6ade | checkpoint | 3.5 - Dress Sets (gaskets & fasteners)
3a0f1f99-1269-5fe6-9828-3c6e6ac4156d | note | Inspection Point: Quality Control Activity - Check and verify that the dress sets are compatible with the flanges and the gasket material is correct. Check correct quantities/sizes/flange patterns etc
8f9cb03d-8536-5e99-a00c-678a24383dad | note | Acceptance Criteria - Must be on the Approved Products list
1cce3895-a10a-51aa-8c5c-71400c8cf6cd | note | Verifying Document - Specification - Approved Materials list
620833ed-05a6-54c6-a9d4-e103b05392e3 | note | Frequency - Once
0fde40c1-4319-5aeb-8476-be8b3f397606 | note | Inspection Type (Visual, other) - Visual
b0c0e7d7-9e0b-5c67-a93c-218a10dd15fe | note | Inspection: Key - C
50ca292e-0c4f-5a2b-bfe4-f9a2835b031a | note | Inspection: By - IP
1082815b-7f12-46f4-9644-53168c3469c6 | section | SECTION 4 – IN-PROCESS INSPECTIONS
f5970011-e40e-4088-b276-83d52ce4e0fe | checkpoint | 4.1 - Fasten Wet Well side/pick-up to spool (cast in wall) Item # 1
f355917e-fb89-5e8f-af9f-27c9c7e6fe28 | note | Inspection Point: Quality Control Activity - Install gasket, bolts & nuts and tighten. Torque fasteners
537059cc-1d7e-53da-ba51-3b8ff85a3653 | note | Acceptance Criteria - Use diametrically opposed touque sequence
0b9dc1c6-98a4-5ddb-bde9-be90e4d9620d | note | Verifying Document - As per WSA-109 Australiann Water Standards Guidelines - 80N.m
6b96b962-7b72-5c6e-bbac-108c8f7a0006 | note | Frequency - Each flange
c851e559-1641-5c9d-b748-bf96129dfd4f | note | Inspection Type (Visual, other) - Record & attach to ITP
15db1b77-09c7-5ac7-8a8a-0b726ef473f9 | note | Inspection: Key - Inspection
63a365ba-80fe-5ce4-8932-d345328a1b14 | note | Inspection: By - IP
854e8896-1f6d-4066-a508-2217683d4f2c | checkpoint | 4.2 - Fasten Dry Well side from spool (cast in wall) Item # 2
f7f7c8bf-5cb6-53dc-9bae-453c31febc73 | note | Inspection Point: Quality Control Activity - Install gasket, bolts & nuts and tighten. Torque fasteners to relevant water standards
7b36e7c6-ebab-5a11-b189-ef975fa4f733 | note | Acceptance Criteria - Use diametrically opposed touque sequence
58b33258-be7d-5eea-8cc7-d96aaf1f417d | note | Verifying Document - As per WSA-109 Australiann Water Standards Guidelines - 80N.m
b3e821db-b62e-5a15-b85b-0948edd9f0b7 | note | Frequency - Each Flange
577fb6a9-197a-5aed-865a-d50c26ce0e70 | note | Inspection Type (Visual, other) - Record & attach to ITP
d93fce37-d7a6-52d5-ab11-5a9bf6809568 | note | Inspection: Key - Inspection
3c3aeb3a-2ad6-5b6a-966d-e6518052c073 | note | Inspection: By - IP
29d4a627-364f-4b14-a925-4864b028b8c9 | checkpoint | 4.3 - Isolation Valve 150mm Item # 3 (suction side)
0375ec7b-7d15-57d9-98d2-8e7a543a7ad4 | note | Inspection Point: Quality Control Activity - Install gasket, bolts & nuts and tighten. Torque fasteners to relevant water standards
482efba2-a973-515e-8a77-ed5ef032b14c | note | Acceptance Criteria - Use diametrically opposed touque sequence
39cd518a-9e5b-57e6-a1f5-3443096bfc0f | note | Verifying Document - As per WSA-109 Australiann Water Standards Guidelines - 80N.m
f61b8005-d97d-5593-8a5c-4ff7843afc30 | note | Frequency - Each Side of Valve
c2687255-cc87-5ad2-ba69-828d75baea83 | note | Inspection Type (Visual, other) - Record & attach to ITP
4fd3cec5-6b22-5c4b-b5bd-4cb0fbb91c5c | note | Inspection: Key - Inspection
7957a4a6-5c9c-57e4-a737-f55aa8af4313 | note | Inspection: By - IP
78efdffc-e0d1-4a57-a893-d9d17664779b | checkpoint | 4.4 - 150mm Dismantling joint (suction side) Item#4
a232328d-1f84-5b34-ab76-5b73f4a5dd9a | note | Inspection Point: Quality Control Activity - Torque fasteners to relevant water standards
b1565531-640b-5c9a-8273-2b4821279298 | note | Acceptance Criteria - Use diametrically opposed touque sequence and manufactruers instructions
830f0a34-7b0f-5759-a540-74605dbf42ce | note | Verifying Document - As per WSA-109 Australiann Water Standards Guidelines - 80N.m
6bff1e55-d2dc-5be7-a076-27329adebcb4 | note | Frequency - Once
44ddfa07-81c0-5538-a6fd-cb9bf95634d8 | note | Inspection Type (Visual, other) - Record & attach to ITP
39aea7bc-928e-5903-8dab-9226fba79dfa | note | Inspection: Key - Inspection
53da1185-624a-573e-9108-c132fcbd0dc6 | note | Inspection: By - IP
983d988b-0e8d-45e6-94aa-7f067703fe6b | checkpoint | 4.5 - 150mm Flange Adaptor Spool. Item # 5
22ae6640-b6ab-5ade-bfe8-4e59b38da88f | note | Inspection Point: Quality Control Activity - Install gasket, bolts & nuts and tighten. Torque fasteners to relevant water standards
577d5fce-8180-5838-9847-3d688ea8078a | note | Acceptance Criteria - Use diametrically opposed touque sequence
466efce7-f27c-5037-815e-77fcb0958732 | note | Verifying Document - As per WSA-109 Australiann Water Standards Guidelines - 80N.m
66b484d4-df7e-513c-a96e-1b8106804c11 | note | Frequency - Once
ffab5aca-e2a5-505f-a931-81ce19d90787 | note | Inspection Type (Visual, other) - Record & attach to ITP
15ea6d3c-e4f6-5cd4-a165-b997725bb5ff | note | Inspection: Key - Inspection
83c77a7e-2270-5660-85b2-0a2dcd246852 | note | Inspection: By - IP
ff1b21a6-f2fe-4b77-8173-9ea539eccbb1 | checkpoint | 4.6 - 100mm to150mm Sweeping Flange Adaptor Spool. Item # 6
3d1fe5a6-3833-508a-bf2d-0f13ab178d49 | note | Inspection Point: Quality Control Activity - Install gasket, bolts & nuts and tighten. Torque fasteners to relevant water standards
2e9f5604-b5d7-5cc6-8d38-74062df8e349 | note | Acceptance Criteria - Use diametrically opposed touque sequence
abc9e1db-baa8-5220-ade7-c52485950a5f | note | Verifying Document - As per WSA-109 Australiann Water Standards Guidelines - 80N.m
ee43245d-7ab0-5f11-bc12-f726955fb47f | note | Frequency - Once
d2da54c9-2b8f-5c09-8efb-af0a07c2c819 | note | Inspection Type (Visual, other) - Record & attach to ITP
9e08647e-0b81-512f-81e2-5ee3c4a730c0 | note | Inspection: Key - Inspection
4083040e-dd17-5967-baa4-9f923ce2b4e6 | note | Inspection: By - IP
84784027-b08b-4162-976b-21c4fe506445 | checkpoint | 4.7 - 150mm swing check valve. Item # 7
e007c05f-4528-5056-b3be-fa1f538a265b | note | Inspection Point: Quality Control Activity - Install gasket, bolts & nuts and tighten. Torque fasteners to relevant water standards
b319815a-8042-5f77-b56c-03fd9a010d9c | note | Acceptance Criteria - Use diametrically opposed touque sequence
f465c2ab-ac7e-53a3-b9c4-cf11223ff9dc | note | Verifying Document - As per WSA-109 Australiann Water Standards Guidelines - 80N.m
9fccb7f6-dea7-55c0-8b1f-3afd00e35696 | note | Frequency - Each Side of Valve
4f985bc2-20c8-5a6c-ae90-eb4583041f36 | note | Inspection Type (Visual, other) - Record & attach to ITP
5a1a4954-7b01-5fd9-98a4-5e8be388130a | note | Inspection: Key - Inspection
94d6fb25-27af-55c3-8d3e-f99519bb3b99 | note | Inspection: By - IP
a770471e-9117-4df3-a739-ce233c50b5d4 | checkpoint | 4.8 - 150mm Sweeping Spool (discharge). Item # 8
ff881459-5ae1-5ff5-8ae0-c5369e90a1f5 | note | Inspection Point: Quality Control Activity - Install gasket, bolts & nuts and tighten. Torque fasteners to relevant water standards
02184b3f-322e-5b0e-a5e8-70106b42815e | note | Acceptance Criteria - Use diametrically opposed touque sequence
6c86f0d4-c930-5b68-a35b-6a7f18890bcc | note | Verifying Document - As per WSA-109 Australiann Water Standards Guidelines - 80N.m
8644d680-9739-5c18-9126-37d15ff4cf23 | note | Frequency - Once
e4bff31f-3106-5ec2-9085-4dd165a8a89c | note | Inspection Type (Visual, other) - Record & attach to ITP
1e23501d-30c4-547d-b5a4-75fabad412ee | note | Inspection: Key - Inspection
d1c248be-adc4-5ce1-b9d7-6836a54f663f | note | Inspection: By - IP
60ada0fe-835e-48f4-918d-bc6975b1649a | checkpoint | 4.9 - 150mm Dismantling joint (discharge side) Item#4
e5da41ac-543b-5c5f-a433-1ad58616d74e | note | Inspection Point: Quality Control Activity - Torque fasteners to relevant water standards
b98d7e7c-9852-5827-855f-c0dcff68ad3a | note | Acceptance Criteria - Use diametrically opposed touque sequence and manufactruers instructions
8957ed58-2574-5547-9aca-9a9df9cc6ca1 | note | Verifying Document - As per WSA-109 Australiann Water Standards Guidelines - 80N.m
5d126ca8-0c2e-5ba1-aaa9-53f7d939dc4d | note | Frequency - Once
8437cc27-e011-5886-b9c6-a07a6caf6475 | note | Inspection Type (Visual, other) - Record & attach to ITP
1009570e-8d54-5add-ac16-1f9183d87b1e | note | Inspection: Key - Inspection
365cda3d-1a48-5e5b-aa2b-abf18b90e42e | note | Inspection: By - IP
638157d3-3704-46a1-8a15-694a4dc3de01 | checkpoint | 4.10 - Isolation Valve 150mm Item # 3 (discharge side)
5fd86e09-fa49-5167-ad1a-5b5336f49421 | note | Inspection Point: Quality Control Activity - Install gasket, bolts & nuts and tighten. Torque fasteners to relevant water standards
84bafd06-76e3-5197-927f-692dd9ff29fa | note | Acceptance Criteria - Use diametrically opposed touque sequence
5c3073c1-dd0d-5525-a388-5eef3f2bbc14 | note | Verifying Document - As per WSA-109 Australiann Water Standards Guidelines - 80N.m
76f19e05-b359-5b93-9187-8f3e78ef659d | note | Frequency - Each Side of Valve
765b8401-b109-5016-8ec6-a3ca954b58e2 | note | Inspection Type (Visual, other) - Record & attach to ITP
15b9e92e-f86b-5682-93cb-b5b83a1692de | note | Inspection: Key - Inspection
c3eed160-23a7-5a81-9f94-6a36ae3f1a6d | note | Inspection: By - IP
7ada870e-4791-485f-98bc-28bc940bf291 | checkpoint | 4.11 - Pipework bracketing installed and is secure.
e57d93b4-344c-54cf-8b18-5c385752d8c9 | note | Inspection Point: Quality Control Activity - At completion of pipework
565a8e62-b6eb-5a39-97fb-409ffea4f689 | note | Acceptance Criteria - Pipework complete and installed. Adjustable brackets
f761ac55-9b2d-5d21-bbb1-311c9def2252 | note | Verifying Document - As indicated on the drawings
d2d1ab37-64be-5247-98b3-69974f35b001 | note | Frequency - once
7d310d1f-fd2c-508c-a296-a6a4141fb9ca | note | Inspection Type (Visual, other) - Visual
fb78e04f-851b-5693-b98c-78ed9038210d | note | Inspection: Key - I
b5bc7163-808d-5024-b340-c0f0cdbc4ac2 | note | Inspection: By - IP
d791a7e9-3ae7-4fd1-99eb-e8ba37d0929e | section | SECTION 5 – FINAL INSPECTION AND HANDOVER
06eac443-4ff1-4eca-80fa-3fc62b4def83 | checkpoint | 5.1 - Final inspection to installed pipework
ad903ae2-fc4b-5736-bdbc-85d2b2b3606b | note | Inspection Point: Quality Control Activity - At completion of pipework
3d0199d3-c4b1-58f8-9d34-b11941790c6d | note | Acceptance Criteria - Flanges are straight and bolts tightened all threads sealed and leak free
163207f0-641e-51d1-9a7c-4a39ae75fc57 | note | Verifying Document - As per drawings
60db29ca-3bca-5fda-9f81-6b88f6d641b5 | note | Frequency - once
fca7dc03-6751-5cb1-a956-7864a139045b | note | Inspection Type (Visual, other) - Visual
5e9b541a-5cc1-52f7-917b-7b751b284b66 | note | Inspection: Key - I
6e1dea6f-aba1-5369-9bbc-7ad039e32527 | note | Inspection: By - IP
02ed4267-273f-4fba-a0cc-8a29aa4e0e97 | checkpoint | 5.2 - Instrumentation. e.g. Pressure transducers and sensors are fitted correctly - No Damage
152cd870-74d1-5982-8143-c31480428267 | note | Inspection Point: Quality Control Activity - At completion of pipework
a3c23e62-1611-5ac3-a93e-b6ec7779c358 | note | Acceptance Criteria - Pipework is installed and correct fittings installed to accept the instrumentation
511ccd85-cfd8-58a8-b1bc-8da5c6e52864 | note | Verifying Document - As per drawing schematics
91ccd3c9-814f-5a5b-99bd-254fe5a4a2f4 | note | Frequency - once
e5b88775-4a7b-53a7-8aad-1a7996192535 | note | Inspection Type (Visual, other) - Visual
e5860c8a-1ffb-5663-8314-32acac5b437b | note | Inspection: Key - I
5198f3f0-ba55-5d05-b523-ae2ef08c5553 | note | Inspection: By - IP
66dfa977-ec12-496a-b3c7-0f81ca7931d2 | checkpoint | 5.3 - Pipework bracketing installed and is secure.
6d270fbc-facc-5a6c-917b-ac9a85071b88 | note | Inspection Point: Quality Control Activity - At completion of pipework
11e86d63-2962-500c-b784-9bde6c6ecdf6 | note | Acceptance Criteria - Pipework complete and installed
0f297426-3853-59b0-9e41-7765922019be | note | Verifying Document - As per drawings
8bd62f33-3999-5f6a-8264-8f6aef453293 | note | Frequency - once
a07bd5e3-6693-599d-a840-5b8c43406a34 | note | Inspection Type (Visual, other) - Visual
c4b4d552-6e28-5728-8e9d-9d35cca50d6b | note | Inspection: Key - I
eb2166f4-24d0-5d16-a977-13f7bdc081ce | note | Inspection: By - IP
7642b5f8-f11d-41d5-a802-8db12ba8dea4 | checklist | 561482-ITP-008 - Wet Well Wall - Final Pre-fill inspection | itp | 561482-ITP-008 - Wet Well Wall - Final Pre-fill inspection
897643ba-07af-4fcc-9320-841be3674d04 | section | SECTION 3 – RECEIVING INSPECTIONS
f12897b8-2b19-4264-9d16-42ec0f75a2d0 | checkpoint | 3.1 - Grout Castings (Penetrations 1 through 3)
bbc24578-6407-5fb2-87a4-22a89aa22937 | note | Inspection Point: Quality Control Activity - Inspection of castings.
1960f9a4-e39d-5777-9cb5-076082b89e82 | note | ○ Inspection for air pockets, cracks, fissures oa any other imperfections
97f30c4c-8e07-5f50-b455-edb28f25b28f | note | Acceptance Criteria - Completion of ITP's
8291fbb4-3c36-54fe-a95f-d5d7b1f80349 | note | ○ 561482-ITP-007.1.
5415109c-1002-5bbb-ba2b-16e662c062c7 | note | ○ 561482-ITP-007.2
20101704-dd44-597d-82b5-793b4ebfdb21 | note | ○ 561482-ITP-007.3
bc9e9c4b-864a-596b-b322-2662d0bf79fe | note | ○ Elapsed time of 7 days post pour
5c3ae48d-5b25-5eee-9cc8-ba630ee25ca0 | note | Verifying Document - None
2b700765-d981-540c-96f8-f727c3f9d53e | note | Frequency - Once
deb94657-1d35-5ce7-a4c7-6dbc56fd2403 | note | Inspection Type (Visual, other) - Visual + Photographs
ff873624-7bb1-58cd-9e65-32762746ec6d | note | Inspection: Key - A
ba4a9bd9-fd41-5d9d-85b4-40efc743858f | note | Inspection: By - IP
ed33693f-5050-4464-b663-4c31b7f705be | section | SECTION 4 – IN-PROCESS INSPECTIONS
4398457c-53ea-4878-b3f2-05c38dbb46e6 | checkpoint | 4.1 - Removal of Formwork - Penetration 1
81700b0b-2834-547d-a639-62c439fab0ff | note | Inspection Point: Quality Control Activity - Check and verify quality of casting both wet well side and Dry side
a19fa2b4-f00e-5aac-ae07-7f43fba12d91 | note | Acceptance Criteria - Approval from Engineer
0c09195a-9013-572f-b485-d4b6f6636f05 | note | Verifying Document - Drawing M0003 and annotations
e6445a2c-04e9-560a-ba23-8f41776f7998 | note | Frequency - once
1c23c4c9-9d9d-5306-8410-6f8f80072714 | note | Inspection Type (Visual, other) - Document + Visual + Photograph + Engineer site Inspection
8e6a1f4b-6c42-5174-9513-1ad7d4a49711 | note | Inspection: Key - H
e4b0b284-d8cd-50c3-a136-f8fefefa4414 | note | Inspection: By - CR
27aad9ec-dddb-4327-82f9-6e481d97e00f | signoff | AUTHORITY HOLDPOINT
fe3fc288-1354-4f7d-ad6d-ced6772537a5 | checkpoint | 4.2 - Removal of Formwork - Penetration 2
1bcb0277-bbea-5c3f-b6d5-4675eb1122fe | note | Inspection Point: Quality Control Activity - Check and verify quality of casting both wet well side and Dry side
8f8ac064-69cf-54e4-baa9-5921c31de038 | note | Acceptance Criteria - Approval from Engineer
0b9df010-81f4-5943-bbd1-aa19d0c4bc5a | note | Verifying Document - Drawing M0003 and annotations
19cf21a7-dad6-5d56-9cda-933c2dc367e3 | note | Frequency - once
04ef2d56-a9b9-5734-b416-9de66b3e7aae | note | Inspection Type (Visual, other) - Document + Visual + Photograph + Engineer site Inspection
0826d7a9-8f47-5ec4-b114-ae067da1c8f1 | note | Inspection: Key - H
a6810b6f-a70f-59bc-8b5a-db9636c29f62 | note | Inspection: By - CR
b526b4c1-206e-4f12-9884-73bf700865ff | signoff | AUTHORITY HOLDPOINT
ff744b9f-c905-4283-847e-ce6947edf9b5 | checkpoint | 4.3 - Removal of Formwork - Penetration 3
887ed539-bb4f-5ee0-aa5b-327974690aea | note | Inspection Point: Quality Control Activity - Check and verify quality of casting both wet well side and Dry side
c085d689-1989-5e62-a9f9-6c30de97001f | note | Acceptance Criteria - Approval from Engineer
f7ec5165-5cbc-514f-b2f0-938c3bf17b03 | note | Verifying Document - Drawing M0003 and annotations
424af3f2-734b-5721-a712-857dc7a0d265 | note | Frequency - once
6628437f-3487-5b82-abeb-3bece3e164f5 | note | Inspection Type (Visual, other) - Document + Visual + Photograph + Engineer site Inspection
6e3b5c08-6cf3-5bbf-88ce-731af695c479 | note | Inspection: Key - H
b057500b-60f8-51fa-8e7f-ce393267b5e3 | note | Inspection: By - CR
b8e43e6d-9f5d-4384-bb1d-c3dbb1521a14 | signoff | AUTHORITY HOLDPOINT
104aaff7-4e81-4310-bf89-4718162073a7 | section | SECTION 5 – FINAL INSPECTION AND HANDOVER
cf3a3214-1823-4c0f-b725-03dc72aeb464 | checkpoint | 5.1 - Clean tank of any Downer construction debris
b98ea6b2-cb7a-5eea-92fa-5b9680b6be1a | note | Inspection Point: Quality Control Activity - Upon removal of boxing and any remedial activities
4ada1e9a-9a4c-5bce-99cf-aecc8c1094e5 | note | Acceptance Criteria - Client Representative acceptance
5f48caee-6e20-59c1-87fe-9c9e844a4b17 | note | Verifying Document - NTC and or other written conformation
2acc671d-940e-5c5d-8fae-152a0a8452c9 | note | Frequency - once
c4421634-8691-5a3f-b840-b0a2df82a5c5 | note | Inspection Type (Visual, other) - Visual Inspection + Photograph
19195ceb-9546-5f78-8959-f716fab30a5c | note | Inspection: Key - H
d50ce20e-2a04-5b93-8167-795a1e60677f | note | Inspection: By - CR
d29e6a87-f5ad-4034-a5d7-4f1a9070e11d | signoff | AUTHORITY HOLDPOINT
b7f75978-2fd3-4215-86b6-e73e8a0bfb7e | checkpoint | 5.2 - Approval to fill Wet well
49c8b265-279c-5837-9b8a-021a862fc6ae | note | Inspection Point: Quality Control Activity - All activities and pre-checks required by client
f4f1b8f0-5849-5b06-af8e-a23c5ce96bb3 | note | Acceptance Criteria - Client Representative acceptance
f4216815-cb23-5beb-9b57-8b52951edb3b | note | Verifying Document - NTC and or other written conformation
88c15c67-3cf1-579e-b988-c0b3424b6dfa | note | Frequency - once
11fd71d4-2b13-5c8c-a2c8-c7b9330b4774 | note | Inspection Type (Visual, other) - Visual Inspection + Photograph
1c45a350-c4fe-5d14-9f0d-97d9dc90250a | note | Inspection: Key - C
ed334922-9caf-5771-8cf5-d8ba726de1a7 | note | Inspection: By - CR