## res
type | name | values | prefix | postfix | usage count | user addable | template name | Resource Id
checklist | 561482-ITP-001 - Switchboard Delivery and Electrical Installation | itp |  |  |  |  | 561482-ITP-001 - Switchboard Delivery and Electrical Installation
section | SECTION 3 – RECEIVING INSPECTIONS
checkpoint | 3.1 - Inspection of Switchboard Cabinet Pieces prior to delivery to site
label | Inspection Point: Quality Control Activity - Check overall condition. check connections for internal electrical components
label | Acceptance Criteria - Visual check and report any defects or areas of concern
label | Verifying Document - Email or NTE to report
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual + Photograph
label | Inspection: Key - C
label | Inspection: By - IP/B
checkpoint | 3.2 - Delivery of Switchboard materials to site
label | Inspection Point: Quality Control Activity - Check and verify that the switchboard materials have been delivered damage free
label | Acceptance Criteria - materials are damage free
label | Verifying Document - Material Delivery Docket
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual + inspection
label | Inspection: Key - C
label | Inspection: By - IP
section | SECTION 4 – IN-PROCESS INSPECTIONS
checkpoint | 4.1 - On-site assembly
label | Inspection Point: Quality Control Activity - Pre-Removal of required covers from Switchboard
label | Acceptance Criteria - isolation of switchboard is proven
label | Verifying Document - on site testing, isolation tags in place
label | Frequency - once
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.2 - On-site assembly
label | Inspection Point: Quality Control Activity - Switchboard exterior panels removed as required
label | Acceptance Criteria - work area secured, all voltage sources isolated. no signs of degradation on switchboard.
label | Verifying Document - Testing, photos as required
label | Frequency - once
label | Inspection Type (Visual, other) - Visual + Photograph
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.3 - Connection of new Generator Change-over cabinet.
label | Inspection Point: Quality Control Activity - connections of electrical cabling/bus bars.
label | Acceptance Criteria - Cabling/busbars connected correctly, insulation resistance between conductors acceptable.
label | Verifying Document - Switchboard Acceptance Test. C.O.C from Switchboard Manufacturers.
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual + Photograph
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.4 - Re-Energizing of switchboard
label | Inspection Point: Quality Control Activity - Switchboard work completed.
label | Acceptance Criteria - Switchboard upgrades completed. testing completed, interlocks between main switch and generator switch tested and verified, phase rotation confirmed
label | Verifying Document - Switchboard C.O.C, instrument test of supply mains.
label | Frequency - once
label | Inspection Type (Visual, other) - Visual + Inspection
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.5 - Submission/review/appr oval of the Level 2 FD
label | Inspection Point: Quality Control Activity - Software functionality meets expectations
label | Acceptance Criteria - Approval from consultant
label | Verifying Document - NTC
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - I
label | Inspection: By - IP
section | SECTION 5 – FINAL INSPECTION AND HANDOVER
checkpoint | 5.1 - Switchboard
label | Inspection Point: Quality Control Activity - Assembled, inspection carried out and approved
label | Acceptance Criteria - Electrical Testing completed, all covers in place and secured.
label | ○ All bolts present.
label | ○ R.O.I issued by electrical inspector.
label | Verifying Document - Switchboard acceptance test sheet.
label | Frequency - once
label | Inspection Type (Visual, other) - Visual + Document
label | Inspection: Key - I
label | Inspection: By - IP
checklist | 561482-ITP-002.2 - VSD2 Delivery and Installation | itp |  |  |  |  | 561482-ITP-002.2 - VSD2 Delivery and Installation
section | SECTION 3 – RECEIVING INSPECTIONS
checkpoint | 3.1 - Inspection of VSD prior to delivery to site
label | Inspection Point: Quality Control Activity - Check overall condition of packaging, noting any obvious signs of damage, Check rating of drives is correct.
label | Acceptance Criteria - Visual check and report any defects or areas of concern
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual + Photograph
label | Inspection: Key - C
label | Inspection: By - IP/B
checkpoint | 3.2 - Delivery of VSD to Site
label | Inspection Point: Quality Control Activity - Check and verify that correct VSD are delivered and that drives are undamaged
label | Acceptance Criteria - VSD are damage free
label | Verifying Document - VSD Delivery documents
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - C
label | Inspection: By - IP
section | SECTION 4 – IN-PROCESS INSPECTIONS
checkpoint | 4.1 - On-site assembly of mounting Frame
label | Inspection Point: Quality Control Activity - materials for frame delivered to site
label | Acceptance Criteria - Correct materials on site, protective coatings correct.
label | Verifying Document - Delivery Docket for Materials
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.2 - Assembly and mounting of Frame
label | Inspection Point: Quality Control Activity - Frame Built and bolted to Ground.
label | Acceptance Criteria - Frame built and Securely attached to ground, minimal flex/ movement when force applied.
label | Verifying Document - N/a
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual + Photograph
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.3 - Mounting of VSD to Frame
label | Inspection Point: Quality Control Activity - VSD Mounted to frame
label | Acceptance Criteria - VSD Mounted satisfactorily, bolts tight, washers and spring washers present, S/S bolts and fixings used.
label | Verifying Document - VSD Inspection Sheets.
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual + Photograph
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.4 - Installation of supply cables to VSD
label | Inspection Point: Quality Control Activity - Cables installed, not terminated into VSDs or switchboard
label | Acceptance Criteria - Correct Cables installed, suitable for full load plus 20 percent of VSD, insulation resistance acceptable
label | Verifying Document - VSD Cable Test Sheets.
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual + Inspection
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.5 - Installation of Output Cables From VSD to Motors
label | Inspection Point: Quality Control Activity - Cables installed, not terminated at motors or VSD
label | Acceptance Criteria - Correct Cables installed, suitable for full load of motor plus 20 percent, insulation resistance acceptable
label | Verifying Document - VSD Cable Test Sheets.
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual + Inspection
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.6 - Termination of cabling to VSD
label | Inspection Point: Quality Control Activity - Cables terminated into VSD
label | Acceptance Criteria - Correct Cables installed, terminals tightened to correct torque, cables prepared correctly. cable earths and screens fit off correctly.
label | Verifying Document - VSD Cable Test Sheets.
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual + Inspection
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.7 - Termination of cabling to Switchboard
label | Inspection Point: Quality Control Activity - Cables fit off at Switchboard.
label | Acceptance Criteria - Correct Cables installed, terminals tightened to correct torque, cables prepared correctly. cable earths and screens fit off correctly.
label | Verifying Document - VSD Cable Test Sheets.
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual + Inspection
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.8 - Verification of motors electrically
label | Inspection Point: Quality Control Activity - Cables installed, not terminated into motor
label | Acceptance Criteria - Correct motors installed. insulation resistance verified, winding configuration confirmed against nameplate.
label | Verifying Document - VSD Cable Test Sheets.
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual + Inspection
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.9 - Termination of cabling to Motor
label | Inspection Point: Quality Control Activity - Cables fit off at Motor
label | Acceptance Criteria - Cables Lugged off correctly, terminals tightened to correct torque
label | Verifying Document - Motor Inspection Sheets
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual + Photograph
label | Inspection: Key - I
label | Inspection: By - IP
section | SECTION 5 – FINAL INSPECTION AND HANDOVER
checkpoint | 5.1 - VSD
label | Inspection Point: Quality Control Activity - VSD Energised and set up, motor nameplate data entered, protections set, Labels attached
label | Acceptance Criteria - VSD parameters set correctly, inputs set up as per drawings. analog i/o set correctly and verified to plc
label | Verifying Document - VSD ITR Document
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual + Document
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 5.2 - Motors
label | Inspection Point: Quality Control Activity - Assembled and in position, inspection carried out and approved
label | Acceptance Criteria - Motors Tested, rotation direction confirmed, pumps operating as intended.
label | Verifying Document - Motor inspection Sheet
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual + Document
label | Inspection: Key - I
label | Inspection: By - IP
checklist | 561482-ITP-002.3 - VSD Delivery and Installation | itp |  |  |  |  | 561482-ITP-002.3 - VSD Delivery and Installation
section | SECTION 3 – RECEIVING INSPECTIONS
checkpoint | 3.1 - Inspection of VSD prior to delivery to site
label | Inspection Point: Quality Control Activity - Check overall condition of packaging, noting any obvious signs of damage, Check rating of drives is correct.
label | Acceptance Criteria - Visual check and report any defects or areas of concern
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual + Photograph
label | Inspection: Key - C
label | Inspection: By - IP/B
checkpoint | 3.2 - Delivery of VSD to Site
label | Inspection Point: Quality Control Activity - Check and verify that correct VSD are delivered and that drives are undamaged
label | Acceptance Criteria - VSD are damage free
label | Verifying Document - VSD Delivery documents
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - C
label | Inspection: By - IP
section | SECTION 4 – IN-PROCESS INSPECTIONS
checkpoint | 4.1 - On-site assembly of mounting Frame
label | Inspection Point: Quality Control Activity - materials for frame delivered to site
label | Acceptance Criteria - Correct materials on site, protective coatings correct.
label | Verifying Document - Delivery Docket for Materials
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.2 - Assembly and mounting of Frame
label | Inspection Point: Quality Control Activity - Frame Built and bolted to Ground.
label | Acceptance Criteria - Frame built and Securely attached to ground, minimal flex/ movement when force applied.
label | Verifying Document - N/a
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual + Photograph
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.3 - Mounting of VSD to Frame
label | Inspection Point: Quality Control Activity - VSDs Mounted to frame
label | Acceptance Criteria - VSD Mounted satisfactorily, bolts tight, washers and spring washers present, S/S bolts and fixings used.
label | Verifying Document - VSD Inspection Sheets.
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual + Photograph
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.4 - Installation of supply cables to VSD
label | Inspection Point: Quality Control Activity - Cables installed, not terminated into VSD or switchboard
label | Acceptance Criteria - Correct Cables installed, suitable for full load plus 20 percent of VSD, insulation resistance acceptable
label | Verifying Document - VSD Cable Test Sheets.
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual + Inspection
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.5 - Installation of Output Cables From VSD to Motors
label | Inspection Point: Quality Control Activity - Cables installed, not terminated at motors or VSD
label | Acceptance Criteria - Correct Cables installed, suitable for full load of motor plus 20 percent, insulation resistance acceptable
label | Verifying Document - VSD Cable Test Sheets.
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual + Inspection
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.6 - Termination of cabling to VSD
label | Inspection Point: Quality Control Activity - Cables terminated into VSD
label | Acceptance Criteria - Correct Cables installed, terminals tightened to correct torque, cables prepared correctly. cable earths and screens fit off correctly.
label | Verifying Document - VSD Cable Test Sheets.
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual + Inspection
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.7 - Termination of cabling to Switchboard
label | Inspection Point: Quality Control Activity - Cables fit off at Switchboard.
label | Acceptance Criteria - Correct Cables installed, terminals tightened to correct torque, cables prepared correctly. Cable earths and screens fit off correctly.
label | Verifying Document - VSD Cable Test Sheets.
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual + Inspection
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.8 - Verification of motors electrically
label | Inspection Point: Quality Control Activity - Cables installed, not terminated into motor
label | Acceptance Criteria - Correct motors installed. insulation resistance verified, winding configuration confirmed against nameplate.
label | Verifying Document - VSD Cable Test Sheets.
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual + Inspection
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.9 - Termination of cabling to Motor
label | Inspection Point: Quality Control Activity - Cables fit off at Motor
label | Acceptance Criteria - Cables Lugged off correctly, terminals tightened to correct torque
label | Verifying Document - Motor Inspection Sheets
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual + Photograph
label | Inspection: Key - I
label | Inspection: By - IP
section | SECTION 5 – FINAL INSPECTION AND HANDOVER
checkpoint | 5.1 - VSD
label | Inspection Point: Quality Control Activity - VSD Energised and set up, motor nameplate data entered, protections set, Labels attached
label | Acceptance Criteria - VSD parameters set correctly, inputs set up as per drawings. analog i/o set correctly and verified to plc
label | Verifying Document - Switchboard acceptance test sheet.
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual + Document
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 5.2 - Motors
label | Inspection Point: Quality Control Activity - Assembled and in position, inspection carried out and approved
label | Acceptance Criteria - Motors Tested, rotation direction confirmed, pumps operating as intended.
label | Verifying Document - Motor inspection Sheet
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual + Document
label | Inspection: Key - I
label | Inspection: By - IP
checklist | 561482-ITP-003.1 - Wet Well Wall Penetration 1 preparation | itp |  |  |  |  | 561482-ITP-003.1 - Wet Well Wall Penetration 1 preparation
section | SECTION 3 – RECEIVING INSPECTIONS
checkpoint | 3.1 - Masonry drill bits 18mm
label | Inspection Point: Quality Control Activity - Verify correct quantity & type
label | Acceptance Criteria - Compatable with the drill unit
label | Verifying Document - Manufacturers Technical data & Physical fitment
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual + Photographs
label | Inspection: Key - Inspection
label | Inspection: By - IP
checkpoint | 3.2 - Reinforcing Bar
label | Inspection Point: Quality Control Activity - Verify correct quantity & size/diameter has been delivered to site
label | Acceptance Criteria - Quantities correct. Dimensions correct.
label | Verifying Document - Drawing M0003
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual + Photographs
label | Inspection: Key - Inspection
label | Inspection: By - IP
checkpoint | 3.3 - Hilti RE-500 Chemical Anchor
label | Inspection Point: Quality Control Activity - Verify correct product is delivered.
label | ○ Check expiration date.
label | Acceptance Criteria - Quantities correct. Within expiration date
label | Verifying Document - HILTI Product Calculator APP. Delivery Docket
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual + Photographs
label | Inspection: Key - Inspection
label | Inspection: By - IP
checkpoint | 3.4 - Grout (Sika MonoTop 438R)
label | Inspection Point: Quality Control Activity - Verify correct product is delivered.
label | ○ Check expiration date.
label | Acceptance Criteria - Quantities correct. Within expiration date
label | Verifying Document - Delivery Docket
label | Frequency - Once
label | Inspection Type (Visual, other) - Written/Submission
label | Inspection: Key - Inspection
label | Inspection: By - IP
section | SECTION 4 – IN-PROCESS INSPECTIONS
checkpoint | 4.1 - Mark out penetration on both sides (wet & dry sides) using existing pipe as reference
label | Inspection Point: Quality Control Activity - Check and verify dimensains against drawings
label | Acceptance Criteria - Approval from Engineer
label | Verifying Document - Drawing M0003
label | Frequency - once
label | Inspection Type (Visual, other) - Document + Visual + Photograph + Engineer site Inspection
label | Inspection: Key - V
label | Inspection: By - CR
checkpoint | 4.2 - Proceed with breakout. Hammer drill
label | Inspection Point: Quality Control Activity - Monitor work and progress report any issues
label | Acceptance Criteria - Approval to proceed from item 4.1
label | Verifying Document - As per drawings listed dimensions & measurements
label | Frequency - once
label | Inspection Type (Visual, other) - Visual & Document
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.3 - Pre-pour inspection
label | Inspection Point: Quality Control Activity - Engineer Inspection
label | Acceptance Criteria - Dimensioin & Surface check. As per Drawing M0003 and notes.
label | ○ Approval to proceed via NTC.
label | ○ Correct profile achieved with 5mm roughness and any loose material removed
label | Verifying Document - NTC or other written confirmation
label | Frequency - once
label | Inspection Type (Visual, other) - Document
label | Inspection: Key - H
label | Inspection: By - CR
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 4.4 - Procurement of Reinforcing bar, starters & trimmers
label | Inspection Point: Quality Control Activity - Check measurents and vereify correct fitment
label | Acceptance Criteria - As detailed on Drawings & specifications
label | Verifying Document - Drawing M0003
label | Frequency - once
label | Inspection Type (Visual, other) - Document + Visual
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.5 - Installation of Reinforcing bar, starters & trimmers
label | Inspection Point: Quality Control Activity - Drill holes around perimeter to receive reinforcing bar. Check for correct diameter & corret embedment
label | Acceptance Criteria - As detailed on Drawings
label | Verifying Document - Drawing M0003
label | Frequency - once
label | Inspection Type (Visual, other) - Visual + Photographs
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.6 - Install pipe spool with puddle flange to be cast within wall
label | Inspection Point: Quality Control Activity - Check that orientation is correct and is in alignment with pump assembly
label | Acceptance Criteria - As detailed on Drawings M0003 and drawing notes
label | Verifying Document - Drawing M0001 Drawing M0002 Drawing M0003 Drawing M0004
label | Frequency - once
label | Inspection Type (Visual, other) - Visual + Photographs
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.7 - Hilti RE500. Chemical Anchor reinforcing bar, starters & trimmers into position
label | Inspection Point: Quality Control Activity - Observe Manufacturers instructions. Monitor curing times and temparatures. Use manufacturers calculator to determine product volumes. Sequence the installion to avoid obstruction
label | Acceptance Criteria - As detailed on Drawings and completion of item 4.6
label | Verifying Document - Drawing M0003
label | Frequency - once
label | Inspection Type (Visual, other) - Visual + Photographs
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.8 - Chemically treat perimeter using product HYDROTITE CJ1020
label | Inspection Point: Quality Control Activity - Observe Manufacturers instructiuons & Health and safety requirements
label | Acceptance Criteria - As detailed on Drawings and completion of item 4.7
label | Verifying Document - Drawing M0003
label | Frequency - once
label | Inspection Type (Visual, other) - Visual + Photographs
label | Inspection: Key - H
label | Inspection: By - IP
holdpoint | AUTHORITY HOLDPOINT
section | SECTION 5 – FINAL INSPECTION AND HANDOVER
checkpoint | 5.1 - Final dimensional check
label | Inspection Point: Quality Control Activity - At completion of all items on this ITP
label | Acceptance Criteria - Dimensions match the measurements shown on drawings
label | Verifying Document - Drawing M0003
label | Frequency - once
label | Inspection Type (Visual, other) - Visual + Photograph + Mark-up drawing
label | Inspection: Key - H
label | Inspection: By - CR
holdpoint | AUTHORITY HOLDPOINT
checklist | 561482-ITP-003.2 - Wet Well Wall Penetration 2 preparation | itp |  |  |  |  | 561482-ITP-003.2 - Wet Well Wall Penetration 2 preparation
section | SECTION 3 – RECEIVING INSPECTIONS
checkpoint | 3.1 - Masonry drill bits 18mm
label | Inspection Point: Quality Control Activity - Verify correct quantity & type
label | Acceptance Criteria - Compatable with the drill unit
label | Verifying Document - Manufacturers Technical data & Physical fitment
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual + Photographs
label | Inspection: Key - Inspection
label | Inspection: By - IP
checkpoint | 3.2 - Reinforcing Bar
label | Inspection Point: Quality Control Activity - Verify correct quantity & size/diameter has been delivered to site
label | Acceptance Criteria - Quantities correct. Dimensions correct.
label | Verifying Document - Drawing M0003
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual + Photographs
label | Inspection: Key - Inspection
label | Inspection: By - IP
checkpoint | 3.3 - Hilti RE-500 Chemical Anchor
label | Inspection Point: Quality Control Activity - Verify correct product is delivered.
label | ○ Check expiration date.
label | Acceptance Criteria - Quantities correct. Within expiration date
label | Verifying Document - HILTI Product Calculator APP. Delivery Docket
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual + Photographs
label | Inspection: Key - Inspection
label | Inspection: By - IP
checkpoint | 3.4 - Grout (Sika MonoTop 438R)
label | Inspection Point: Quality Control Activity - Verify correct product is delivered.
label | ○ Check expiration date.
label | Acceptance Criteria - Quantities correct. Within expiration date
label | Verifying Document - Delivery Docket
label | Frequency - Once
label | Inspection Type (Visual, other) - Written/Submission
label | Inspection: Key - Inspection
label | Inspection: By - IP
section | SECTION 4 – IN-PROCESS INSPECTIONS
checkpoint | 4.1 - Mark out penetration on both sides (wet & dry sides) using existing pipe as reference
label | Inspection Point: Quality Control Activity - Check and verify dimensains against drawings
label | Acceptance Criteria - Approval from Engineer
label | Verifying Document - Drawing M0003
label | Frequency - once
label | Inspection Type (Visual, other) - Document + Visual + Photograph + Engineer site Inspection
label | Inspection: Key - V
label | Inspection: By - CR
checkpoint | 4.2 - Proceed with breakout. Hammer drill
label | Inspection Point: Quality Control Activity - Monitor work and progress report any issues
label | Acceptance Criteria - Approval to proceed from item 4.1
label | Verifying Document - As per drawings listed dimensions & measurements
label | Frequency - once
label | Inspection Type (Visual, other) - Visual & Document
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.3 - Pre pour inspection
label | Inspection Point: Quality Control Activity - Engineer Inspection
label | Acceptance Criteria - Dimensioin & Surface sheck. As per Drawing M0003 and notes.
label | ○ Approval to proceed via NTC.
label | ○ Correct profile achieved with 5mm roughness and any loose material removed
label | Verifying Document - NTC or other written confirmation
label | Frequency - once
label | Inspection Type (Visual, other) - Document
label | Inspection: Key - H
label | Inspection: By - CR
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 4.4 - Procurement of Reinforcing bar, starters & trimmers
label | Inspection Point: Quality Control Activity - Check measurents and vereify correct fitment
label | Acceptance Criteria - As detailed on Drawings & specifications
label | Verifying Document - Drawing M0003
label | Frequency - once
label | Inspection Type (Visual, other) - Document + Visual
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.5 - Installation of Reinforcing bar, starters & trimmers
label | Inspection Point: Quality Control Activity - Drill holes around perimeter to receive reinforcing bar. Check for correct diameter & corret embedment
label | Acceptance Criteria - As detailed on Drawings
label | Verifying Document - Drawing M0003
label | Frequency - once
label | Inspection Type (Visual, other) - Visual + Photographs
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.6 - Install pipe spool with puddle flange to be cast within wall
label | Inspection Point: Quality Control Activity - Check that orientation is correct and is in alignment with pump assembly
label | Acceptance Criteria - As detailed on Drawings M0003 and drawing notes
label | Verifying Document - Drawing M0001 Drawing M0002 Drawing M0003 Drawing M0004
label | Frequency - once
label | Inspection Type (Visual, other) - Visual + Photographs
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.7 - Hilti RE500. Chemical Anchor reinforcing bar, starters & trimmers into position
label | Inspection Point: Quality Control Activity - Observe Manufacturers instructions. Monitor curing times and temparatures. Use manufacturers calculator to determine product volumes. Sequence the installion to avoid obstruction
label | Acceptance Criteria - As detailed on Drawings and completion of item 4.6
label | Verifying Document - Drawing M0003
label | Frequency - once
label | Inspection Type (Visual, other) - Visual + Photographs
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.8 - Chemically treat perimeter using product HYDROTITE CJ1020
label | Inspection Point: Quality Control Activity - Observe Manufacturers instructiuons & Health and safety requirements
label | Acceptance Criteria - As detailed on Drawings and completion of item 4.7
label | Verifying Document - Drawing M0003
label | Frequency - once
label | Inspection Type (Visual, other) - Visual + Photographs
label | Inspection: Key - H
label | Inspection: By - IP
holdpoint | AUTHORITY HOLDPOINT
section | SECTION 5 – FINAL INSPECTION AND HANDOVER
checkpoint | 5.1 - Final dimensional check
label | Inspection Point: Quality Control Activity - At completion of all items on this ITP
label | Acceptance Criteria - Dimensions match the measurements shown on drawings
label | Verifying Document - Drawing M0003
label | Frequency - once
label | Inspection Type (Visual, other) - Visual + Photograph + Mark-up drawing
label | Inspection: Key - H
label | Inspection: By - CR
holdpoint | AUTHORITY HOLDPOINT
checklist | 561482-ITP-003.3 - Wet Well Wall Penetration 3 preparation | itp |  |  |  |  | 561482-ITP-003.3 - Wet Well Wall Penetration 3 preparation
section | SECTION 3 – RECEIVING INSPECTIONS
checkpoint | 3.1 - Masonry drill bits 18mm
label | Inspection Point: Quality Control Activity - Verify correct quantity & type
label | Acceptance Criteria - Compatable with the drill unit
label | Verifying Document - Manufacturers Technical data & Physical fitment
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual + Photographs
label | Inspection: Key - Inspection
label | Inspection: By - IP
checkpoint | 3.2 - Reinforcing Bar
label | Inspection Point: Quality Control Activity - Verify correct quantity & size/diameter has been delivered to site
label | Acceptance Criteria - Quantities correct. Dimensions correct.
label | Verifying Document - Drawing M0003
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual + Photographs
label | Inspection: Key - Inspection
label | Inspection: By - IP
checkpoint | 3.3 - Hilti RE-500 Chemical Anchor
label | Inspection Point: Quality Control Activity - Verify correct product is delivered.
label | ○ Check expiration date.
label | Acceptance Criteria - Quantities correct. Within expiration date
label | Verifying Document - HILTI Product Calculator APP. Delivery Docket
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual + Photographs
label | Inspection: Key - Inspection
label | Inspection: By - IP
checkpoint | 3.4 - Grout (Sika MonoTop 438R)
label | Inspection Point: Quality Control Activity - Verify correct product is delivered.
label | ○ Check expiration date.
label | Acceptance Criteria - Quantities correct. Within expiration date
label | Verifying Document - Delivery Docket
label | Frequency - Once
label | Inspection Type (Visual, other) - Written/Submission
label | Inspection: Key - Inspection
label | Inspection: By - IP
section | SECTION 4 – IN-PROCESS INSPECTIONS
checkpoint | 4.1 - Mark out penetration on both sides (wet & dry sides) using existing pipe as reference
label | Inspection Point: Quality Control Activity - Check and verify dimensains against drawings
label | Acceptance Criteria - Approval from Engineer
label | Verifying Document - Drawing M0003
label | Frequency - once
label | Inspection Type (Visual, other) - Document + Visual + Photograph + Engineer site Inspection
label | Inspection: Key - V
label | Inspection: By - CR
checkpoint | 4.2 - Proceed with breakout. Hammer drill
label | Inspection Point: Quality Control Activity - Monitor work and progress report any issues
label | Acceptance Criteria - Approval to proceed from item 4.1
label | Verifying Document - As per drawings listed dimensions & measurements
label | Frequency - once
label | Inspection Type (Visual, other) - Visual & Document
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.3 - Pre pour inspection
label | Inspection Point: Quality Control Activity - Engineer Inspection
label | Acceptance Criteria - Dimensioin & Surface sheck. As per Drawing M0003 and notes.
label | ○ Approval to proceed via NTC.
label | ○ Correct profile achieved with 5mm roughness and any loose material removed
label | Verifying Document - NTC or other written confirmation
label | Frequency - once
label | Inspection Type (Visual, other) - Document
label | Inspection: Key - H
label | Inspection: By - CR
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 4.4 - Procurement of Reinforcing bar, starters & trimmers
label | Inspection Point: Quality Control Activity - Check measurents and vereify correct fitment
label | Acceptance Criteria - As detailed on Drawings & specifications
label | Verifying Document - Drawing M0003
label | Frequency - once
label | Inspection Type (Visual, other) - Document + Visual
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.5 - Installation of Reinforcing bar, starters & trimmers
label | Inspection Point: Quality Control Activity - Drill holes around perimeter to receive reinforcing bar. Check for correct diameter & corret embedment
label | Acceptance Criteria - As detailed on Drawings
label | Verifying Document - Drawing M0003
label | Frequency - once
label | Inspection Type (Visual, other) - Visual + Photographs
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.6 - Install pipe spool with puddle flange to be cast within wall
label | Inspection Point: Quality Control Activity - Check that orientation is correct and is in alignment with pump assembly
label | Acceptance Criteria - As detailed on Drawings M0003 and drawing notes
label | Verifying Document - Drawing M0001 Drawing M0002 Drawing M0003 Drawing M0004
label | Frequency - once
label | Inspection Type (Visual, other) - Visual + Photographs
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.7 - Hilti RE500. Chemical Anchor reinforcing bar, starters & trimmers into position
label | Inspection Point: Quality Control Activity - Observe Manufacturers instructions. Monitor curing times and temparatures. Use manufacturers calculator to determine product volumes. Sequence the installion to avoid obstruction
label | Acceptance Criteria - As detailed on Drawings and completion of item 4.6
label | Verifying Document - Drawing M0003
label | Frequency - once
label | Inspection Type (Visual, other) - Visual + Photographs
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.8 - Chemically treat perimeter using product HYDROTITE CJ1020
label | Inspection Point: Quality Control Activity - Observe Manufacturers instructiuons & Health and safety requirements
label | Acceptance Criteria - As detailed on Drawings and completion of item 4.7
label | Verifying Document - Drawing M0003
label | Frequency - once
label | Inspection Type (Visual, other) - Visual + Photographs
label | Inspection: Key - H
label | Inspection: By - IP
holdpoint | AUTHORITY HOLDPOINT
section | SECTION 5 – FINAL INSPECTION AND HANDOVER
checkpoint | 5.1 - Final dimensional check
label | Inspection Point: Quality Control Activity - At completion of all items on this ITP
label | Acceptance Criteria - Dimensions match the measurements shown on drawings
label | Verifying Document - Drawing M0003
label | Frequency - once
label | Inspection Type (Visual, other) - Visual + Photograph + Mark-up drawing
label | Inspection: Key - H
label | Inspection: By - CR
holdpoint | AUTHORITY HOLDPOINT
checklist | 561482-ITP-004.2 - Base. Pump. Motor Installation - Pumpset 2 | itp |  |  |  |  | 561482-ITP-004.2 - Base. Pump. Motor Installation - Pumpset 2
section | SECTION 3 – RECEIVING INSPECTIONS
checkpoint | 3.1 - Inspection of Plinths for pump 2
label | Inspection Point: Quality Control Activity - Check overall condition. Cracks/fissures or breaks or areas of weakness
label | Acceptance Criteria - Visual check and report any defects or areas of concern
label | Verifying Document - Email or NTE to report
label | Frequency - once
label | Inspection Type (Visual, other) - Visual + Photograph
label | Inspection: Key - C
label | Inspection: By - IP/B
checkpoint | 3.2 - Delivery of Pump 2 to site from Downer storage facility
label | Inspection Point: Quality Control Activity - Check and verify that correct pump is delivered
label | Acceptance Criteria - Pump is damage free
label | Verifying Document - 1. KSB delivery docket.
label | 2. Pump storage ITP
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - C
label | Inspection: By - IP
checkpoint | 3.3 - Delivery of Pump 2 Motor to site from Downer storage facility.
label | Inspection Point: Quality Control Activity - Check and verify that correct motor is delivered
label | Acceptance Criteria - Motor is damage free
label | Verifying Document - 1. KSB delivery docket.
label | 2. Pump storage ITP
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - C
label | Inspection: By - IP
checkpoint | 3.4 - Delivery of Pump & Motor mounting plate Downer storage facility
label | Inspection Point: Quality Control Activity - Check & Verify that correct Mounting plate is delivered
label | Acceptance Criteria - Mounting plate is dumensionally correct and is damage free
label | Verifying Document - 1. KSB delivery docket.
label | 2. Pump storage ITP
label | Frequency - Once
label | Inspection Type (Visual, other) - other
label | Inspection: Key - R
label | Inspection: By - CR
section | SECTION 4 – IN-PROCESS INSPECTIONS
checkpoint | 4.2 - On-site assembly
label | Inspection Point: Quality Control Activity - Correct Pump to Mounting Plate Assembly.
label | Acceptance Criteria - Ensure all fasteners are tight and toqued to manufacturers specifications
label | Verifying Document - KSB documentation & Installation Instructiions
label | Frequency - Once/per pumpset
label | Inspection Type (Visual, other) - Visual + Written
label | Inspection: Key - Inspection
label | Inspection: By - IP
checkpoint | 4.3 - Pump 2 Installation
label | Inspection Point: Quality Control Activity - Correct Mounting plate position on plinth, correct use of fasteners and torque requirements, in accordance with KSB installation instruction
label | Acceptance Criteria - Position is determined by the fixed pipework. Ensure alignment of flange face is parallel to wet well wall
label | Verifying Document - Drawing M0001
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual + Photograph
label | Inspection: Key - A/D
label | Inspection: By - IP
checkpoint | 4.4 - Pump 2 Motor Installation
label | Inspection Point: Quality Control Activity - Motor/Pump shaft alignment
label | Acceptance Criteria - Motor and shaft aligment as best as possible
label | Verifying Document - KSB documentation & Installation Instructiions. Nothing final alignment to be undertaken by a Technician - Ref: 561482-ITP-005.2
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual + Photograph
label | Inspection: Key - A/D
label | Inspection: By - IP
section | SECTION 5 – FINAL INSPECTION AND HANDOVER
checkpoint | 5.1 - Pump 2 & Motor assembly complete
label | Inspection Point: Quality Control Activity - Proceed with 561482-ITP005.2
label | Acceptance Criteria - Pump & Motor bolted to mounting plate and mounted to plinth.
label | Verifying Document - This ITP
label | Frequency - once
label | Inspection Type (Visual, other) - Visual + Document
label | Inspection: Key - I
label | Inspection: By - IP
checklist | 561482-ITP-004.3 - Base. Pump. Motor Installation - Pumpset 3 | itp |  |  |  |  | 561482-ITP-004.3 - Base. Pump. Motor Installation - Pumpset 3
section | SECTION 3 – RECEIVING INSPECTIONS
checkpoint | 3.1 - Inspection of Plinths for pump 3
label | Inspection Point: Quality Control Activity - Check overall condition. Cracks/fissures or breaks or areas of weakness
label | Acceptance Criteria - Visual check and report any defects or areas of concern
label | Verifying Document - Email or NTE to report
label | Frequency - once
label | Inspection Type (Visual, other) - Visual + Photograph
label | Inspection: Key - C
label | Inspection: By - IP/B
checkpoint | 3.2 - Delivery of Pump 3 to site from Downer storage facility
label | Inspection Point: Quality Control Activity - Check and verify that correct pump is delivered
label | Acceptance Criteria - Pump is damage free
label | Verifying Document - 1. KSB delivery docket.
label | 2. Pump storage ITP
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - C
label | Inspection: By - IP
checkpoint | 3.3 - Delivery of Pump 3 Motor to site from Downer storage facility.
label | Inspection Point: Quality Control Activity - Check and verify that correct motor is delivered
label | Acceptance Criteria - Motor is damage free
label | Verifying Document - 1. KSB delivery docket.
label | 2. Pump storage ITP
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - C
label | Inspection: By - IP
checkpoint | 3.4 - Delivery of Pump & Motor mounting plate Downer storage facility
label | Inspection Point: Quality Control Activity - Check & Verify that correct Mounting plate is delivered
label | Acceptance Criteria - Mounting plate is dumensionally correct and is damage free
label | Verifying Document - 1. KSB delivery docket.
label | 2. Pump storage ITP
label | Frequency - Once
label | Inspection Type (Visual, other) - other
label | Inspection: Key - R
label | Inspection: By - CR
section | SECTION 4 – IN-PROCESS INSPECTIONS
checkpoint | 4.2 - On-site assembly
label | Inspection Point: Quality Control Activity - Correct Pump to Mounting Plate Assembly.
label | Acceptance Criteria - Ensure all fasteners are tight and toqued to manufacturers specifications
label | Verifying Document - KSB documentation & Installation Instructiions
label | Frequency - Once/per pumpset
label | Inspection Type (Visual, other) - Visual + Written
label | Inspection: Key - Inspection
label | Inspection: By - IP
checkpoint | 4.3 - Pump 3 Installation
label | Inspection Point: Quality Control Activity - Correct Mounting plate position on plinth, correct use of fasteners and torque requirements, in accordance with KSB installation instruction
label | Acceptance Criteria - Position is determined by the fixed pipework. Ensure alignment of flange face is parallel to wet well wall
label | Verifying Document - Drawing M0001
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual + Photograph
label | Inspection: Key - A/D
label | Inspection: By - IP
checkpoint | 4.4 - Pump 3 Motor Installation
label | Inspection Point: Quality Control Activity - Motor/Pump shaft alignment
label | Acceptance Criteria - Motor and shaft aligment as best as possible
label | Verifying Document - KSB documentation & Installation Instructiions. Nothing filal alignment to be undertaken by a Technician - Ref: 561482-ITP-005.3
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual + Photograph
label | Inspection: Key - A/D
label | Inspection: By - IP
section | SECTION 5 – FINAL INSPECTION AND HANDOVER
checkpoint | 5.1 - Pump 3 & Motor assembly complete
label | Inspection Point: Quality Control Activity - Proceed with 561482-ITP005.3
label | Acceptance Criteria - Pump & Motor bolted to mounting plate and mounted to plinth.
label | Verifying Document - This ITP
label | Frequency - once
label | Inspection Type (Visual, other) - Visual + Document
label | Inspection: Key - I
label | Inspection: By - IP
checklist | 561482-ITP-007.1 - Wet Well Wall Penetration 1 pour | itp |  |  |  |  | 561482-ITP-007.1 - Wet Well Wall Penetration 1 pour
section | SECTION 3 – RECEIVING INSPECTIONS
checkpoint | 3.1 - Grout - SIKA MonoTop- 438R
label | Inspection Point: Quality Control Activity - Calculate Quantity
label | Acceptance Criteria - Correct volume to be calculated
label | Verifying Document - Product Datasheet
label | Frequency - Once
label | Inspection Type (Visual, other) - Written
label | Inspection: Key - R
label | Inspection: By - CR
checkpoint | 3.2 - Installed Reinforcing
label | Inspection Point: Quality Control Activity - Measure and check
label | Acceptance Criteria - Matches Design Drawings
label | Verifying Document - Drawing M0003
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual + Photographs
label | Inspection: Key - V
label | Inspection: By - IP
checkpoint | 3.3 - Spool/Puddle Flange
label | Inspection Point: Quality Control Activity - Measure and check
label | Acceptance Criteria - Pipework is straight and parallel to structure & pump
label | Verifying Document - As per drawing M0001 & M0002
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual + Photographs
label | Inspection: Key - V
label | Inspection: By - IP
section | SECTION 4 – IN-PROCESS INSPECTIONS
checkpoint | 4.1 - Boxing of penertation
label | Inspection Point: Quality Control Activity - Measure & Check. Ensure perimeter of boxing and pipe penetration is sealed to stop grout spill.
label | Acceptance Criteria - Matches Design Drawings by dinension and configuration
label | Verifying Document - Drawing M0003
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual + Inspection HOLD POINT
label | Inspection: Key - H
label | Inspection: By - CR
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 4.2 - Mixing of Grout
label | Inspection Point: Quality Control Activity - Ensure product is on hand & plenty of clean fresh water is readily available
label | Acceptance Criteria - As per manufacturers instructions/guidelines
label | Verifying Document - Product technical instruction sheets or certificate (if delivered)
label | Frequency - once
label | Inspection Type (Visual, other) - Document
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.3 - Casting of wall penetration
label | Inspection Point: Quality Control Activity - Monitor the consistency and quality of the grout fill
label | Acceptance Criteria - As per manufacturers instructions/guidelines
label | Verifying Document - Product technical instructions
label | Frequency - once
label | Inspection Type (Visual, other) - Dodument + Visual
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.4 - Vibrate
label | Inspection Point: Quality Control Activity - Vibrate to remove entrained air. Ensure all air is removed
label | Acceptance Criteria - Grout Placer Approval
label | Verifying Document - This ITP
label | Frequency - once
label | Inspection Type (Visual, other) - Visual + Photographs + Short video
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.5 - Monitor curing process
label | Inspection Point: Quality Control Activity - Monitor curing inspectiong the boxing and areas of potential grout leakage.
label | Acceptance Criteria - No evident shrinkage or deformation. Repotr any issues to Engineer
label | Verifying Document - As per drawings allowing 7 days curing time. Boxing can be removed after 72 hours
label | Frequency - once
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - I
label | Inspection: By - IP
section | SECTION 5 – FINAL INSPECTION AND HANDOVER
checkpoint | 5.1 - Remove boxing
label | Inspection Point: Quality Control Activity - At completion of all items on this ITP
label | Acceptance Criteria - Time period as indicated on programme
label | Verifying Document - This ITP
label | Frequency - once
label | Inspection Type (Visual, other) - Visual + Photograph
label | Inspection: Key - I
label | Inspection: By - IP
checklist | 561482-ITP-007.2 - Wet Well Wall Penetration 2 pour | itp |  |  |  |  | 561482-ITP-007.2 - Wet Well Wall Penetration 2 pour
section | SECTION 3 – RECEIVING INSPECTIONS
checkpoint | 3.1 - Grout - SIKA MonoTop- 438R
label | Inspection Point: Quality Control Activity - Calculate Quantity
label | Acceptance Criteria - Correct volume to be calculated
label | Verifying Document - Product Datasheet
label | Frequency - Once
label | Inspection Type (Visual, other) - Written
label | Inspection: Key - R
label | Inspection: By - CR
checkpoint | 3.2 - Installed Reinforcing
label | Inspection Point: Quality Control Activity - Measure and check
label | Acceptance Criteria - Matches Design Drawings
label | Verifying Document - Drawing M0003
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual + Photographs
label | Inspection: Key - V
label | Inspection: By - IP
checkpoint | 3.3 - Spool/Puddle Flange
label | Inspection Point: Quality Control Activity - Measure and check
label | Acceptance Criteria - Pipework is straight and parallel to structure & pump
label | Verifying Document - As per drawing M0001 & M0002
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual + Photographs
label | Inspection: Key - V
label | Inspection: By - IP
section | SECTION 4 – IN-PROCESS INSPECTIONS
checkpoint | 4.1 - Boxing of penertation
label | Inspection Point: Quality Control Activity - Measure & Check. Ensure perimeter of boxing and pipe penetration is sealed to stop grout spill.
label | Acceptance Criteria - Matches Design Drawings by dinension and configuration
label | Verifying Document - Drawing M0003
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual + Inspection HOLD POINT
label | Inspection: Key - H
label | Inspection: By - CR
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 4.2 - Mixing of Grout
label | Inspection Point: Quality Control Activity - Ensure product is on hand & plenty of clean fresh water is readily available
label | Acceptance Criteria - As per manufacturers instructions/guidelines
label | Verifying Document - Product technical instruction sheets or certificate (if delivered)
label | Frequency - once
label | Inspection Type (Visual, other) - Document
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.3 - Casting of wall penetration
label | Inspection Point: Quality Control Activity - Monitor the consistency and quality of the grout fill
label | Acceptance Criteria - As per manufacturers instructions/guidelines
label | Verifying Document - Product technical instructions
label | Frequency - once
label | Inspection Type (Visual, other) - Dodument + Visual
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.4 - Vibrate
label | Inspection Point: Quality Control Activity - Vibrate to remove entrained air. Ensure all air is removed
label | Acceptance Criteria - Grout Placer Approval
label | Verifying Document - This ITP
label | Frequency - once
label | Inspection Type (Visual, other) - Visual + Photographs + Short video
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.5 - Monitor curing process
label | Inspection Point: Quality Control Activity - Monitor curing inspectiong the boxing and areas of potential grout leakage.
label | Acceptance Criteria - No evident shrinkage or deformation. Repotr any issues to Engineer
label | Verifying Document - As per drawings allowing 7 days curing time. Boxing can be removed after 72 hours
label | Frequency - once
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - I
label | Inspection: By - IP
section | SECTION 5 – FINAL INSPECTION AND HANDOVER
checkpoint | 5.1 - Remove boxing
label | Inspection Point: Quality Control Activity - At completion of all items on this ITP
label | Acceptance Criteria - Time period as indicated on programme
label | Verifying Document - This ITP
label | Frequency - once
label | Inspection Type (Visual, other) - Visual + Photograph
label | Inspection: Key - I
label | Inspection: By - IP
checklist | 561482-ITP-007.3 - Wet Well Wall Penetration 3 pour | itp |  |  |  |  | 561482-ITP-007.3 - Wet Well Wall Penetration 3 pour
section | SECTION 3 – RECEIVING INSPECTIONS
checkpoint | 3.1 - Grout - SIKA MonoTop- 438R
label | Inspection Point: Quality Control Activity - Calculate Quantity
label | Acceptance Criteria - Correct volume to be calculated
label | Verifying Document - Product Datasheet
label | Frequency - Once
label | Inspection Type (Visual, other) - Written
label | Inspection: Key - R
label | Inspection: By - CR
checkpoint | 3.2 - Installed Reinforcing
label | Inspection Point: Quality Control Activity - Measure and check
label | Acceptance Criteria - Matches Design Drawings
label | Verifying Document - Drawing M0003
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual + Photographs
label | Inspection: Key - V
label | Inspection: By - IP
checkpoint | 3.3 - Spool/Puddle Flange
label | Inspection Point: Quality Control Activity - Measure and check
label | Acceptance Criteria - Pipework is straight and parallel to structure & pump
label | Verifying Document - As per drawing M0001 & M0002
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual + Photographs
label | Inspection: Key - V
label | Inspection: By - IP
section | SECTION 4 – IN-PROCESS INSPECTIONS
checkpoint | 4.1 - Boxing of penertation
label | Inspection Point: Quality Control Activity - Measure & Check. Ensure perimeter of boxing and pipe penetration is sealed to stop grout spill.
label | Acceptance Criteria - Matches Design Drawings by dinension and configuration
label | Verifying Document - Drawing M0003
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual + Inspection HOLD POINT
label | Inspection: Key - H
label | Inspection: By - CR
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 4.2 - Mixing of Grout
label | Inspection Point: Quality Control Activity - Ensure product is on hand & plenty of clean fresh water is readily available
label | Acceptance Criteria - As per manufacturers instructions/guidelines
label | Verifying Document - Product technical instruction sheets or certificate (if delivered)
label | Frequency - once
label | Inspection Type (Visual, other) - Document
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.3 - Casting of wall penetration
label | Inspection Point: Quality Control Activity - Monitor the consistency and quality of the grout fill
label | Acceptance Criteria - As per manufacturers instructions/guidelines
label | Verifying Document - Product technical instructions
label | Frequency - once
label | Inspection Type (Visual, other) - Dodument + Visual
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.4 - Vibrate
label | Inspection Point: Quality Control Activity - Vibrate to remove entrained air. Ensure all air is removed
label | Acceptance Criteria - Grout Placer Approval
label | Verifying Document - This ITP
label | Frequency - once
label | Inspection Type (Visual, other) - Visual + Photographs + Short video
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.5 - Monitor curing process
label | Inspection Point: Quality Control Activity - Monitor curing inspectiong the boxing and areas of potential grout leakage.
label | Acceptance Criteria - No evident shrinkage or deformation. Repotr any issues to Engineer
label | Verifying Document - As per drawings allowing 7 days curing time. Boxing can be removed after 72 hours
label | Frequency - once
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - I
label | Inspection: By - IP
section | SECTION 5 – FINAL INSPECTION AND HANDOVER
checkpoint | 5.1 - Remove boxing
label | Inspection Point: Quality Control Activity - At completion of all items on this ITP
label | Acceptance Criteria - Time period as indicated on programme
label | Verifying Document - This ITP
label | Frequency - once
label | Inspection Type (Visual, other) - Visual + Photograph
label | Inspection: Key - I
label | Inspection: By - IP
checklist | 561482-ITP-009.2 - Pre Commissioning Testing Pump & Valves - Pump 2 | itp |  |  |  |  | 561482-ITP-009.2 - Pre Commissioning Testing Pump & Valves - Pump 2
section | SECTION 3 – RECEIVING INSPECTIONS
checkpoint | 3.1 - Fill Wet Well
label | Inspection Point: Quality Control Activity - Pressure testing between suction and discharge isolation valves
label | Acceptance Criteria - Completion of 561482- ITP-008
label | Verifying Document - This ITP
label | Frequency - once
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - Inspection
label | Inspection: By - IP
section | SECTION 4 – IN-PROCESS INSPECTIONS
checkpoint | 4.1 - Filling of pipeline
label | Inspection Point: Quality Control Activity - Remove Entrained air
label | Acceptance Criteria - Bleed until water visible
label | Verifying Document - None
label | Frequency - once
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - Inspection
label | Inspection: By - IP
checkpoint | 4.2 - Visual Check over of Pump 2 and motor
label | Inspection Point: Quality Control Activity - Look for any visible leaking
label | Acceptance Criteria - All pipework connections tight All Cable & Terminations secure
label | Verifying Document - This ITP
label | Frequency - once
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - Inspection
label | Inspection: By - IP
checkpoint | 4.3 - Bump Start Pump 2
label | Inspection Point: Quality Control Activity - Check for correct pump rotation direction
label | Acceptance Criteria - Rotation direction is correct
label | Verifying Document - Pump build sheet literature
label | Frequency - once
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - Inspection
label | Inspection: By - IP
checkpoint | 4.4 - Pressure testing between suction and diacharge isolation valves - Pump 2
label | Inspection Point: Quality Control Activity - VSD Energised, water in pump pipelines
label | Acceptance Criteria - No visible leaking as per Item 4.2
label | Verifying Document - To meet Specification requirements and not to exceed pump manufacturers maximum pressure (Pump flanges 16Bar, Seal max pressure 30Bar)
label | Frequency - once
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - Inspection
label | Inspection: By - IP
section | SECTION 5 – FINAL INSPECTION AND HANDOVER
checkpoint | 5.1 - Pump 2 rotation direction
label | Inspection Point: Quality Control Activity - Pump rotation direction as per manufacturers technical information
label | Acceptance Criteria - Pump rotation direction is correct and matched the technical information
label | Verifying Document - This ITP
label | Frequency - Once
label | Inspection Type (Visual, other) - Record on ITP
label | Inspection: Key - Inspection
label | Inspection: By - IP
checkpoint | 5.2 - Pump 2 pressure test pass
label | Inspection Point: Quality Control Activity - Record Gauge pressure
label | Acceptance Criteria - Pass - no pressure loss or visible weaping
label | Verifying Document - This ITP & Specified Pressure testing document
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual / Photo
label | Inspection: Key - Inspection
label | Inspection: By - IP
checklist | 561482-ITP-009.3 - Pre Commissioning Testing Pump & Valves - Pump 3 | itp |  |  |  |  | 561482-ITP-009.3 - Pre Commissioning Testing Pump & Valves - Pump 3
section | SECTION 3 – RECEIVING INSPECTIONS
checkpoint | 3.1 - Fill Wet Well
label | Inspection Point: Quality Control Activity - Pressure testing between suction and discharge isolation valves
label | Acceptance Criteria - Completion of 561482- ITP-008
label | Verifying Document - This ITP
label | Frequency - once
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - Inspection
label | Inspection: By - IP
section | SECTION 4 – IN-PROCESS INSPECTIONS
checkpoint | 4.1 - Filling of pipeline
label | Inspection Point: Quality Control Activity - Remove Entrained air
label | Acceptance Criteria - Bleed until water visible
label | Verifying Document - None
label | Frequency - once
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - Inspection
label | Inspection: By - IP
checkpoint | 4.2 - Visual Check over of Pump 3 and motor
label | Inspection Point: Quality Control Activity - Look for any visible leaking
label | Acceptance Criteria - All pipework connections tight All Cable & Terminations secure
label | Verifying Document - This ITP
label | Frequency - once
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - Inspection
label | Inspection: By - IP
checkpoint | 4.3 - Bump Start Pump 3
label | Inspection Point: Quality Control Activity - Check for correct pump rotation direction
label | Acceptance Criteria - Rotation direction is correct
label | Verifying Document - Pump build sheet literature
label | Frequency - once
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - Inspection
label | Inspection: By - IP
checkpoint | 4.4 - Pressure testing between suction and diacharge isolation valves - Pump 3
label | Inspection Point: Quality Control Activity - VSD Energised, water in pump pipelines
label | Acceptance Criteria - No visible leaking as per Item 4.2
label | Verifying Document - requirements and not to exceed pump manufacturers maximum pressure (Pump flanges 16Bar, Seal max pressure
label | Frequency - once
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - Inspection
label | Inspection: By - IP
section | SECTION 5 – FINAL INSPECTION AND HANDOVER
checkpoint | 5.1 - Pump 3 rotation direction
label | Inspection Point: Quality Control Activity - Pump rotation direction as per manufacturers technical information
label | Acceptance Criteria - Pump rotation direction is correct and matched the technical information
label | Verifying Document - This ITP
label | Frequency - Once
label | Inspection Type (Visual, other) - Record on ITP
label | Inspection: Key - Inspection
label | Inspection: By - IP
checkpoint | 5.2 - Pump 3 pressure test pass
label | Inspection Point: Quality Control Activity - Record Gauge pressure
label | Acceptance Criteria - Pass - no pressure loss or visible weaping
label | Verifying Document - This ITP & Specified Pressure testing document
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual / Photo
label | Inspection: Key - Inspection
label | Inspection: By - IP