## res
type | name | values | prefix | postfix | usage count | user addable | template name | Resource Id
checklist | ITP026 - AGL General Works, Testing & Commissioning | itp |  |  |  |  | FH-ZU2-QU-ITP026 - AGL General Works, Testing & Commissioning - Rev 0
section | 1.0 - Preliminary Works
checkpoint | 1.1 - Enabling works
label | Frequency - Prior to Start
label | Acceptance Criteria - The contractor shall provide enabling work details for approval before commencing of any works where existing services to taxiways not part of the works will be affected.
label | Reference Documents - ZULU-BECA-001-SPC-00003
label | Inspection/Test Method - Verify
label | Record of conformity - Letter of Approval
label | AP
label | Responsibility - Project Engineer / ADB Safegate / Principal’s Representative
date | Date Completed:
checkpoint | 1.2 - AGL control system
label | Frequency - Prior to Start
label | Acceptance Criteria - Changes to existing AGL or new AGL being integrated into the existing system must be done so in a manner, which allows continual operation of the existing system.
label | ○ Prepare and submit for review, a detailed implementation plan showing proposed works methodology allowing continual operation of existing systems. This plan must include contingency to revert to a suitable system in the event of faults.
label | Reference Documents - ZULU-BECA-001-SPC-00003 Cl 9.6
label | Inspection/Test Method - Verify
label | Record of conformity - Works Methodology Plan Submission Reference
label | AP
label | Responsibility - Project Engineer / ADB Safegate / Principal’s Representative
date | Date Completed:
section | 2.0 - Testing & Commissioning
checkpoint | 2.1 - Constant current regulators
label | Frequency - Each Lot
label | Acceptance Criteria - Commissioning shall include:
label | — Checking all connections
label | — Input voltage check
label | — Output tapping check
label | — Open circuit trip
label | — Over Current trip
label | — Brilliancy Check
label | — Lamp Outage alarms (if applicable)
label | — Earth Fault Alarms (If applicable)
label | Reference Documents - ZULU-BECA-001-SPC-00003 Cl 4.8
label | Inspection/Test Method - Verify
label | Record of conformity - Commissioning Checklist
label | TP
label | Responsibility - Project Engineer / ADB Safegate
date | Date Completed:
checkpoint | 2.2 - Circuit insulation tests
label | Frequency - Each Lot
label | Acceptance Criteria - The minimum acceptable reading is 1 Giga-Ohm to earth initially upon cable installation and 500 Meg-Ohm to Earth after at completion of the defects liability period
label | ○ Readings shall be taken before and after the following task:
label | a) each new section of cable is laid
label | b) each section of cable is jointed and buried
label | c) the connection of the SITs into the circuit
label | d) prior to connection into supply feeders by others
label | e) before any “return to service”
label | ○ Tests to be performed as per the works procedure.
label | Reference Documents - ZULU-BECA-001-SPC-00003 Cl 9.6
label | Inspection/Test Method - Verify
label | Record of conformity - Test Report
label | TP
label | Responsibility - Project Engineer / ADB Safegate / Principal’s Representative
date | Date Completed:
checkpoint | 2.3 - Photometric performance
label | Frequency - Each Lot
label | Acceptance Criteria - Photometric output performance of all AGL light fittings to be in accordance with the requirements of MOS 139.
label | Reference Documents - ZULU-BECA-001-SPC-00003 Cl 4.4.3
label | Inspection/Test Method - Verify
label | Record of conformity - Test Report
label | TP
label | Responsibility - Project Engineer / ADB Safegate / Principal’s Representative
date | Date Completed:
section | 3.0 - Post Construction Submissions
checkpoint | 3.1 - AGL components list & spare parts
label | Frequency - Prior to Practical Completion
label | Acceptance Criteria - The Contractor shall supply spare equipment as detailed in the cl 11.3 of Zulu Spec Volume 3. A spares Bill of Quantities (BoQ) shall be provided to APAM OPS at the beginning of the project and be handed over to APAM OPS with a signed hand over sheet at the completion of the project.
label | ○ Spare equipment shall be as per the levels stated below at the end of the designated Defects Liability Period.
label | ○ All spares shall be delivered to Building 52 and evidence of quantities and types of spares including handover to APAM OPS shall be included within the Operation and Maintenance Manuals.
label | Reference Documents - ZULU-BECA-001-SPC-00003 Cl 11.3
label | Inspection/Test Method - Verify
label | Record of conformity - Component List Submission Reference
label | IP
label | Responsibility - Project Engineer / ADB Safegate
date | Date Completed:
checkpoint | 3.2 - Training airfield maintenance
label | Frequency - Prior to Practical Completion
label | Acceptance Criteria - Provide training on all equipment installed under the project to the satisfaction of the airfield maintenance team.
label | ○ Such instruction shall be at a time and for a period as necessary to demonstrate the operation and maintenance requirements for all installed equipment and make the APAM/APAM OPS personnel competent in operating and maintaining those systems.
label | ○ Contractor to submit a training plan outlining items to be covered during training.
label | Reference Documents - ZULU-BECA-001-SPC-00003 Cl 9.10
label | Inspection/Test Method - Verify
label | Record of conformity - Operating and Maintenance Manual
label | IP
label | Responsibility - Project Engineer / ADB Safegate
date | Date Completed:
checkpoint | 3.3 - Certificate of electrical safety
label | Frequency - Prior to Practical Completion
label | Acceptance Criteria - Submission of a certificate of electrical safety for all new electrical systems installed in the project
label | Reference Documents - ZULU-BECA-001-SPC-00003 Cl 10.5
label | Inspection/Test Method - Verify
label | Record of conformity - Certificate of Electrical Safety
label | IP
label | Responsibility - Project Engineer / ADB Safegate
date | Date Completed:
checkpoint | 3.4 - Handover documentation
label | Frequency - Prior to Practical Completion
label | Acceptance Criteria - Submission of all quality assurance documentation including as-builts and schedules to the Project Manager.
label | ○ Information provided shall include:
label | — Circuit details including cable route, loading, Quantity per conduit, origin & destination.
label | — Number of series transformers and location of joints.
label | — Equipment and materials used.
label | — Testing and commissioning values for all modified or new equipment.
label | Reference Documents - ZULU-BECA-001-SPC-00003 Cl 11
label | Inspection/Test Method - Verify
label | Record of conformity - Submission Reference
label | HP*
label | Responsibility - Project Engineer
date | Date Completed:
checkpoint | 3.5 - Acceptance Testing
label | Frequency - Prior to Practical Completion
label | Acceptance Criteria - HOLD POINT
label | ○ Submission of the results and records of the commissioning as well as any further commissioning testing shall be undertaken in the presence of Contract Administrator and representatives of APAM
label | Reference Documents - ZULU-BECA-001-SPC-00003 Cl 9.7
label | Inspection/Test Method - Verify
label | Record of conformity - Letter of Compliance
label | ○ Primary Circuit Commissioning Sheet (Testing of Primary Circuits: Existing + New for IR, Continuity)
label | ○ JCOES (Electrical Safety Certificate for compliance with Electrical Safety Act 1998 and Electrical Safety (Installations) Regulations 2009)
label | ○ Light Fitting MOS/NATA Reports (Covers MOS compliance for fitting brilliancy)
label | ○ O&M Manuals for Materials Installed
label | ○ All standard AS/NZS 3000 cable tests on all power supplied cables
label | ○ Additional – AC 139.C-11 V1.0
label | ○ Ground check report to satisfy requirements around ‘flight testing’ etc.
label | HP
label | Responsibility - Project Engineer / ADB Safegate / BECA
date | Date Completed:
holdpoint | AUTHORITY HOLDPOINT
checkpoint | Final Inspection
label | The signature below verifies that this ITP has been completed in accordance with the Fulton Hogan’s Quality system Procedures and verifies lot compliance with specifications.
textbox | Print Name:
textbox | Position:
date | Work Completed On:
date | Date: