## res
type | name | values | prefix | postfix | usage count | user addable | template name | Resource Id
checklist | ITP031 - ALER 3 Onsite Concrete | itp |  |  |  |  | FH-ZU2-QU-ITP031 - ALER 3 Onsite Concrete - Rev 2
section | 1.0 - Preliminaries
checkpoint | 1.1 - The current revision drawings are being used including subcontractors copy.
label | Frequency - Prior to Start
label | Acceptance Criteria - Current revision drawing is being used (including the subcontractors copy). Current revision to be obtained via Aconex or ACC
label | Reference Documents - Drawings and drawing registers
label | Inspection/Test Method - Verify
label | Record of conformity - Up to date drawing sets and this ITP signed
label | HP*
label | Responsibility - FH Engineer
date | Date Completed:
checkpoint | 1.2 - Implementation of all measures and controls
label | Frequency - Prior to Start
label | Acceptance Criteria - All necessary measures and controls being implemented, that is CEMP, TMP, SWMS, & WP
label | Reference Documents - CEMP, TMP, SWMS, & WP
label | Inspection/Test Method - Verify
label | Record of conformity - Site and office Inspection
label | HP*
label | Responsibility - FH Engineer
date | Date Completed:
checkpoint | 1.3 - Excavation Permit
label | Frequency - Prior to Start
label | Acceptance Criteria - Excavation Permit issued by APAM obtained prior to any excavation on site.
label | Reference Documents - APAM Excavation Permit
label | Inspection/Test Method - Verify
label | Record of conformity - Proof of & permit ITP sign
label | HP*
label | Responsibility - FH Engineer
date | Date Completed:
section | 2.0 - Supply of Materials
checkpoint | 2.1 - Reinforcement
label | Frequency - Pre-commencement
label | Acceptance Criteria - HOLD POINT
label | ○ Test Certificates demonstrating compliance of the reinforcement with the requirements of AS 3600
label | Reference Documents - Drawings and Specification
label | Inspection/Test Method - Verify
label | Record of conformity - Aconex Reference
label | HP
label | Responsibility - FH Engineer / Principals Representative
date | Date Completed:
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 2.2 - Concrete Mix Designs
label | Frequency - Each Lot
label | Acceptance Criteria - HOLD POINT
label | ○ Mix design to be submitted to contract administrator for review and acceptance.
label | Reference Documents - Drawings ZULU-BECA-014-DWG-00201, ZULU-BECA-030-DWG-20001
label | Inspection/Test Method - Verify
label | Record of conformity - Aconex Reference
label | HP
label | Responsibility - FH Engineer / Principals Representative
date | Date Completed:
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 2.3 - Review of Curing Regime
label | Frequency - Each Lot
label | Acceptance Criteria - HOLD POINT
label | ○ Concrete curing regime to be reviewed and approved by the contract administrator prior to use
label | Reference Documents - ZULU-BECA-030-DWG-20001
label | Inspection/Test Method - Verify
label | Record of conformity - Aconex Reference
label | HP
label | Responsibility - FH Engineer / Principals Representative
date | Date Completed:
holdpoint | AUTHORITY HOLDPOINT
section | 3.0 - Construction\Erection of Formwork
checkpoint | 3.1 - Setout
label | Frequency - Each Lot
label | Acceptance Criteria - Setout completed and conformance with Beca IFC Drawings.
label | Reference Documents - Drawings
label | Inspection/Test Method - Verify
label | Record of conformity - Survey Report
label | SCP
label | Responsibility - FH Engineer Surveyor
date | Date Completed:
checkpoint | 3.2 - Excavate
label | Frequency - Each Lot
label | Acceptance Criteria - WITNESS POINT
label | ○ Excavation depth shall be as per specified or as shown on Drawings to accommodate structures.
label | ○ Principals representative to be notified for at the completion of excavations for inspection prior to any blinding being poured.
label | Reference Documents - Specifications as per Drawings
label | Inspection/Test Method - Verify
label | Record of conformity - This ITP signed
label | WP
label | Responsibility - FH Engineer
date | Date Completed:
checkpoint | 3.3 - Confirm Ground
label | Frequency - Each lot
label | Acceptance Criteria - HOLD POINT
label | ○ Completion of excavation and inspection of subgrade materials.
label | ○ No soft spots, unsuitable material. Confirm ground bearing pressure
label | ○ Density Testing to be carried put at a minimum of 1 Test for each 100m2 area per layer of compacted excavations for footings & concrete works
label | Reference Documents - Drawing 00201 Note E40
label | Inspection/Test Method - Verify
label | Record of conformity - DCP Test Results
label | HP
label | Responsibility - FH Engineer
date | Date Completed:
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 3.4 - Concrete Sub-Base
label | Frequency - Each Lot
label | Acceptance Criteria - Blinding layer is installed as per drawings
label | Reference Documents - Drawings
label | Inspection/Test Method - Visual Inspec tion
label | Record of conformity - This ITP Signed
label | HP*
label | Responsibility - Site Engineer / Foreman
date | Date Completed:
checkpoint | 3.5 - Formwork
label | Frequency - Each Lot
label | Acceptance Criteria - Formwork / Reverse Shall conform to shapes, lines, levels and dimensions of the concrete shown or indicated on the Drawings.
label | Reference Documents - Specifications as per Drawings
label | Inspection/Test Method - Verify
label | Record of conformity - This ITP Signed
label | IP
label | Responsibility - FH Engineer Surveyor
date | Date Completed:
checkpoint | 3.6 - Penetrations/Cast in items
label | Frequency - Each Lot
label | Acceptance Criteria - Penetrations/cast in items are present in the formwork.
label | Reference Documents - Drawings
label | Inspection/Test Method - Verify
label | Record of conformity - This ITP Signed
label | IP
label | Responsibility - FH Engineer Surveyor
date | Date Completed:
section | 4.0 - Reinforcement
checkpoint | 4.1 - Reinforcement installation
label | Frequency - Prior to concrete pour
label | Acceptance Criteria - Pre-Pour Checklist Completed:
label | ○ Position and spacing check and recorded.
label | ○ Cover checked and recorded.
label | ○ Reinforcing supports checked and recorded.
label | ○ Laps at required length.
label | ○ Penetrations/cast in items
label | Reference Documents - Specifications and drawings
label | Inspection/Test Method - Verify
label | Record of conformity - Pre-pour inspection List CLA31A
label | IP
label | HP*
label | Responsibility - FH Engineer
date | Date Completed:
section | 5.0 - Pre-pour Planning and Inspections and Placement (1st Pour)
checkpoint | 5.1 - Pre-pour Inspection
label | Frequency - Prior to concrete pour
label | Acceptance Criteria - HOLD POINT
label | ○ Superintendent or Engineer to conduct pre-pour inspection prior to concrete pour
label | ○ Principals representative to inspect formwork and steel fixing
label | ○ Provide the Airport Building Controller with 72 hr Notification for mandatory inspection prior to pouring footings.
label | Reference Documents - Specifications and Drawings ALER 3 Building Permit
label | Inspection/Test Method - Verify
label | Record of conformity - Pre-pour inspection List CLA31A
label | HP
label | Responsibility - FH Engineer / Principals Representative
date | Date Completed:
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 5.2 - Pour in-situ
label | Frequency - Each Lot
label | Acceptance Criteria - Concrete shall be placed within 90mins from batching.
label | ○ All concrete supplied for concrete structures shall be subject to project control testing in accordance with AS 1379.
label | Reference Documents - Specifications and drawings
label | Inspection/Test Method - Verify
label | Record of conformity - This ITP signed
label | IP
label | Responsibility - FH Engineer
date | Date Completed:
checkpoint | 5.3 - Concrete Testing – Compressive Tests
label | Frequency - Each Lot
label | Acceptance Criteria - Composite samples to be taken in accordance with AS 1012.1.
label | ○ 2 – 7 Day cylinder and 2 – 28 day cylinders to be taken.
label | ○ Frequency of testing shall be one sample taken either every 50m3 or once per day, whichever yields a higher frequency.
label | Reference Documents - Drawing 00201 Note 51.AS 1012.1, AS 1012.9
label | Inspection/Test Method - Verify
label | Record of conformity - Concrete Testers Sheet/Results
label | TP
label | Responsibility - FH Engineer
date | Date Completed:
checkpoint | 5.4 - Concrete Slump
label | Frequency - Each Truck
label | Acceptance Criteria - Slump test is required for each load per day
label | Reference Documents - Drawing 00201 Note 51.
label | Inspection/Test Method - Verify
label | Record of conformity - Concrete Testers Sheet/Results
label | TP
label | Responsibility - FH Engineer
date | Date Completed:
checkpoint | 5.5 - Finishing & Curing
label | Frequency - Each Lot
label | Acceptance Criteria - Concrete to be vibrated to ensure compaction and air voids removed. Screed finish required on exposed surfaces.
label | ○ Concrete shall be moist cured or coated by an approved curing compound for a period not less than seven days unless approved by the Superintendent.
label | Reference Documents - Specifications and drawings
label | Inspection/Test Method - Verify
label | Record of conformity - This Signed ITP
label | IP
label | Responsibility - FH Engineer
date | Date Completed:
section | 6.0 - Post Pour Details and Inspections
checkpoint | 6.1 - Removal of Formwork
label | Frequency - Each Lot
label | Acceptance Criteria - Forms shall remain and be maintained firmly in place until the concrete has attained the necessary strength to support its own weight.
label | Inspection/Test Method - Verify
label | Record of conformity - This ITP signed
label | IP
label | Responsibility - FH Engineer
date | Date Completed:
checkpoint | 6.2 - Review of Test Results
label | Frequency - Each Lot
label | Acceptance Criteria - Review of 7 day and 28 day test certificates
label | Reference Documents - Drawing 00201 Note 52.
label | Inspection/Test Method - Verify
label | Record of conformity - Aconex Reference
label | HP
label | Responsibility - FH Engineer / Principals Representative
date | Date Completed:
holdpoint | AUTHORITY HOLDPOINT
checkpoint | Final Inspection
label | On behalf of Fulton Hogan it is hereby certified that the Works represented by the items of work listed have been tested in accordance with the Project Quality Plan and conform in all respects with the requirements of the Contract.
textbox | Print Name:
textbox | Position:
date | Work Completed On:
date | Date:
checklist | ITP032 - ALER 3 Structure | itp |  |  |  |  | FH-ZU2-QU-ITP032 - ALER 3 Structure - Rev 1
section | 1.0 - Preliminary Activities – Permits, Documentation, Approvals, Survey Documentation
checkpoint | 1.1 - Check for correct documentation
label | Frequency - Prior to commencing activity
label | Acceptance Criteria - Ensure that all employees and subcontractors are:
label | — using the correct and complete set of drawings.
label | — all drawings are the latest revision.
label | Reference Documents - Drawings / Aconex Register
label | Inspection/Test Method - Verify
label | Record of conformity - Drawings and drawing registers
label | HP*
label | Responsibility - Project Engineer
date | Date Completed:
checkpoint | 1.2 - Implementation of all measures and controls
label | Frequency - Prior to commencing activity
label | Acceptance Criteria - All necessary measures and controls being implemented, that is PSP, EMP, TMP, SWMS & WP.
label | Reference Documents - PSP, EMP, TMP, JSEA, SWMS, WP
label | Inspection/Test Method - Visual inspection
label | Record of conformity - This ITP signed
label | HP*
label | Responsibility - Project Engineer
date | Date Completed:
checkpoint | 1.3 - Survey Checks
label | Frequency - Prior to commencing activity
label | Acceptance Criteria - Check survey to be completed of all footing positions prior to placing any of the panels.
label | Reference Documents - Drawings
label | Inspection/Test Method - Verify
label | Record of conformity - This ITP signed Survey Report
label | HP*
label | Responsibility - Project Engineer / Surveyor
date | Date Completed:
checkpoint | 1.4 - Submission & approval of precast shop drawings
label | Frequency - Prior to commencing activity
label | Acceptance Criteria - HOLD POINT
label | ○ Submit precast wall panel shop drawings to the principal’s representative for approval prior to fabrication commencement.
label | Reference Documents - ZULU-BECA-001-SPC-00005 0321 cl 1.16, Drawing 20003 note PC7
label | Inspection/Test Method - Verify
label | Record of conformity - Aconex Reference
label | HP
label | Responsibility - Project Engineer / Principals Representative
date | Date Completed:
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 1.5 - Submission & approval of structural steel shop drawings
label | Frequency - Prior to commencing activity
label | Acceptance Criteria - HOLD POINT
label | ○ Submit structural steel shop drawings to the principal’s representative for approval prior to fabrication commencement.
label | Reference Documents - Drawings 20002, 20020, 20113, 20221
label | Inspection/Test Method - Verify
label | Record of conformity - Aconex Reference
label | HP
label | Responsibility - Project Engineer / Principals Representative
date | Date Completed:
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 1.6 - Material Submissions
label | Frequency - Prior to commencing activity
label | Acceptance Criteria - HOLD POINT
label | ○ Items to include but not limited to:
label | — Concrete Mix Design
label | — Element Casting Checklist
label | — Steel Reinforcement
label | — Precast Sample
label | — Bolts
label | — Ferrules
label | — Grout
label | — Incompressible filler
label | Reference Documents - ZULU-BECA-001-SPC-00005 cl 1.16, Structural Drawing Set 030-20 AS/NZS 1252.2
label | Inspection/Test Method - Verify
label | Record of conformity - Aconex Reference
label | HP
label | Responsibility - Project Engineer / Principals Representative
date | Date Completed:
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 1.7 - Welding Certification
label | Frequency - Prior to commencing activity
label | Acceptance Criteria - Submission & approval of the following:
label | — Welding Procedure Qualification
label | — Welding Procedure Specification
label | — Welder Qualification
label | — Approved Consumables
label | Reference Documents - AS1554.1
label | Inspection/Test Method - Verify
label | Record of conformity - This ITP Signed, Qualification Documents
label | HP*
label | Responsibility - Project Engineer
date | Date Completed:
checkpoint | 1.8 - Temporary Works – Pre- Cast Concrete Panels
label | Frequency - Prior to commencing activity
label | Acceptance Criteria - Submission and approval of the following documentation by the FH Temp Works Coordinator (not limited to):
label | — Certification of Lifting Points
label | — Propping plan
label | — Erection sequence
label | — Lift Plan
label | — Certification of Ground Platform for lift
label | — Lifting inserts
label | Reference Documents - Structural Drawing Set 030-20
label | Inspection/Test Method - Verify
label | Record of conformity - Certification of lifting points, propping plan, erection sequence, lift study, Geo Report
label | HP*
label | Responsibility - Project Engineer
date | Date Completed:
checkpoint | 1.9 - Temporary Works – Structural Steel Roof
label | Frequency - Prior to commencing activity
label | Acceptance Criteria - Submission and approval of the following documentation by the FH Temp Works Coordinator (not limited to):
label | — Certification of Lifting Points
label | — Installation sequence
label | — Lift Plan
label | — Lifting Point calculation
label | — Certification of Ground Platform for lift
label | Reference Documents - Structural Drawing Set 030-20
label | Inspection/Test Method - Verify
label | Record of conformity - Certification of lifting points, erection sequence, lift study, Geo Report
label | HP*
label | Responsibility - Project Engineer
date | Date Completed:
section | 2.0 - Construction - Precast Concrete Panel
checkpoint | 2.1 - Fabrication Inspections
label | Frequency - Each Lot
label | Acceptance Criteria - Inspection of the following prior to casting:
label | — Formwork dimensions & stability
label | — Edge details and penetrations
label | — Connection materials and inserts in place
label | — Reinforcement
label | — Concreting
label | ○ Inspection of the following after casting
label | — First precast element of each type at the earliest possible time before and immediately after stripping
label | — Stripping & storage
label | Reference Documents - ZULU-BECA-001-SPC-00005 0321 Shop Drawings
label | Inspection/Test Method - Verify
label | Record of conformity - This ITP Signed, Element Casting Checklist
label | WP
label | Responsibility - Project Engineer / Principals Representative
date | Date Completed:
checkpoint | 2.2 - Delivery of Precast Panels
label | Frequency - Each Lot
label | Acceptance Criteria - Complete inspection of precast panels whilst still loaded on the truck prior to accepting the delivery on site.
label | ○ Identify any damage/defects prior to unloading of the material and correct panel being delivered as per the sequence.
label | ○ Precast element identification is available on each panel
label | Reference Documents - FH Quality Process
label | Inspection/Test Method - Visual Inspection
label | Record of conformity - This ITP Signed, Materials Inspection Checklist on Conqa
label | IP
label | Responsibility - Project Engineer / Site Engineer
date | Date Completed:
checkpoint | 2.3 - Erection Preparation
label | Frequency - Each Lot
label | Acceptance Criteria - Complete Pre-Lift/s Commencement Checklist
label | ○ Ensure erection drawings & propping plans available to the crew
label | Reference Documents - ZULU-BECA-001-SPC-00005 0321, AS 3850 cl 4.4.2
label | Inspection/Test Method - Visual Inspection
label | Record of conformity - Pre-Lift/s Commencement Checklist, This ITP Signed
label | IP, SCP
label | Responsibility - Site Engineer / Foreman / Surveyor
date | Date Completed:
checkpoint | 2.4 - Panel Placement
label | Frequency - Each Lot
label | Acceptance Criteria - Levelling shims have been set correctly and gap between the footing & precast panel is not greater than 40mm
label | ○ Survey to confirm panel placement as per the design
label | Reference Documents - ZULU-BECA-001-SPC-00005 0321 Drawings
label | Inspection/Test Method - Verify
label | Record of conformity - This ITP Signed
label | IP / SCP
label | Responsibility - Site Engineer / Surveyor
date | Date Completed:
checkpoint | 2.5 - Propping & supports
label | Frequency - Each Lot
label | Acceptance Criteria - Witness Point
label | ○ Propping plan is available for each precast panel
label | ○ Ensure propping is installed as per engineer’s design and/or conforms to AS 3850.2 Sections 5
label | ○ Inspection Notice provided for installed temporary bracing
label | Reference Documents - ZULU-BECA-001-SPC-00005 0321, AS 3850.2 Section 5
label | Inspection/Test Method - Visual Inspection
label | Record of conformity - This ITP Signed, Building Engineering ITP
label | WP
label | Responsibility - Site Engineer / Foreman / Principals Representative
date | Date Completed:
checkpoint | 2.6 - Fixing & Welding on Precast Elements
label | Frequency - Each Lot
label | Acceptance Criteria - Install all fixings as per the drawings & engineers plan
label | ○ All welding shall be carried out in accordance with AS 1554.1 unless noted otherwise, all welds shall be 6 continuous fillet category SP using E49XX electrodes - butt welds shall be complete penetration butt welds, category SP.
label | Reference Documents - AS 1554.1 Drawing 20002
label | Inspection/Test Method - Verify
label | Record of conformity - This ITP Signed Welding Certificate
label | HP*
label | Responsibility - Site Engineer / Foreman
date | Date Completed:
checkpoint | 2.7 - Testing of Welding on Precast Elements (if required)
label | Frequency - Each Lot
label | Acceptance Criteria - A competent inspector shall inspect welding works as per the below table or as otherwise stated by the engineer:
label | – – – – – – – – –
label | WELD TYPE ¦¦ % OF WELDS TESTED ¦¦ TESTING PROCEDURE
label | – – – – – – – – –
label | ALL GP/SP ¦¦ 100% ¦¦ VISUALLY SCANNED
label | SP ¦¦ 20% ¦¦ VISUALLY EXAMINED
label | SP BUTT ¦¦ 5% ¦¦ ULTRASONICALLY OR RADIOGRAPHICALLY
label | – – – – – – – – –
label | Reference Documents - Drawing 20002 Note S8
label | Inspection/Test Method - Verify
label | Record of conformity - This Signed ITP, Welding Test Certificate
label | HP*
label | Responsibility - Project Engineer / Site Engineer
date | Date Completed:
checkpoint | 2.8 - Grouting
label | Frequency - Each Lot
label | Acceptance Criteria - Grout to be used shall be non-shrink and have a 28 day characteristic strength of 40 MPA. Details of the proposed grout used to be submitted to the engineer for approval.
label | ○ Note: sealing of the panel vertical joints will be by the precast contractor.
label | Reference Documents - Drawing 20003 Note PC35
label | Inspection/Test Method - Verify
label | Record of conformity - This ITP Signed, Building Engineering ITP
label | IP
label | Responsibility - Site Engineer / Foreman
date | Date Completed:
checkpoint | 2.9 - Removal of Props and Inspection of Completed Precast Walls
label | Frequency - Each Lot
label | Acceptance Criteria - HOLD POINT
label | ○ Inspection Notice provided of the final structure before removal of temporary bracing
label | ○ All propping must remain in position until all structural elements (roof beams, bracing, struts and purlins) affecting stability are fully erected and braced, securely fixed to the panels and the panels have become an integral part of the structure. During construction the builder must ensure no panel props are disconnected by contractors other than the panel contractor.
label | ○ No propping is to be removed without the written consent of the engineer
label | Reference Documents - Approved Shop Drawings Drawing 20003
label | Inspection/Test Method - Visual Inspection
label | Record of conformity - This ITP Signed, Engineers Written Approval, Building Engineering ITP
label | HP*
label | Responsibility - Project Engineer / Principal’s Representative
date | Date Completed:
section | 3.0 - Construction - Structural Steel Roof
checkpoint | 3.1 - Delivery of Steel Sections
label | Frequency - Each Lot
label | Acceptance Criteria - Complete a materials inspection upon arrival of steel sections.
label | ○ Ensure correct components and sections have been sent
label | Reference Documents - FH Quality Process
label | Inspection/Test Method - Visual Inspection
label | Record of conformity - This ITP Signed, Building Engineering ITP, Materials Inspection Checklist on Conqa
label | HP*
label | Responsibility - Project Engineer / Site Engineer
date | Date Completed:
checkpoint | 3.2 - Erection Preparation
label | Frequency - Each Lot
label | Acceptance Criteria - Complete Pre-Lift/s Commencement Checklist
label | ○ Lift sequence/arrangement of steel members available
label | ○ Adequate fall protection in place eg guard rails, safety mesh
label | Reference Documents - Drawing 20002
label | Inspection/Test Method - Verify
label | Record of conformity - This ITP Signed, Building Engineering ITP
label | HP*
label | Responsibility - Project Engineer / Site Engineer
date | Date Completed:
checkpoint | 3.3 - Erection of Steel Members
label | Frequency - Each Lot
label | Acceptance Criteria - Steel Members erected as per design layout and Steel Framing Schedule
label | Reference Documents - Erection Sequence Approved Shop Drawings, Structural Drawing Set 030-20
label | Inspection/Test Method - Visual Inspection
label | Record of conformity - This ITP Signed, Building Engineering ITP
label | IP
label | Responsibility - Site Engineer / Foreman
date | Date Completed:
checkpoint | 3.4 - Bolt installation
label | Frequency - Each Lot
label | Acceptance Criteria - Unless otherwise noted, all bolts shall be M20 Grade 8.8/S, all H/D bolts shall be grade 4.6/S.
label | ○ No connection shall have less than 2 bolts
label | ○ Bolts to be installed as per manufacturer/engineer specification
label | Reference Documents - Drawing 20002 Note S6
label | Inspection/Test Method - Visual inspection
label | Record of conformity - This ITP Signed
label | IP
label | Responsibility - Site Engineer / Foreman
date | Date Completed:
checkpoint | 3.5 - Welding on Steel Framing
label | Frequency - Each Lot
label | Acceptance Criteria - All welding shall be carried out in accordance with AS 1554.1 unless noted otherwise, all welds shall be 6 continuous fillet category SP using E49XX electrodes - butt welds shall be complete penetration butt welds, category SP.
label | Reference Documents - AS 1554.1 Drawing 20002
label | Inspection/Test Method - Verify
label | Record of conformity - This ITP Signed Welding Certificate
label | HP* IP
label | Responsibility - Project Engineer / Site Engineer
date | Date Completed:
checkpoint | 3.6 - Testing of Welding on Steel Framing
label | Frequency - Each Lot
label | Acceptance Criteria - A competent inspector shall inspect welding works as per the below table:
label | – – – – – – – – –
label | WELD TYPE ¦¦ % OF WELDS TESTED ¦¦ TESTING PROCEDURE
label | – – – – – – – – –
label | ALL GP/SP ¦¦ 100% ¦¦ VISUALLY SCANNED
label | SP ¦¦ 20% ¦¦ VISUALLY EXAMINED
label | SP BUTT ¦¦ 5% ¦¦ ULTRASONICALLY OR RADIOGRAPHICALLY
label | – – – – – – – – –
label | Reference Documents - Drawing 20002 Note
label | Inspection/Test Method - Verify
label | Record of conformity - This Signed ITP, Welding Test Certificate
label | HP*
label | Responsibility - Project Engineer / Site Engineer
date | Date Completed:
checkpoint | 3.7 - Inspection of Completed Steel Framing
label | Frequency - Each Lot
label | Acceptance Criteria - WITNESS POINT
label | ○ Provide notice for an inspection of the Steel Framing erected on site before installation of roofing sheets/lining.
label | Reference Documents - ZULU-BECA-001-SPC-00005 0342 cl 1.17
label | Inspection/Test Method - Visual Inspection
label | Record of conformity - This ITP Signed, Building Engineering Structural Steel ITP
label | WP
label | Responsibility - Project Engineer / Principal’s Representative
date | Date Completed:
section | 4.0
checkpoint | 4.1 - Airport Building Controller Sign Off
label | Frequency - At the completion of works
label | Acceptance Criteria - HOLD POINT
label | ○ Give 72 Hr Notification to the Airport Building Controller for Mandatory Inspection of completed precast & steel framework.
label | Reference Documents - ALER 3 Building Permit
label | Inspection/Test Method - Verify
label | Record of conformity - This ITP Signed Inspection Certificate
label | HP
label | Responsibility - Project Engineer / Principal’s Representative
date | Date Completed:
holdpoint | AUTHORITY HOLDPOINT
checkpoint | Final Inspection
label | The signature below verifies that this ITP has been completed in accordance with the Fulton Hogan’s Quality system Procedures and verifies lot compliance with specifications.
textbox | Print Name:
textbox | Position:
date | Work Completed On:
date | Date: