## Sheet1
561482-ITP-001 - Switchboard Delivery and Electrical Installation | [16 empty] | 3.1 - Fill Wet Well
3.1 | Inspection of Switchboard Cabinet Pieces prior to delivery to site | Check overall condition. check connections for internal electrical components | Visual check and report any defects or areas of concern | Email or NTE to report | Once | Visual + Photograph | C | IP/B | [8 empty] | Inspection Point: Quality Control Activity - Pressure testing between suction and discharge isolation valves
3.2 | Delivery of Switchboard materials to site | Check and verify that the switchboard materials have been delivered damage free | materials are damage free | Material Delivery Docket | Once | Visual + inspection | C | IP | [8 empty] | Acceptance Criteria - Completion of 561482- ITP-008
4.1 | On-site assembly | Pre-Removal of required covers from Switchboard | isolation of switchboard is proven | on site testing, isolation tags in place | once | Visual | I | IP | [8 empty] | Verifying Document - This ITP
4.2 | On-site assembly | Switchboard exterior panels removed as required | work area secured, all voltage sources isolated. no signs of degradation on switchboard. | Testing, photos as required | once | Visual + Photograph | I | IP | [8 empty] | Frequency - once
4.3 | Connection of new Generator Change-over cabinet. | connections of electrical cabling/bus bars. | Cabling/busbars connected correctly, insulation resistance between conductors acceptable. | Switchboard Acceptance Test. C.O.C from Switchboard Manufacturers. | Once | Visual + Photograph | I | IP | [8 empty] | Inspection Type (Visual, other) - Visual
4.4 | Re-Energizing of switchboard | Switchboard work completed. | Switchboard upgrades completed. testing completed, interlocks between main switch and generator switch tested and verified, phase rotation confirmed | Switchboard C.O.C, instrument test of supply mains. | once | Visual + Inspection | I | IP | [8 empty] | Inspection: Key - Inspection
4.5 | Submission/review/appr oval of the Level 2 FD | Software functionality meets expectations | Approval from consultant | NTC | Once | Visual | I | IP | [8 empty] | Inspection: By - IP
5.1 | Switchboard | Assembled, inspection carried out and approved | Electrical Testing completed, all covers in place and secured. all bolts present. R.O.I issued by electrical inspector. | Switchboard acceptance test sheet. | once | Visual + Document | I | IP | [8 empty] | 4.1 - Filling of pipeline
Inspection Point: Quality Control Activity - Remove Entrained air
561482-ITP-002.2 - VSD2 Delivery and Installation | [16 empty] | Acceptance Criteria - Bleed until water visible
3.1 | Inspection of VSD prior to delivery to site | Check overall condition of packaging, noting any obvious signs of damage, Check rating of drives is correct. | Visual check and report any defects or areas of concern |  | Once | Visual + Photograph | C | IP/B | [8 empty] | Verifying Document - None
3.2 | Delivery of VSD to Site | Check and verify that correct VSD are delivered and that drives are undamaged | VSD are damage free | VSD Delivery documents | Once | Visual | C | IP | [8 empty] | Frequency - once
4.1 | On-site assembly of mounting Frame | materials for frame delivered to site | Correct materials on site, protective coatings correct. | Delivery Docket for Materials | Once | Visual | I | IP | [8 empty] | Inspection Type (Visual, other) - Visual
4.2 | Assembly and mounting of Frame | Frame Built and bolted to Ground. | Frame built and Securely attached to ground, minimal flex/ movement when force applied. | N/a | Once | Visual + Photograph | I | IP | [8 empty] | Inspection: Key - Inspection
4.3 | Mounting of VSD to Frame | VSD Mounted to frame | VSD Mounted satisfactorily, bolts tight, washers and spring washers present, S/S bolts and fixings used. | VSD Inspection Sheets. | Once | Visual + Photograph | I | IP | [8 empty] | Inspection: By - IP
4.4 | Installation of supply cables to VSD | Cables installed, not terminated into VSDs or switchboard | Correct Cables installed, suitable for full load plus 20 percent of VSD, insulation resistance acceptable | VSD Cable Test Sheets. | Once | Visual + Inspection | I | IP | [8 empty] | 4.2 - Visual Check over of Pump 2 and motor
4.5 | Installation of Output Cables From VSD to Motors | Cables installed, not terminated at motors or VSD | Correct Cables installed, suitable for full load of motor plus 20 percent, insulation resistance acceptable | VSD Cable Test Sheets. | Once | Visual + Inspection | I | IP | [8 empty] | Inspection Point: Quality Control Activity - Look for any visible leaking
4.6 | Termination of cabling to VSD | Cables terminated into VSD | Correct Cables installed, terminals tightened to correct torque, cables prepared correctly. cable earths and screens fit off correctly. | VSD Cable Test Sheets. | Once | Visual + Inspection | I | IP | [8 empty] | Acceptance Criteria - All pipework connections tight All Cable CHAR(AMP) Terminations secure
4.7 | Termination of cabling to Switchboard | Cables fit off at Switchboard. | Correct Cables installed, terminals tightened to correct torque, cables prepared correctly. cable earths and screens fit off correctly. | VSD Cable Test Sheets. | Once | Visual + Inspection | I | IP | [8 empty] | Verifying Document - This ITP
4.8 | Verification of motors electrically | Cables installed, not terminated into motor | Correct motors installed. insulation resistance verified, winding configuration confirmed against nameplate. | VSD Cable Test Sheets. | Once | Visual + Inspection | I | IP | [8 empty] | Frequency - once
4.9 | Termination of cabling to Motor | Cables fit off at Motor | Cables Lugged off correctly, terminals tightened to correct torque | Motor Inspection Sheets | Once | Visual + Photograph | I | IP | [8 empty] | Inspection Type (Visual, other) - Visual
5.1 | VSD | VSD Energised and set up, motor nameplate data entered, protections set, Labels attached | VSD parameters set correctly, inputs set up as per drawings. analog i/o set correctly and verified to plc | VSD ITR Document | Once | Visual + Document | I | IP | [8 empty] | Inspection: Key - Inspection
5.2 | Motors | Assembled and in position, inspection carried out and approved | Motors Tested, rotation direction confirmed, pumps operating as intended. | Motor inspection Sheet | Once | Visual + Document | I | IP | [8 empty] | Inspection: By - IP
4.3 - Bump Start Pump 2
561482-ITP-002.3 - VSD Delivery and Installation | [16 empty] | Inspection Point: Quality Control Activity - Check for correct pump rotation direction
3.1 | Inspection of VSD prior to delivery to site | Check overall condition of packaging, noting any obvious signs of damage, Check rating of drives is correct. | Visual check and report any defects or areas of concern | Once |  | Visual + Photograph | C | IP/B | [8 empty] | Acceptance Criteria - Rotation direction is correct
3.2 | Delivery of VSD to Site | Check and verify that correct VSD are delivered and that drives are undamaged | VSD are damage free | VSD Delivery documents | Once | Visual | C | IP | [8 empty] | Verifying Document - Pump build sheet literature
4.1 | On-site assembly of mounting Frame | materials for frame delivered to site | Correct materials on site, protective coatings correct. | Delivery Docket for Materials | Once | Visual | I | IP | [8 empty] | Frequency - once
4.2 | Assembly and mounting of Frame | Frame Built and bolted to Ground. | Frame built and Securely attached to ground, minimal flex/ movement when force applied. | N/a | Once | Visual + Photograph | I | IP | [8 empty] | Inspection Type (Visual, other) - Visual
4.3 | Mounting of VSD to Frame | VSDs Mounted to frame | VSD Mounted satisfactorily, bolts tight, washers and spring washers present, S/S bolts and fixings used. | VSD Inspection Sheets. | Once | Visual + Photograph | I | IP | [8 empty] | Inspection: Key - Inspection
4.4 | Installation of supply cables to VSD | Cables installed, not terminated into VSD or switchboard | Correct Cables installed, suitable for full load plus 20 percent of VSD, insulation resistance acceptable | VSD Cable Test Sheets. | Once | Visual + Inspection | I | IP | [8 empty] | Inspection: By - IP
4.5 | Installation of Output Cables From VSD to Motors | Cables installed, not terminated at motors or VSD | Correct Cables installed, suitable for full load of motor plus 20 percent, insulation resistance acceptable | VSD Cable Test Sheets. | Once | Visual + Inspection | I | IP | [8 empty] | 4.4 - Pressure testing between suction and diacharge isolation valves - Pump 2
4.6 | Termination of cabling to VSD | Cables terminated into VSD | Correct Cables installed, terminals tightened to correct torque, cables prepared correctly. cable earths and screens fit off correctly. | VSD Cable Test Sheets. | Once | Visual + Inspection | I | IP | [8 empty] | Inspection Point: Quality Control Activity - VSD Energised, water in pump pipelines
4.7 | Termination of cabling to Switchboard | Cables fit off at Switchboard. | Correct Cables installed, terminals tightened to correct torque, cables prepared correctly. cable earths and screens fit off correctly. | VSD Cable Test Sheets. | Once | Visual + Inspection | I | IP | [8 empty] | Acceptance Criteria - No visible leaking as per Item 4.2
4.8 | Verification of motors electrically | Cables installed, not terminated into motor | Correct motors installed. insulation resistance verified, winding configuration confirmed against nameplate. | VSD Cable Test Sheets. | Once | Visual + Inspection | I | IP | [8 empty] | Verifying Document - To meet Specification requirements and not to exceed pump manufacturers maximum pressure (Pump flanges 16Bar, Seal max pressure 30Bar)
4.9 | Termination of cabling to Motor | Cables fit off at Motor | Cables Lugged off correctly, terminals tightened to correct torque | Motor Inspection Sheets | Once | Visual + Photograph | I | IP | [8 empty] | Frequency - once
5.1 | VSD | VSD Energised and set up, motor nameplate data entered, protections set, Labels attached | VSD parameters set correctly, inputs set up as per drawings. analog i/o set correctly and verified to plc | Switchboard acceptance test sheet. | Once | Visual + Document | I | IP | [8 empty] | Inspection Type (Visual, other) - Visual
5.2 | Motors | Assembled and in position, inspection carried out and approved | Motors Tested, rotation direction confirmed, pumps operating as intended. | Motor inspection Sheet | Once | Visual + Document | I | IP | [8 empty] | Inspection: Key - Inspection
Inspection: By - IP
561482-ITP-003.1 - Wet Well Wall Penetration 1 preparation | [16 empty] | 5.1 - Pump 2 rotation direction
3.1 | Masonry drill bits 18mm | Verify correct quantity CHAR(AMP) type | Compatable with the drill unit | Manufacturers Technical data CHAR(AMP) Physical fitment | Once | Visual + Photographs | Inspection | IP | [8 empty] | Inspection Point: Quality Control Activity - Pump rotation direction as per manufacturers technical information
3.2 | Reinforcing Bar | Verify correct quantity CHAR(AMP) size/diameter has been delivered to site | Quantities correct. Dimensions correct. | Drawing M0003 | Once | Visual + Photographs | Inspection | IP | [8 empty] | Acceptance Criteria - Pump rotation direction is correct and matched the technicxal information
3.3 | Hilti RE-500 Chemical Anchor | Verify correct product is deivered. Check expiratrion date. | Quantities correct. Within expiration date | HILTI Product Calculator APP. Delivery Docket | Once | Visual + Photographs | Inspection | IP | [8 empty] | Verifying Document - This ITP
3.4 | Grout (Sika MonoTop 438R) | Verify correct product is deivered. Check expiratrion date. | Quantities correct. Within expiration date | Delivery Docket | Once | Written/Submission | Inspection | IP | [8 empty] | Frequency - Once
4.1 | Mark out penetration on both sides (wet CHAR(AMP) dry sides) using existing pipe as reference | Check and verify dimensains against drawings | Approval from Engineer | Drawing M0003 | once | Document + Visual + Photograph + Engineer site Inspection | V | CR | [8 empty] | Inspection Type (Visual, other) - Record on ITP
4.2 | Proceed with breakout. Hammer drill | Monitor work and progress report any issues | Approval to proceed from item 4.1 | As per drawings listed dimensions CHAR(AMP) measurements | once | Visual CHAR(AMP) Document | I | IP | [8 empty] | Inspection: Key - Inspection
4.3 | Pre-pour inspection | Engineer Inspection | Dimensioin CHAR(AMP) Surface check. As per Drawing M0003 and notes. Approval to proceed via NTC. Correct profile achieved with 5mm roughness and any loose material removed | NTC or other written confirmation | once | Document | H | CR | [8 empty] | Inspection: By - IP
4.4 | Procurement of Reinforcing bar, starters CHAR(AMP) trimmers | Check measurents and vereify correct fitment | As detailed on Drawings CHAR(AMP) specifications | Drawing M0003 | once | Document + Visual | I | IP | [8 empty] | 5.2 - Pump 2 pressure test pass
4.5 | Installation of Reinforcing bar, starters CHAR(AMP) trimmers | Drill holes around perimeter to receive reinforcing bar. Check for correct diameter CHAR(AMP) corret embedment | As detailed on Drawings | Drawing M0003 | once | Visual + Photographs | I | IP | [8 empty] | Inspection Point: Quality Control Activity - Record Guage pressure
4.6 | Install pipe spool with puddle flange to be cast within wall | Check that orientation is correct and is in alignment with pump assembly | As detailed on Drawings M0003 and drawing notes | Drawing M0001 Drawing M0002 Drawing M0003 Drawing M0004 | once | Visual + Photographs | I | IP | [8 empty] | Acceptance Criteria - Pass - no pressure loss or visible weaping
4.7 | Hilti RE500. Chemical Anchor reinforcing bar, starters CHAR(AMP) trimmers into position | Observe Manufacturers instructions. Monitor curing times and temparatures. Use manufacturers calculator to determine product volumes. Sequence the installion to avoid obstruction | As detailed on Drawings and completion of item 4.6 | Drawing M0003 | once | Visual + Photographs | I | IP | [8 empty] | Verifying Document - This ITP CHAR(AMP) Specified Pressure testing document
4.8 | Chemically treat perimeter using product HYDROTITE CJ1020 | Observe Manufacturers instructiuons CHAR(AMP) Health and safety requirements | As detailed on Drawings and completion of item 4.7 | Drawing M0003 | once | Visual + Photographs | H | IP | [8 empty] | Frequency - Once
5.1 | Final dimensional check | At completion of all items on this ITP | Dimensions match the measurements shown on drawings | Drawing M0003 | once | Visual + Photograph + Mark-up drawing | H | CR | [8 empty] | Inspection Type (Visual, other) - Visual / Photo
Inspection: Key - Inspection
561482-ITP-003.2 - Wet Well Wall Penetration 2 preparation | [16 empty] | Inspection: By - IP
3.1 | Masonry drill bits 18mm | Verify correct quantity CHAR(AMP) type | Compatable with the drill unit | Manufacturers Technical data CHAR(AMP) Physical fitment | Once | Visual + Photographs | Inspection | IP | [8 empty] | 3.1 - Fill Wet Well
3.2 | Reinforcing Bar | Verify correct quantity CHAR(AMP) size/diameter has been delivered to site | Quantities correct. Dimensions correct. | Drawing M0003 | Once | Visual + Photographs | Inspection | IP | [8 empty] | Inspection Point: Quality Control Activity - Pressure testing between suction and discharge isolation valves
3.3 | Hilti RE-500 Chemical Anchor | Verify correct product is deivered. Check expiratrion date. | Quantities correct. Within expiration date | HILTI Product Calculator APP. Delivery Docket | Once | Visual + Photographs | Inspection | IP | [8 empty] | Acceptance Criteria - Completion of 561482- ITP-008
3.4 | Grout (Sika MonoTop 438R) | Verify correct product is deivered. Check expiratrion date. | Quantities correct. Within expiration date | Delivery Docket | Once | Written/Submission | Inspection | IP | [8 empty] | Verifying Document - This ITP
4.1 | Mark out penetration on both sides (wet CHAR(AMP) dry sides) using existing pipe as reference | Check and verify dimensains against drawings | Approval from Engineer | Drawing M0003 | once | Document + Visual + Photograph + Engineer site Inspection | V | CR | [8 empty] | Frequency - once
4.2 | Proceed with breakout. Hammer drill | Monitor work and progress report any issues | Approval to proceed from item 4.1 | As per drawings listed dimensions CHAR(AMP) measurements | once | Visual CHAR(AMP) Document | I | IP | [8 empty] | Inspection Type (Visual, other) - Visual
4.3 | Pre pour inspection | Engineer Inspection | Dimensioin CHAR(AMP) Surface sheck. As per Drawing M0003 and notes. Approval to proceed via NTC. Correct profile achieved with 5mm roughness and any loose material removed | NTC or other written confirmation | once | Document | H | CR | [8 empty] | Inspection: Key - Inspection
4.4 | Procurement of Reinforcing bar, starters CHAR(AMP) trimmers | Check measurents and vereify correct fitment | As detailed on Drawings CHAR(AMP) specifications | Drawing M0003 | once | Document + Visual | I | IP | [8 empty] | Inspection: By - IP
4.5 | Installation of Reinforcing bar, starters CHAR(AMP) trimmers | Drill holes around perimeter to receive reinforcing bar. Check for correct diameter CHAR(AMP) corret embedment | As detailed on Drawings | Drawing M0003 | once | Visual + Photographs | I | IP | [8 empty] | 4.1 - Filling of pipeline
4.6 | Install pipe spool with puddle flange to be cast within wall | Check that orientation is correct and is in alignment with pump assembly | As detailed on Drawings M0003 and drawing notes | Drawing M0001 Drawing M0002 Drawing M0003 Drawing M0004 | once | Visual + Photographs | I | IP | [8 empty] | Inspection Point: Quality Control Activity - Remove Entrained air
4.7 | Hilti RE500. Chemical Anchor reinforcing bar, starters CHAR(AMP) trimmers into position | Observe Manufacturers instructions. Monitor curing times and temparatures. Use manufacturers calculator to determine product volumes. Sequence the installion to avoid obstruction | As detailed on Drawings and completion of item 4.6 | Drawing M0003 | once | Visual + Photographs | I | IP | [8 empty] | Acceptance Criteria - Bleed until water visible
4.8 | Chemically treat perimeter using product HYDROTITE CJ1020 | Observe Manufacturers instructiuons CHAR(AMP) Health and safety requirements | As detailed on Drawings and completion of item 4.7 | Drawing M0003 | once | Visual + Photographs | H | IP | [8 empty] | Verifying Document - None
5.1 | Final dimensional check | At completion of all items on this ITP | Dimensions match the measurements shown on drawings | Drawing M0003 | once | Visual + Photograph + Mark-up drawing | H | CR | [8 empty] | Frequency - once
Inspection Type (Visual, other) - Visual
561482-ITP-003.3 - Wet Well Wall Penetration 3 preparation | [16 empty] | Inspection: Key - Inspection
3.1 | Masonry drill bits 18mm | Verify correct quantity CHAR(AMP) type | Compatable with the drill unit | Manufacturers Technical data CHAR(AMP) Physical fitment | Once | Visual + Photographs | Inspection | IP | [8 empty] | Inspection: By - IP
3.2 | Reinforcing Bar | Verify correct quantity CHAR(AMP) size/diameter has been delivered to site | Quantities correct. Dimensions correct. | Drawing M0003 | Once | Visual + Photographs | Inspection | IP | [8 empty] | 4.2 - Visual Check over of Pump 3 and motor
3.3 | Hilti RE-500 Chemical Anchor | Verify correct product is deivered. Check expiratrion date. | Quantities correct. Within expiration date | HILTI Product Calculator APP. Delivery Docket | Once | Visual + Photographs | Inspection | IP | [8 empty] | Inspection Point: Quality Control Activity - Look for any visible leaking
3.4 | Grout (Sika MonoTop 438R) | Verify correct product is deivered. Check expiratrion date. | Quantities correct. Within expiration date | Delivery Docket | Once | Written/Submission | Inspection | IP | [8 empty] | Acceptance Criteria - All pipework connections tight All Cable CHAR(AMP) Terminations secure
4.1 | Mark out penetration on both sides (wet CHAR(AMP) dry sides) using existing pipe as reference | Check and verify dimensains against drawings | Approval from Engineer | Drawing M0003 | once | Document + Visual + Photograph + Engineer site Inspection | V | CR | [8 empty] | Verifying Document - This ITP
4.2 | Proceed with breakout. Hammer drill | Monitor work and progress report any issues | Approval to proceed from item 4.1 | As per drawings listed dimensions CHAR(AMP) measurements | once | Visual CHAR(AMP) Document | I | IP | [8 empty] | Frequency - once
4.3 | Pre pour inspection | Engineer Inspection | Dimensioin CHAR(AMP) Surface sheck. As per Drawing M0003 and notes. Approval to proceed via NTC. Correct profile achieved with 5mm roughness and any loose material removed | NTC or other written confirmation | once | Document | H | CR | [8 empty] | Inspection Type (Visual, other) - Visual
4.4 | Procurement of Reinforcing bar, starters CHAR(AMP) trimmers | Check measurents and vereify correct fitment | As detailed on Drawings CHAR(AMP) specifications | Drawing M0003 | once | Document + Visual | I | IP | [8 empty] | Inspection: Key - Inspection
4.5 | Installation of Reinforcing bar, starters CHAR(AMP) trimmers | Drill holes around perimeter to receive reinforcing bar. Check for correct diameter CHAR(AMP) corret embedment | As detailed on Drawings | Drawing M0003 | once | Visual + Photographs | I | IP | [8 empty] | Inspection: By - IP
4.6 | Install pipe spool with puddle flange to be cast within wall | Check that orientation is correct and is in alignment with pump assembly | As detailed on Drawings M0003 and drawing notes | Drawing M0001 Drawing M0002 Drawing M0003 Drawing M0004 | once | Visual + Photographs | I | IP | [8 empty] | 4.3 - Bump Start Pump 3
4.7 | Hilti RE500. Chemical Anchor reinforcing bar, starters CHAR(AMP) trimmers into position | Observe Manufacturers instructions. Monitor curing times and temparatures. Use manufacturers calculator to determine product volumes. Sequence the installion to avoid obstruction | As detailed on Drawings and completion of item 4.6 | Drawing M0003 | once | Visual + Photographs | I | IP | [8 empty] | Inspection Point: Quality Control Activity - Check for correct pump rotation direction
4.8 | Chemically treat perimeter using product HYDROTITE CJ1020 | Observe Manufacturers instructiuons CHAR(AMP) Health and safety requirements | As detailed on Drawings and completion of item 4.7 | Drawing M0003 | once | Visual + Photographs | H | IP | [8 empty] | Acceptance Criteria - Rotation direction is correct
5.1 | Final dimensional check | At completion of all items on this ITP | Dimensions match the measurements shown on drawings | Drawing M0003 | once | Visual + Photograph + Mark-up drawing | H | CR | [8 empty] | Verifying Document - Pump build sheet literature
Frequency - once
561482-ITP-004.2 - Base. Pump. Motor Installation - Pumpset 2 | [16 empty] | Inspection Type (Visual, other) - Visual
3.1 | Inspection of Plinths for pump 2 | Check overall condition. Cracks/fissures or breaks or areas of weakness | Visual check and report any defects or areas of concern | Email or NTE to report | once | Visual + Photograph | C | IP/B | [8 empty] | Inspection: Key - Inspection
3.2 | Delivery of Pump 2 to site from Downer storage facility | Check and verify that correct pump is delivered | Pump is damage free | 1. KSB delivery docket. 2. Pump storage ITP | Once | Visual | C | IP | [8 empty] | Inspection: By - IP
3.3 | Delivery of Pump 2 Motor to site from Downer storage facility. | Check and verify that correct motor is delivered | Motor is damage free | 1. KSB delivery docket. 2. Pump storage ITP | Once | Visual | C | IP | [8 empty] | 4.4 - Pressure testing between suction and diacharge isolation valves - Pump 3
3.4 | Delivery of Pump CHAR(AMP) Motor mounting plate Downer storage facility | Check CHAR(AMP) Verify that correct Mounting plate is delivered | Mounting plate is dumensionally correct and is damage free | 1. KSB delivery docket. 2. Pump storage ITP | Once | other | R | CR | [8 empty] | Inspection Point: Quality Control Activity - VSD Energised, water in pump pipelines
4.2 | On-site assembly | Correct Pump to Mounting Plate Assembly. | Ensure all fasteners are tight and toqued to manufacturers specifications | KSB documentation CHAR(AMP) Installation Instructiions | Once/per pumpset | Visual + Written | Inspection | IP | [8 empty] | Acceptance Criteria - No visible leaking as per Item 4.2
4.3 | Pump 2 Installation | Correct Mounting plate position on plinth, correct use of fasteners and torque requirements, in accordance with KSB installation instruction | Position is determined by the fixed pipework. Ensure alignment of flange face is parallel to wet well wall | Drawing M0001 | Once | Visual + Photograph | A/D | IP | [8 empty] | Verifying Document - requirements and not to exceed pump manufacturers maximum pressure (Pump flanges 16Bar, Seal max pressure
4.4 | Pump 2 Motor Installation | Motor/Pump shaft alignment | Motor and shaft aligment as best as possible | KSB documentation CHAR(AMP) Installation Instructiions. Nothing final alignment to be undertaken by a Technician - Ref: 561482-ITP-005.2 | Once | Visual + Photograph | A/D | IP | [8 empty] | Frequency - once
5.1 | Pump 2 CHAR(AMP) Motor assembly complete | Proceed with 561482-ITP005.2 | Pump CHAR(AMP) Motor bolted to mounting plate and mounted to plinth. | This ITP | once | Visual + Document | I | IP | [8 empty] | Inspection Type (Visual, other) - Visual
Inspection: Key - Inspection
561482-ITP-004.3 - Base. Pump. Motor Installation - Pumpset 3 | [16 empty] | Inspection: By - IP
3.1 | Inspection of Plinths for pump 3 | Check overall condition. Cracks/fissures or breaks or areas of weakness | Visual check and report any defects or areas of concern | Email or NTE to report | once | Visual + Photograph | C | IP/B | [8 empty] | 5.1 - Pump 3 rotation direction
3.2 | Delivery of Pump 3 to site from Downer storage facility | Check and verify that correct pump is delivered | Pump is damage free | 1. KSB delivery docket. 2. Pump storage ITP | Once | Visual | C | IP | [8 empty] | Inspection Point: Quality Control Activity - Pump rotation direction as per manufacturers technical information
3.3 | Delivery of Pump 3 Motor to site from Downer storage facility. | Check and verify that correct motor is delivered | Motor is damage free | 1. KSB delivery docket. 2. Pump storage ITP | Once | Visual | C | IP | [8 empty] | Acceptance Criteria - Pump rotation direction is correct and matched the technicxal information
3.4 | Delivery of Pump CHAR(AMP) Motor mounting plate Downer storage facility | Check CHAR(AMP) Verify that correct Mounting plate is delivered | Mounting plate is dumensionally correct and is damage free | 1. KSB delivery docket. 2. Pump storage ITP | Once | other | R | CR | [8 empty] | Verifying Document - This ITP
4.2 | On-site assembly | Correct Pump to Mounting Plate Assembly. | Ensure all fasteners are tight and toqued to manufacturers specifications | KSB documentation CHAR(AMP) Installation Instructiions | Once/per pumpset | Visual + Written | Inspection | IP | [8 empty] | Frequency - Once
4.3 | Pump 3 Installation | Correct Mounting plate position on plinth, correct use of fasteners and torque requirements, in accordance with KSB installation instruction | Position is determined by the fixed pipework. Ensure alignment of flange face is parallel to wet well wall | Drawing M0001 | Once | Visual + Photograph | A/D | IP | [8 empty] | Inspection Type (Visual, other) - Record on ITP
4.4 | Pump 3 Motor Installation | Motor/Pump shaft alignment | Motor and shaft aligment as best as possible | KSB documentation CHAR(AMP) Installation Instructiions. Nothing filal alignment to be undertaken by a Technician - Ref: 561482-ITP-005.3 | Once | Visual + Photograph | A/D | IP | [8 empty] | Inspection: Key - Inspection
5.1 | Pump 3 CHAR(AMP) Motor assembly complete | Proceed with 561482-ITP005.3 | Pump CHAR(AMP) Motor bolted to mounting plate and mounted to plinth. | This ITP | once | Visual + Document | I | IP | [8 empty] | Inspection: By - IP
5.2 - Pump 3 pressure test pass
561482-ITP-007.1 - Wet Well Wall Penetration 1 pour | [16 empty] | Inspection Point: Quality Control Activity - Record Guage pressure
3.1 | Grout - SIKA MonoTop- 438R | Calculate Quantity | Correct volume to be calculated | Product Datasheet | Once | Written | R | CR | [8 empty] | Acceptance Criteria - Pass - no pressure loss or visible weaping
3.2 | Installed Reinforcing | Measure and check | Matches Design Drawings | Drawing M0003 | Once | Visual + Photographs | V | IP | [8 empty] | Verifying Document - This ITP CHAR(AMP) Specified Pressure testing document
3.3 | Spool/Puddle Flange | Measure and check | Pipework is straight and parrallel to structure CHAR(AMP) pump | As per drawing M0001 CHAR(AMP) M0002 | Once | Visual + Photographs | V | IP | [8 empty] | Frequency - Once
4.1 | Boxing of penertation | Measure CHAR(AMP) Check. Ensure perimeter of boxing and pipe penetration is sealed to stop grout spill. | Matches Design Drawings by dinension and configuration | Drawing M0003 | Once | Visual + Inspection HOLD POINT | H | CR | [8 empty] | Inspection Type (Visual, other) - Visual / Photo
4.2 | Mixing of Grout | Ensure product is on hand CHAR(AMP) plenty of clean fresh water is readily available | As per manufacturers instructions/guidelines | Product technical instruction sheets or certificate (if delivered) | once | Document | I | IP | [8 empty] | Inspection: Key - Inspection
4.3 | Casting of wall penetration | Monitor the consistency and quality of the grout fill | As per manufacturers instructions/guidelines | Product technical instructions | once | Dodument + Visual | I | IP | [8 empty] | Inspection: By - IP
4.4 | Vibrate | Vibrate to remove entrained air. Ensure all air is removed | Grout Placer Approval | This ITP | once | Visual + Photographs + Short video | I | IP
4.5 | Monitor curing process | Monitor curing inspectiong the boxing and areas of potential grout leakage. | No evident shrinkage or deformation. Repotr any issues to Engineer | As per drawings allowing 7 days curing time. Boxing can be removed after 72 hours | once | Visual | I | IP
5.1 | Remove boxing | At completion of all items on this ITP | Time period as indicated on programme | This ITP | once | Visual + Photograph | I | IP
561482-ITP-007.2 - Wet Well Wall Penetration 2 pour
3.1 | Grout - SIKA MonoTop- 438R | Calculate Quantity | Correct volume to be calculated | Product Datasheet | Once | Written | R | CR
3.2 | Installed Reinforcing | Measure and check | Matches Design Drawings | Drawing M0003 | Once | Visual + Photographs | V | IP
3.3 | Spool/Puddle Flange | Measure and check | Pipework is straight and parrallel to structure CHAR(AMP) pump | As per drawing M0001 CHAR(AMP) M0002 | Once | Visual + Photographs | V | IP
4.1 | Boxing of penertation | Measure CHAR(AMP) Check. Ensure perimeter of boxing and pipe penetration is sealed to stop grout spill. | Matches Design Drawings by dinension and configuration | Drawing M0003 | Once | Visual + Inspection HOLD POINT | H | CR
4.2 | Mixing of Grout | Ensure product is on hand CHAR(AMP) plenty of clean fresh water is readily available | As per manufacturers instructions/guidelines | Product technical instruction sheets or certificate (if delivered) | once | Document | I | IP
4.3 | Casting of wall penetration | Monitor the consistency and quality of the grout fill | As per manufacturers instructions/guidelines | Product technical instructions | once | Dodument + Visual | I | IP
4.4 | Vibrate | Vibrate to remove entrained air. Ensure all air is removed | Grout Placer Approval | This ITP | once | Visual + Photographs + Short video | I | IP
4.5 | Monitor curing process | Monitor curing inspectiong the boxing and areas of potential grout leakage. | No evident shrinkage or deformation. Repotr any issues to Engineer | As per drawings allowing 7 days curing time. Boxing can be removed after 72 hours | once | Visual | I | IP
5.1 | Remove boxing | At completion of all items on this ITP | Time period as indicated on programme | This ITP | once | Visual + Photograph | I | IP
561482-ITP-007.3 - Wet Well Wall Penetration 3 pour
3.1 | Grout - SIKA MonoTop- 438R | Calculate Quantity | Correct volume to be calculated | Product Datasheet | Once | Written | R | CR
3.2 | Installed Reinforcing | Measure and check | Matches Design Drawings | Drawing M0003 | Once | Visual + Photographs | V | IP
3.3 | Spool/Puddle Flange | Measure and check | Pipework is straight and parrallel to structure CHAR(AMP) pump | As per drawing M0001 CHAR(AMP) M0002 | Once | Visual + Photographs | V | IP
4.1 | Boxing of penertation | Measure CHAR(AMP) Check. Ensure perimeter of boxing and pipe penetration is sealed to stop grout spill. | Matches Design Drawings by dinension and configuration | Drawing M0003 | Once | Visual + Inspection HOLD POINT | H | CR
4.2 | Mixing of Grout | Ensure product is on hand CHAR(AMP) plenty of clean fresh water is readily available | As per manufacturers instructions/guidelines | Product technical instruction sheets or certificate (if delivered) | once | Document | I | IP
4.3 | Casting of wall penetration | Monitor the consistency and quality of the grout fill | As per manufacturers instructions/guidelines | Product technical instructions | once | Dodument + Visual | I | IP
4.4 | Vibrate | Vibrate to remove entrained air. Ensure all air is removed | Grout Placer Approval | This ITP | once | Visual + Photographs + Short video | I | IP
4.5 | Monitor curing process | Monitor curing inspectiong the boxing and areas of potential grout leakage. | No evident shrinkage or deformation. Repotr any issues to Engineer | As per drawings allowing 7 days curing time. Boxing can be removed after 72 hours | once | Visual | I | IP
5.1 | Remove boxing | At completion of all items on this ITP | Time period as indicated on programme | This ITP | once | Visual + Photograph | I | IP
561482-ITP-009.2 - Pre Commissioning Testing Pump CHAR(AMP) Valves - Pump 2
3.1 | Fill Wet Well | Pressure testing between suction and discharge isolation valves | Completion of 561482- ITP-008 | This ITP | once | Visual | Inspection | IP | 3.1 - Fill Wet Well | Inspection Point: Quality Control Activity - Pressure testing between suction and discharge isolation valves | Acceptance Criteria - Completion of 561482- ITP-008 | Verifying Document - This ITP | Frequency - once | Inspection Type (Visual, other) - Visual | Inspection: Key - Inspection | Inspection: By - IP
4.1 | Filling of pipeline | Remove Entrained air | Bleed until water visible | None | once | Visual | Inspection | IP | 4.1 - Filling of pipeline | Inspection Point: Quality Control Activity - Remove Entrained air | Acceptance Criteria - Bleed until water visible | Verifying Document - None | Frequency - once | Inspection Type (Visual, other) - Visual | Inspection: Key - Inspection | Inspection: By - IP
4.2 | Visual Check over of Pump 2 and motor | Look for any visible leaking | All pipework connections tight All Cable CHAR(AMP) Terminations secure | This ITP | once | Visual | Inspection | IP | 4.2 - Visual Check over of Pump 2 and motor | Inspection Point: Quality Control Activity - Look for any visible leaking | Acceptance Criteria - All pipework connections tight All Cable CHAR(AMP) Terminations secure | Verifying Document - This ITP | Frequency - once | Inspection Type (Visual, other) - Visual | Inspection: Key - Inspection | Inspection: By - IP
4.3 | Bump Start Pump 2 | Check for correct pump rotation direction | Rotation direction is correct | Pump build sheet literature | once | Visual | Inspection | IP | 4.3 - Bump Start Pump 2 | Inspection Point: Quality Control Activity - Check for correct pump rotation direction | Acceptance Criteria - Rotation direction is correct | Verifying Document - Pump build sheet literature | Frequency - once | Inspection Type (Visual, other) - Visual | Inspection: Key - Inspection | Inspection: By - IP
4.4 | Pressure testing between suction and diacharge isolation valves - Pump 2 | VSD Energised, water in pump pipelines | No visible leaking as per Item 4.2 | To meet Specification requirements and not to exceed pump manufacturers maximum pressure (Pump flanges 16Bar, Seal max pressure 30Bar) | once | Visual | Inspection | IP | 4.4 - Pressure testing between suction and diacharge isolation valves - Pump 2 | Inspection Point: Quality Control Activity - VSD Energised, water in pump pipelines | Acceptance Criteria - No visible leaking as per Item 4.2 | Verifying Document - To meet Specification requirements and not to exceed pump manufacturers maximum pressure (Pump flanges 16Bar, Seal max pressure 30Bar) | Frequency - once | Inspection Type (Visual, other) - Visual | Inspection: Key - Inspection | Inspection: By - IP
5.1 | Pump 2 rotation direction | Pump rotation direction as per manufacturers technical information | Pump rotation direction is correct and matched the technicxal information | This ITP | Once | Record on ITP | Inspection | IP | 5.1 - Pump 2 rotation direction | Inspection Point: Quality Control Activity - Pump rotation direction as per manufacturers technical information | Acceptance Criteria - Pump rotation direction is correct and matched the technicxal information | Verifying Document - This ITP | Frequency - Once | Inspection Type (Visual, other) - Record on ITP | Inspection: Key - Inspection | Inspection: By - IP
5.2 | Pump 2 pressure test pass | Record Guage pressure | Pass - no pressure loss or visible weaping | This ITP CHAR(AMP) Specified Pressure testing document | Once | Visual / Photo | Inspection | IP | 5.2 - Pump 2 pressure test pass | Inspection Point: Quality Control Activity - Record Guage pressure | Acceptance Criteria - Pass - no pressure loss or visible weaping | Verifying Document - This ITP CHAR(AMP) Specified Pressure testing document | Frequency - Once | Inspection Type (Visual, other) - Visual / Photo | Inspection: Key - Inspection | Inspection: By - IP
561482-ITP-009.3 - Pre Commissioning Testing Pump CHAR(AMP) Valves - Pump 3
3.1 | Fill Wet Well | Pressure testing between suction and discharge isolation valves | Completion of 561482- ITP-008 | This ITP | once | Visual | Inspection | IP | 3.1 - Fill Wet Well | Inspection Point: Quality Control Activity - Pressure testing between suction and discharge isolation valves | Acceptance Criteria - Completion of 561482- ITP-008 | Verifying Document - This ITP | Frequency - once | Inspection Type (Visual, other) - Visual | Inspection: Key - Inspection | Inspection: By - IP
4.1 | Filling of pipeline | Remove Entrained air | Bleed until water visible | None | once | Visual | Inspection | IP | 4.1 - Filling of pipeline | Inspection Point: Quality Control Activity - Remove Entrained air | Acceptance Criteria - Bleed until water visible | Verifying Document - None | Frequency - once | Inspection Type (Visual, other) - Visual | Inspection: Key - Inspection | Inspection: By - IP
4.2 | Visual Check over of Pump 3 and motor | Look for any visible leaking | All pipework connections tight All Cable CHAR(AMP) Terminations secure | This ITP | once | Visual | Inspection | IP | 4.2 - Visual Check over of Pump 3 and motor | Inspection Point: Quality Control Activity - Look for any visible leaking | Acceptance Criteria - All pipework connections tight All Cable CHAR(AMP) Terminations secure | Verifying Document - This ITP | Frequency - once | Inspection Type (Visual, other) - Visual | Inspection: Key - Inspection | Inspection: By - IP
4.3 | Bump Start Pump 3 | Check for correct pump rotation direction | Rotation direction is correct | Pump build sheet literature | once | Visual | Inspection | IP | 4.3 - Bump Start Pump 3 | Inspection Point: Quality Control Activity - Check for correct pump rotation direction | Acceptance Criteria - Rotation direction is correct | Verifying Document - Pump build sheet literature | Frequency - once | Inspection Type (Visual, other) - Visual | Inspection: Key - Inspection | Inspection: By - IP
4.4 | Pressure testing between suction and diacharge isolation valves - Pump 3 | VSD Energised, water in pump pipelines | No visible leaking as per Item 4.2 | requirements and not to exceed pump manufacturers maximum pressure (Pump flanges 16Bar, Seal max pressure | once | Visual | Inspection | IP | 4.4 - Pressure testing between suction and diacharge isolation valves - Pump 3 | Inspection Point: Quality Control Activity - VSD Energised, water in pump pipelines | Acceptance Criteria - No visible leaking as per Item 4.2 | Verifying Document - requirements and not to exceed pump manufacturers maximum pressure (Pump flanges 16Bar, Seal max pressure | Frequency - once | Inspection Type (Visual, other) - Visual | Inspection: Key - Inspection | Inspection: By - IP
5.1 | Pump 3 rotation direction | Pump rotation direction as per manufacturers technical information | Pump rotation direction is correct and matched the technicxal information | This ITP | Once | Record on ITP | Inspection | IP | 5.1 - Pump 3 rotation direction | Inspection Point: Quality Control Activity - Pump rotation direction as per manufacturers technical information | Acceptance Criteria - Pump rotation direction is correct and matched the technicxal information | Verifying Document - This ITP | Frequency - Once | Inspection Type (Visual, other) - Record on ITP | Inspection: Key - Inspection | Inspection: By - IP
5.2 | Pump 3 pressure test pass | Record Guage pressure | Pass - no pressure loss or visible weaping | This ITP CHAR(AMP) Specified Pressure testing document | Once | Visual / Photo | Inspection | IP | 5.2 - Pump 3 pressure test pass | Inspection Point: Quality Control Activity - Record Guage pressure | Acceptance Criteria - Pass - no pressure loss or visible weaping | Verifying Document - This ITP CHAR(AMP) Specified Pressure testing document | Frequency - Once | Inspection Type (Visual, other) - Visual / Photo | Inspection: Key - Inspection | Inspection: By - IP