## res
type | name | values | prefix | postfix | usage count | user addable | template name | Resource Id
checklist | ITP043 - AGL Deep Base Cans | itp |  |  |  |  | FH-ZU2-QU-ITP043 - AGL Deep Base Cans - Rev 0
section | 1.0 - Preliminary Works
checkpoint | 1.1 - Check for correct documentation
label | Frequency - Prior to commencing any activity
label | Acceptance Criteria - Ensure that all employees and subcontractors are using the latest and complete set of drawings
label | Reference Documents - IFC Drawings
label | Inspection/Test Method - Verify
label | Record of conformity - Drawings
label | IP
label | Responsibility - Project Engineer
date | Date Completed:
checkpoint | 1.2 - Implementation of all measures and controls
label | Frequency - Prior to commencing any activities
label | Acceptance Criteria - All necessary measures and controls are being implemented, that is PSP, EMP, TMP, SWMS & WP.
label | Reference Documents - PSP, EMP, TMP, JSEA, SWMS, WP
label | Inspection/Test Method - Verify
label | Record of conformity - Site and office Inspection
label | HP*
label | Responsibility - Project Engineer / Site Supervisor
date | Date Completed:
checkpoint | 1.3 - Material/equipment approvals
label | Frequency - Prior to start
label | Acceptance Criteria - Materials and equipment that shall be used in the construction of the works as nominated on the Drawings.
label | Reference Documents - ZULU-BECA-001-SPC-00003 cl 2.3
label | Inspection/Test Method - Verify
label | Record of conformity - Aconex reference(s)
label | HP*
label | Responsibility - Project Engineer
date | Date Completed:
checkpoint | 1.4 - Setting out for airfield luminaires
label | Frequency - Each Lot
label | Acceptance Criteria - HOLD POINT
label | ○ The Contractor shall survey the proposed light locations in conjunction with the new and existing line-marking to set out the proposed lights. A schedule of the proposed lights shall be produced and submitted to the Contract Administrator.
label | Reference Documents - ZULU-BECA-001-SPC-00003 cl 5.4
label | Inspection/Test Method - Verify
label | Record of conformity - Aconex reference
label | HP
label | Responsibility - Project Engineer / Beca
date | Date Completed:
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 1.5 - Installation of Initial Light Base
label | Frequency - Once
label | Acceptance Criteria - HOLD POINT
label | ○ The initial installation of the light base shall be witnessed by the Contractor Administrator
label | Reference Documents - ZULU-BECA-001-SPC-00003 cl 5.4
label | Inspection/Test Method - Visual, Inspection
label | Record of conformity - This ITP Signed
label | HP
label | Responsibility - Project Engineer / Beca
date | Date Completed:
holdpoint | AUTHORITY HOLDPOINT
section | 2.0 - Installation of Base Canister
checkpoint | 2.1 - Steel Reinforcement Mesh and Reo Cage
label | Frequency - Each Lot
label | Acceptance Criteria - N12-150 steel mesh installed on both direction with 43.5mm cover.
label | ○ N12 reinforcement cage to be installed as per AGL details
label | Reference Documents - ZULU-BECA-024-DWG-07506
label | Inspection/Test Method - Visual Inspection
label | Record of conformity - This ITP signed, Avionics Base Canister Installation ITC
label | IP
label | Responsibility - Project Engineer
date | Date Completed:
checkpoint | 2.2 - Base Canister and Conduit Installation
label | Frequency - Each Lot
label | Acceptance Criteria - Concrete encasement for electrical conduit shall have a minimum cover of 40mm.
label | – Ensure bottom of can is 200mm minimum to the bottom of foundation.
label | – 700mm x 700mm 40MPa concrete foundation
label | – Compressive Strength Test Sample to be conducted per 50 m3 of concrete
label | – Install 19mm plywood cover with mud plate (sealed and bolts torqued to 40NM)
label | – Check the elevation (RL) of the bottom canister (top plate) relative to the FSL of PCC concrete.
label | Reference Documents - ZULU-BECA-024-DWG-07507
label | Inspection/Test Method - Visual Inspection
label | Record of conformity - This ITP signed, Avionics Base Canister Installation ITC, Concrete Test Results
label | IP
label | Responsibility - Project Engineer
date | Date Completed:
section | 3.0 - Installation of Top Canister
checkpoint | 3.1 - Top Canister Installation
label | Frequency - Each Lot
label | Acceptance Criteria - Core pilot hole (150mm) down to target ring and establish exact centre.
label | – Core diameter of approximately 355mm
label | – Install top canister with spacer rings and dam rings
label | Reference Documents - ZULU-BECA-024-DWG
label | Inspection/Test Method - Visual Inspection
label | Record of conformity - This ITP signed, Avionics Top Canister Installation ITC
label | IP
label | Responsibility - Project Engineer
date | Date Completed:
checkpoint | 3.2 - Top Canister Close out
label | Frequency - Each Lot
label | Acceptance Criteria - Install bolts and tightened to manufacturer’s recommended torque using a calibrated torque wrench.
label | – Apply Webertec FG epoxy sealant to the void between housing and side of excavation
label | Reference Documents - ZULU-BECA-024-DWG
label | Inspection/Test Method - Visual Inspection
label | Record of conformity - This ITP signed, Avionics Top Canister Installation ITC
label | IP
label | Responsibility - Project Engineer
date | Date Completed:
checkpoint | 3.4 - Elevated Luminaire Base
label | Frequency - Each Lot
label | Acceptance Criteria - Installed and backfill in accordance with drawings.
label | – Two piece deep base cans to be installed.
label | – Min. 500mm cover from finished surface to top of conduit.
label | – Can fitted with frangible coupling and FAA type/secondary socket retaining arrangement plug and socket.
label | – Foundation and reinforcement installation to match Deep Can Installation for Rigid Pavement
label | Reference Documents - ZULU-BECA-024-DWG-07507
label | Inspection/Test Method - Visual Inspection
label | Record of conformity - This ITP signed, Avionics Base Canister Installation Checklist
label | IP
label | Responsibility - Project Engineer/Site Supervisor
date | Date Completed:
checkpoint | Final Inspection
note | The signature below verifies that this ITP has been completed in accordance with the Fulton Hogan’s Quality system Procedures and verifies lot compliance with specifications.
textbox | Print Name:
textbox | Position:
date | Work Completed On:
date | Date: