## res_ITP_1_Inspection_and_Test_P
type | name | values | prefix | postfix | usage count | user addable | template name
checklist | T3084984 - Wiri RAP Interface Returns - ITP Rev03 | itp |  |  |  |  | T3084984 - Wiri RAP Interface Returns - ITP Rev03
section | T3084984 - Wiri RAP Interface Returns
checkpoint | 1 - Issued For Construction Drawings
label | SPECIFICATION REFERENCE - IFC Drawings Issued by Client/Engineer
label | ACCEPTANCE CRITERIA - Issued For Construction Drawings Available
label | DATE/SIGN - Contractor Rep - H
holdpoint | HOLD POINT
checkpoint | 2 - Underground Services Confirmation
label | SPECIFICATION REFERENCE - CTS Permit to Work
label | ACCEPTANCE CRITERIA - Underground Services Drawings to accompany permit and marked out onsite where excavation is to be undertaken
label | DATE/SIGN - Contractor Rep - P
label | ○ CTS Civil Inspector - R
checkpoint | 3 - Survey & Setout
label | SPECIFICATION REFERENCE - IFC Drawings
label | ○ CTS General Civil Construction Spec
label | ○ CTS Excavation Works Spec
label | ACCEPTANCE CRITERIA - Foundations and embedded items shall be setout following the tolerances, heights and positions shown in each foundations respective drawing.
checkpoint | 4 - Waste Management & Disposal
label | SPECIFICATION REFERENCE - CTS General Civil Construction Spec
label | ○ CTS Excavation Works Spec
label | ○ CTS Contaminated Environmental Ground Soil Managenet Plan RW-231
label | ACCEPTANCE CRITERIA - Waste management plan prepared and followed. Supporting documents available on request.
label | DATE/SIGN - Contractor Rep - P
label | ○ CTS Civil Inspector - R
checkpoint | P1185A - Demolition
label | SPECIFICATION REFERENCE - IFC Drawings
label | ACCEPTANCE CRITERIA - Existing pedestal removed at ground level. Concrete removed to approved landfill.
label | DATE/SIGN - Contractor Rep - P
label | ○ CTS Civil Inspector - R
checkpoint | P1185A - Position of Pump Pedestal Setout
label | SPECIFICATION REFERENCE - IFC Drawings
label | ACCEPTANCE CRITERIA - Setout as per IFC Drawings
label | DATE/SIGN - Contractor Rep - P
label | ○ CTS Civil Inspector - R
checkpoint | P1185A - Pump pedestal location Cleaned & Scabbled
label | SPECIFICATION REFERENCE - IFC Drawings
label | ACCEPTANCE CRITERIA - Foundation area cleaned and free from contamination and dust/oil or grease, surface roughened to accept further concrete pour
label | DATE/SIGN - Contractor Rep - P
label | ○ CTS Civil Inspector - R
checkpoint | P1185A - Cast in Items - Bolts & Nuts
label | SPECIFICATION REFERENCE - IFC Drawings
label | ○ CTS General Civil Construction Specification
label | ○ CTS Epoxy Grouting of Anchor Bolts
label | ○ Manufacturers Documentation
label | ○ Inspection Records
label | ACCEPTANCE CRITERIA - If drilled in, Epoxy Grout Shall be Ramset C8 placed in accordance with manufacturers recommendations to the levels and positions setout in the drawings
label | ○ Drilled holes for Anchors shall be inspected
label | ○ Cast in anchor bolts shall be set to spec in IFC drawings and positioned with template to design measurenments in IFC drawings
label | DATE/SIGN - Contractor Rep - P
label | ○ CTS Civil Inspector - R
checkpoint | P1185A - Formwork, Reinforcing & Concrete
label | SPECIFICATION REFERENCE - IFC Drawings
label | ○ CTS General Civil Construction Specification NZS3109/3112
label | ○ Manufacturers Documentation
label | ○ Inspection Records
label | ACCEPTANCE CRITERIA - All reinforcing bars shall be Micro-Alloy Class E to AS/NZS 4671 as shown in IFC's.
label | ○ All reinforcing bar hooks, laps and bends shall be in accordance with NZS3109 unless otherwise noted.
label | ○ All reinforcing and formwork to comply with IFC drawings
label | ○ Concrete to be min 30MPa at 28 days
label | ○ Testing of concrete per CTS Specifications
label | ○ Prepour Inspection Record Filled out Prior to Concrete
label | DATE/SIGN - Contractor Rep - P
label | ○ CTS Civil Inspector - H
holdpoint | HOLD POINT
checkpoint | P1185A - Grouting of Baseplate
label | SPECIFICATION REFERENCE - IFC Drawings
label | ○ CTS General Civil Construction Specification
label | ○ Manufacturers Documentation
label | ACCEPTANCE CRITERIA - Grouting shall be Sika 212 or Sika 214 placed in accordance with manufacturers recommendations and the IFC drawings
label | DATE/SIGN - Contractor Rep - P
label | ○ CTS Civil Inspector - W
checkpoint | P1185B - Demolition
label | SPECIFICATION REFERENCE - IFC Drawings
label | ACCEPTANCE CRITERIA - Existing pedestal removed at ground level
label | DATE/SIGN - Contractor Rep - P
label | ○ CTS Civil Inspector - R
checkpoint | P1185B - Position of Pump Pedestal Setout
label | SPECIFICATION REFERENCE - IFC Drawings
label | ACCEPTANCE CRITERIA - Setout as per drawings
label | DATE/SIGN - Contractor Rep - P
label | ○ CTS Civil Inspector - R
checkpoint | P1185B - Pump Pedestal Location Cleaned & Scabbled
label | SPECIFICATION REFERENCE - IFC Drawings
label | ACCEPTANCE CRITERIA - Foundation area cleaned and free from contamination and dust/oil or grease, surface roughened to accept further concrete pour
label | DATE/SIGN - Contractor Rep - P
label | ○ CTS Civil Inspector - R
checkpoint | P1185B - Cast in Items - Bolts & Nuts
label | SPECIFICATION REFERENCE - IFC Drawings
label | ○ CTS General Civil Construction Specification
label | ○ CTS Epoxy Grouting of Anchor Bolts
label | ○ Manufacturers Documentation
label | ○ Inspection Records
label | ACCEPTANCE CRITERIA - If drilled in, Epoxy Grout Shall be Ramset C8 placed in accordance with manufacturers recommendations to the levels and positions setout in the drawings
label | ○ Drilled holes for Anchors shall be inspected
label | ○ Cast in anchor bolts shall be set to spec in IFC drawings and positioned with template to design measurenments in IFC drawings
label | DATE/SIGN - Contractor Rep - P
label | ○ CTS Civil Inspector - R
checkpoint | P1185B - Formwork, Reinforcing & Concrete
label | SPECIFICATION REFERENCE - IFC Drawings
label | ○ CTS General Civil Construction Specification NZS3109/3112
label | ○ Manufacturers Documentation
label | ○ Inspection Records
label | ACCEPTANCE CRITERIA - All reinforcing bars shall be Micro-Alloy Class E to AS/NZS 4671 as shown in IFC's.
label | ○ All reinforcing bar hooks, laps and bends shall be in accordance with NZS3109 unless otherwise noted.
label | ○ All reinforcing and formwork to comply with IFC drawings
label | ○ Concrete to be min 30MPa at 28 days
label | ○ Testing of concrete per CTS Specifications
label | ○ Prepour Inspection Record Filled out Prior to Concrete
label | DATE/SIGN - Contractor Rep - P
label | ○ CTS Civil Inspector - H
holdpoint | HOLD POINT
checkpoint | P1185B - Grouting of Baseplate
label | SPECIFICATION REFERENCE - IFC Drawings
label | ○ CTS General Civil Construction Specification
label | ○ Manufacturers Documentation
label | ACCEPTANCE CRITERIA - Grouting shall be Sika 212 or Sika 214 placed in accordance with manufacturers recommendations and the IFC drawings
label | DATE/SIGN - Contractor Rep - P
label | ○ CTS Civil Inspector - W
checkpoint | PSS3259/PSS3263/PSS3264/PSS3282 - Setout of Pipe Sleeper
label | SPECIFICATION REFERENCE - IFC Drawings
label | ACCEPTANCE CRITERIA - Comply with setout in drawings
label | DATE/SIGN - Contractor Rep - P
label | ○ CTS Civil Inspector - R
checkpoint | PSS3259/PSS3263/PSS3264/PSS3282 - Excavation & Foundation Preparation inc Site Concrete
label | SPECIFICATION REFERENCE - IFC Drawings
label | ○ CTS Excavation Works Specification
label | ○ CTS General Civil Construction Specification
label | ACCEPTANCE CRITERIA - Excavated as per IFC drawings to line and levels shown. Foundation compaction Inspection Record completed.
label | DATE/SIGN - Contractor Rep - P
label | ○ CTS Civil Inspector - W
checkpoint | PSS3259/PSS3263/PSS3264/PSS3282 - Formwork, Reinforcing & Concrete
label | SPECIFICATION REFERENCE - IFC Drawings
label | ○ CTS General Civil Construction Specification NZS3109/3112
label | ○ Manufacturers Documentation
label | ○ Inspection Records
label | ACCEPTANCE CRITERIA - All reinforcing bars shall be Micro-Alloy Class E to AS/NZS 4671 as shown in IFC's.
label | ○ All reinforcing bar hooks, laps and bends shall be in accordance with NZS3109 unless otherwise noted.
label | ○ All reinforcing and formwork to comply with IFC drawings
label | ○ Concrete to be min 30MPa at 28 days
label | ○ Testing of concrete per CTS Specifications
label | ○ Prepour Inspection Record Filled out Prior to Concrete
label | DATE/SIGN - Contractor Rep - P
label | ○ CTS Civil Inspector - H
holdpoint | HOLD POINT
checkpoint | PSS3268/PSS3269 - Position of Slab Extension Setout
label | SPECIFICATION REFERENCE - IFC Drawings
label | ACCEPTANCE CRITERIA - Setout as per drawings
label | DATE/SIGN - Contractor Rep - P
label | ○ CTS Civil Inspector - R
checkpoint | PSS3268/PSS3269 - Excavation & Foundation Preparation inc Site Concrete
label | SPECIFICATION REFERENCE - IFC Drawings
label | ○ CTS Excavation Works Specification
label | ○ CTS General Civil Construction Specification
label | ACCEPTANCE CRITERIA - Excavated as per IFC drawings to line and levels shown. Foundation compaction Inspection Record completed.
label | DATE/SIGN - Contractor Rep - P
label | ○ CTS Civil Inspector - W
checkpoint | PSS3268/PSS3269 - Formwork, Reinforcing & Concrete
label | SPECIFICATION REFERENCE - IFC Drawings
label | ○ CTS General Civil Construction Specification NZS3109/3112
label | ○ Manufacturers Documentation
label | ○ Inspection Records
label | ACCEPTANCE CRITERIA - All reinforcing bars shall be Micro-Alloy Class E to AS/NZS 4671 as shown in IFC's.
label | ○ All reinforcing bar hooks, laps and bends shall be in accordance with NZS3109 unless otherwise noted.
label | ○ All reinforcing and formwork to comply with IFC drawings
label | ○ Concrete to be min 30MPa at 28 days
label | ○ Testing of concrete per CTS Specifications
label | ○ Prepour Inspection Record Filled out Prior to Concrete
label | DATE/SIGN - Contractor Rep - P
label | ○ CTS Civil Inspector - H
holdpoint | HOLD POINT
checkpoint | PSS3272/PSS3273 - Position of Slab Extension Setout
label | SPECIFICATION REFERENCE - IFC Drawings
label | ACCEPTANCE CRITERIA - Setout as per drawings
label | DATE/SIGN - Contractor Rep - P
label | ○ CTS Civil Inspector - R
checkpoint | PSS3272/PSS3273 - Excavation & Foundation Preparation inc Site Concrete
label | SPECIFICATION REFERENCE - IFC Drawings
label | ○ CTS Excavation Works Specification
label | ○ CTS General Civil Construction Specification
label | ACCEPTANCE CRITERIA - Excavated as per IFC drawings to line and levels shown. Foundation compaction Inspection Record completed.
label | DATE/SIGN - Contractor Rep - P
label | ○ CTS Civil Inspector - W
checkpoint | PSS3272/PSS3273 - Formwork, Reinforcing & Concrete
label | SPECIFICATION REFERENCE - IFC Drawings
label | ○ CTS General Civil Construction Specification NZS3109/3112
label | ○ Manufacturers Documentation
label | ○ Inspection Records
label | ACCEPTANCE CRITERIA - All reinforcing bars shall be Micro-Alloy Class E to AS/NZS 4671 as shown in IFC's.
label | ○ All reinforcing bar hooks, laps and bends shall be in accordance with NZS3109 unless otherwise noted.
label | ○ All reinforcing and formwork to comply with IFC drawings
label | ○ Concrete to be min 30MPa at 28 days
label | ○ Testing of concrete per CTS Specifications
label | ○ Prepour Inspection Record Filled out Prior to Concrete
label | DATE/SIGN - Contractor Rep - P
label | ○ CTS Civil Inspector - H
holdpoint | HOLD POINT
checkpoint | P3658 - Position of Pump Pedestal Setout
label | SPECIFICATION REFERENCE - IFC Drawings
label | ACCEPTANCE CRITERIA - Setout as per drawings
label | DATE/SIGN - Contractor Rep - P
label | ○ CTS Civil Inspector - R
checkpoint | P3658 - Pump Pedestal Location Cleaned & Scabbled
label | SPECIFICATION REFERENCE - IFC Drawings
label | ACCEPTANCE CRITERIA - Foundation area cleaned and free from contamination and dust/oil or grease, surface roughened to accept further concrete pour
label | DATE/SIGN - Contractor Rep - P
label | ○ CTS Civil Inspector - R
checkpoint | P3658 - Cast in Items - Bolts & Nuts
label | SPECIFICATION REFERENCE - IFC Drawings
label | ○ CTS General Civil Construction Specification
label | ○ CTS Epoxy Grouting of Anchor Bolts
label | ○ Manufacturers Documentation
label | ○ Inspection Records
label | ACCEPTANCE CRITERIA - If drilled in, Epoxy Grout Shall be Ramset C8 placed in accordance with manufacturers recommendations to the levels and positions setout in the drawings
label | ○ Drilled holes for Anchors shall be inspected
label | ○ Cast in anchor bolts shall be set to spec in IFC drawings and positioned with template to design measurenments in IFC drawings
label | DATE/SIGN - Contractor Rep - P
label | ○ CTS Civil Inspector - R
checkpoint | P3658 - Formwork, Reinforcing & Concrete
label | SPECIFICATION REFERENCE - IFC Drawings
label | ○ CTS General Civil Construction Specification NZS3109/3112
label | ○ Manufacturers Documentation
label | ○ Inspection Records
label | ACCEPTANCE CRITERIA - All reinforcing bars shall be Micro-Alloy Class E to AS/NZS 4671 as shown in IFC's.
label | ○ All reinforcing bar hooks, laps and bends shall be in accordance with NZS3109 unless otherwise noted.
label | ○ All reinforcing and formwork to comply with IFC drawings
label | ○ Concrete to be min 30MPa at 28 days
label | ○ Testing of concrete per CTS Specifications
label | ○ Prepour Inspection Record Filled out Prior to Concrete
label | DATE/SIGN - Contractor Rep - P
label | ○ CTS Civil Inspector - H
holdpoint | HOLD POINT
checkpoint | P3658 - Grouting of Baseplate
label | SPECIFICATION REFERENCE - IFC Drawings
label | ○ CTS General Civil Construction Specification
label | ○ Manufacturers Documentation
label | ACCEPTANCE CRITERIA - Grouting shall be Sika 212 or Sika 214 placed in accordance with manufacturers recommendations and the IFC drawings
label | DATE/SIGN - Contractor Rep - P
label | ○ CTS Civil Inspector - W
checkpoint | 5 - Other
label | SPECIFICATION REFERENCE - Other
label | ACCEPTANCE CRITERIA - Other
label | DATE/SIGN - Contractor Rep - H
label | ○ Project/Construction Engineer - H
holdpoint | HOLD POINT
checkpoint | 6 - Complete final Civil Inspection and close off ITP
label | SPECIFICATION REFERENCE - IFC Drawings
label | ○ CTS General Civil Construction Specification
label | ○ Manufacturers Specification
label | ACCEPTANCE CRITERIA - ITP/QC has been completed; all steps & hold points signed byrelevant party.
label | ○ All work completed as per work pack, and any field instructions issued during construction compiled
label | DATE/SIGN - Contractor Rep - P
label | ○ CTS Civil Inspector - H
holdpoint | HOLD POINT
checkpoint | 7 - Non-Conformance Reporting
label | SPECIFICATION REFERENCE - UCC Internal NCR and or Lucidity event NCR
label | ○ QC Requirements for Civil Works
label | ACCEPTANCE CRITERIA - All Non-Conformance reports and Investigations are attached and closed out
label | DATE/SIGN - Contractor Rep - R
checkpoint | 8 - As Built & Final Design Documentation
label | ACCEPTANCE CRITERIA - Confirmation From Engineer on as built records & redline mark ups
label | DATE/SIGN - Contractor Rep - P
checkpoint | 9 - Reference Info, Specifications
label | ACCEPTANCE CRITERIA - All Reference Information and relevant Product Specifications
checkpoint | 10 - Punch Listing
label | SPECIFICATION REFERENCE - CTS QC Requirments for Civil Work
label | ACCEPTANCE CRITERIA - All punch list items are closed out in the relevant timeframe to the required standard
label | DATE/SIGN - Contractor Rep - P
label | ○ Project/Construction Engineer - R
checkpoint | 11 - Compilation of ITP
label | ACCEPTANCE CRITERIA - ITP Completed and Signed off
label | DATE/SIGN - Contractor Rep - H
label | Project/Construction Engineer - H
holdpoint | HOLD POINT