## Project Checklist Templates
Id | Type | Name | Values | Prompting Name | Resource Id
| checklist | ITP-0001 - DI Watermain | itp | ITP-0001 - DI Watermain | 767915b5-898d-42a5-95b5-d535a75b7515
| section | SECTION 3 - RECEIVING INSPECTIONS
| checkpoint | 3.1 - Material Delivery
95f0052a-c399-5b13-b0b9-382fd441a454 | note | Inspection Point: Quality Control Activity - Inspect for damage and wear, Confirm items are correct as per drawings and Specifications
70dfd956-df25-5b7f-86f0-7193b5662c5f | note | Acceptance Criteria - DI Pipes shall be DN150 PN35 with cement mortar or concrete lining
dcb55c98-9f9d-58ec-ade2-b287fbeeb0f0 | note | ○ Material and fittings are approved as per contract specification
1e329314-d334-5eac-ac9e-6cb29ff28813 | note | Verifying Document - Photos, delivery docket, MDD results for backfill materials
6a900a08-cf3a-5a34-986b-8d6abbd14ea0 | note | Frequency - On Delivery
8fc40037-93e4-5baf-b841-9b67d77c2c6d | note | Inspection Type (Visual, other) - Visual
807e8f18-403e-57d4-aa8b-df95aa6912b4 | note | Inspection: Key - C
| checkpoint | 3.2 - Set out
299af1f6-b465-5cf7-837b-e19ce4fc81d1 | note | Inspection Point: Quality Control Activity - Allignment set out completed by an approved surveyor marked allignment
314918e2-3f45-55aa-8f18-6e5e59f44ed0 | note | Acceptance Criteria - Set out matches drawings, 2D data and linework provided or aggreed with the Engineer
e44535bb-5a5b-5708-8ccc-9e5e4c02dbbe | note | Verifying Document - Survey marks, photos
cb3c9eea-9691-54df-b7ba-490d3f53f66c | note | Frequency - Prior to commencement of works
3bfa345e-a230-5232-aa4e-aff9d673994b | note | Inspection Type (Visual, other) - Visual, Instrumental
9433c7f8-1e69-50c6-9616-f12667fdc477 | note | Inspection: Key - H
| signoff | HOLD POINT
| section | SECTION 4 - IN-PROCESS INSPECTIONS
| checkpoint | 4.1 - Trench Excavation
59010ff7-a58b-5930-a62f-f7f1aee9fefc | note | Inspection Point: Quality Control Activity - Excavate to acheive required depth to invert as per drawing C4500
7b767845-458a-5cf4-9389-5d9975f8ab65 | note | ○ Floor of trench to be even across width and length
f027339a-c927-5cae-a105-e737961ad5c9 | note | Acceptance Criteria - Allow 100mm for bedding
48b68b52-d794-5a42-b9be-298f7bb284fa | note | ○ Allow for minimum cover of 750mm. Max cover not exceeding 1000mm unless shown on Drawings C4500
81016198-c266-5a3e-aefb-51cf2e8133a4 | note | Verifying Document - Photos
fa9aff56-159a-53fb-a2a3-8cbfa9603454 | note | Frequency - During Installation
4d5a8c12-b117-5105-aea3-4f3537b97130 | note | Inspection Type (Visual, other) - Visual
245cff37-160f-5a3a-892d-c2664137d75f | note | Inspection: Key - V
| checkpoint | 4.2 - Foundation
857be670-bc35-536b-a536-03b584ae17ed | note | Inspection Point: Quality Control Activity - Scala tests on base of trench
bce46be0-68f3-5dca-9796-bf7345159e9f | note | Acceptance Criteria - minimum of 2 blows per 100mm
1e8e82ea-d609-5ab8-acbf-c589247e8cba | note | Verifying Document - test results
2b85e972-d27a-5e78-ad4f-7dc08f0d5ee3 | note | Frequency - During installation, per 20m
b149e75b-9ad3-5a32-9894-e58a4acdfae3 | note | Inspection Type (Visual, other) - Visual, On site test
69645629-13c6-51f9-8c76-3ea0f4ba9fc9 | note | Inspection: Key - H
| signoff | HOLD POINT
| checkpoint | 4.3 - Ductile Iron Pipe Installation
27a1ac53-6186-56a6-b519-35fb8e1c8e7a | note | Inspection Point: Quality Control Activity - Pipes installed and positioned as per design
c4695230-3e9e-52d6-9063-dfc8677fdfaa | note | Acceptance Criteria - Pipe not damaged during installation
dcab95bf-dea1-550d-9902-18556550594c | note | ○ Pipe is centrally located within trench
f7bcbd19-1d01-557d-9316-879d969b6514 | note | ○ Pipe levels are within tolerance and according to the drawings
93e01d6b-2cde-5cc8-b34d-cd87c14b9e4c | note | Verifying Document - Photos, Survey of position for asbuilt
19863c04-fad6-59cc-bce6-0e5f7ad6ae83 | note | Frequency - During installation
6bb84f5f-54d1-5950-84d3-7eb8bd47d653 | note | Inspection Type (Visual, other) - Visual
0ae62b89-b361-51b9-ba5a-211bc7b40731 | note | Inspection: Key - V
| checkpoint | 4.4 - Embedment zone
809c1018-e052-592c-8094-c6940702520d | note | Inspection Point: Quality Control Activity - Embedment material shall be AP20 or approved by the Engineer in writing
3a8be8d3-5271-5443-8885-e836871f838c | note | Acceptance Criteria - Min 100mm bedding
436329b5-94f9-59e1-8dc8-818d7c7cb4b4 | note | ○ 100mm overlay
4cd20966-44a6-569d-93f2-71b0efca2daa | note | Verifying Document - Photos
5584e74a-6509-5ee8-9cea-73acbd196731 | note | Frequency - During Installation
62aaf457-6c46-5554-9926-7e38143346ac | note | Inspection Type (Visual, other) - Visual
fa488abc-db7f-5f8b-8e62-9fe565493efc | note | Inspection: Key - V
| checkpoint | 4.5 - Backfill and Compact
daaaf144-0ceb-539a-8599-9ae01570e671 | note | Inspection Point: Quality Control Activity - Backfill material shall be AP65
8c67a3f8-1833-50d7-8f4c-f72d9f195f93 | note | ○ Backfill in 200mm layers of compacted material
025b65db-01cf-5584-8039-85fa20e47d3f | note | ○ Compaction testing one test every two layers as required
34c7cce5-59c1-54f8-837a-34ae28ffd96c | note | ○ Conductive signal strip to be laid at 300mm above pipe
474037b9-3d34-5285-82c0-e42f0771aeae | note | Acceptance Criteria - 95% MDD in roads, paths, and pavements
32e0dff3-54b2-5883-944c-d5b33858cfc2 | note | Verifying Document - Photos, Compaction test results
dbc37c94-5497-55f6-a47a-7b11fe4236ae | note | Frequency - During Installation, compaction testing per 50m of pipeline
c6157455-9d54-53de-9422-3ae10fb80541 | note | Inspection Type (Visual, other) - Visual, On Site test
43763bde-2eee-599c-87cb-3f1c815a649a | note | Inspection: Key - H
| signoff | HOLD POINT
| section | SECTION 5 - FINAL INSPECTION AND HANDOVER
| checkpoint | 5.1 - Pressure Testing (non-PE pipeline)
57ead7f5-36b5-593e-9441-93539912cf78 | note | Inspection Point: Quality Control Activity - Non PE pipelines to be tested in accordance with specifications
b62d67ac-924b-56d9-b8d0-88474c05ea4a | note | Acceptance Criteria - Specification WM 4.6.1: No Thrust block failures, No visible leaks, Do not exceed make-up water limit.
f4b5f43d-7068-547f-a2b9-021a2f91888c | note | Verifying Document - Test Records
3cff9625-4950-5871-a68d-f4e816b21ece | note | Frequency - Before commisioning
cdc40938-3c80-5010-94ad-97c0058da5ad | note | Inspection Type (Visual, other) - On-Site Test
d968d8cb-2885-5a1e-bcaf-d01096beba67 | note | Inspection: Key - H
| signoff | HOLD POINT
| checkpoint | 5.2 - Disinfection
4a784473-5f0a-5c40-9386-b5aed470a608 | note | Inspection Point: Quality Control Activity - Disinfection to be completed in accordance with specifications
d3be427f-204c-584b-aef1-07069bd4f5b7 | note | Acceptance Criteria - Specification WM 4.11:
716f865d-16f4-52ff-9840-cede1d671e85 | note | Verifying Document - Test Records
a7d1aec7-09c8-50cb-baf6-987c379f0dad | note | Frequency - Before commisioning
34f71a4f-7a08-5861-96da-ccac84ee8382 | note | Inspection Type (Visual, other) - On-Site Test
6fdf1c8c-1d03-5aa7-8875-29064814b7c2 | note | Inspection: Key - H
| signoff | HOLD POINT
| checkpoint | 5.3 - As-Built
23f9b5c9-96b0-573e-b1fc-7fe29078b8cc | note | Acceptance Criteria - Engineer Approval
f7fa94e0-15a2-56ec-900b-6ede2571580c | note | Verifying Document - QA records
51c92772-3f69-59c9-a227-d29c46abbc7b | note | Frequency - At completion
28e83814-cc29-5f0d-8ea1-2be2402fecf5 | note | Inspection: Key - H
| signoff | HOLD POINT
| section | SECTION 6 - COMMENTS
| checkpoint | Customer Release Granted
27096ed5-7ed3-5ae7-835d-594e7d6f8960 | textbox | Certificate Number:
f3465670-ba4d-5743-98fe-c26ba105d920 | date | Date:
| checklist | ITP-0002 - PE Watermain | itp | ITP-0002 - PE Watermain | 9834426f-1a5f-47db-983e-6e40f3d0e12e
| section | SECTION 3 - RECEIVING INSPECTIONS
| checkpoint | 3.1 - Material Delivery
2db0b0ce-8e5c-5fbe-93c8-ac0e778e3993 | note | Inspection Point: Quality Control Activity - Inspect for damage and wear, Confirm items are correct as per drawings and Specifications
2fd06242-83c9-568c-9e57-3058d29bd0a7 | note | Acceptance Criteria - Pipes shall be DN63 PN16 PE80
8a530a5b-b19d-5b80-a024-b6a0a3107801 | note | ○ Material and fittings are approved as per contract specification
41036e47-785f-5a27-863b-8b426772dbf4 | note | Verifying Document - Photos,delivery docket, MDD results for backfill materials
fdb7957b-1d37-58c0-a66d-bafe66ae53fa | note | Frequency - On Delivery
1767c647-cc30-5c2e-8660-a6ab563654ff | note | Inspection Type (Visual, other) - Visual
a13e224d-dd93-5322-8734-9af4a4037369 | note | Inspection: Key - C
| checkpoint | 3.2 - Set out
02cfc7b8-03d2-505a-a322-0eaf3645cf93 | note | Inspection Point: Quality Control Activity - Allignment set out completed by an approved surveyor marked allignment
4e841cb8-1c5f-5108-8458-12fe12a4187c | note | Acceptance Criteria - Set out matches drawings, 2D data and linework provided or aggreed with the Engineer
659acb46-0359-5c53-9dd0-9f650ea6a039 | note | Verifying Document - Survey marks, photos
3f62f40b-f52a-5f30-ac8c-a5459c532fde | note | Frequency - Prior to commencement of works
fbaab756-18a9-583b-be7f-558fd1e0a12b | note | Inspection Type (Visual, other) - Visual, Instrumental
497ae945-d0d1-5bc5-97c5-e153337d57da | note | Inspection: Key - H
| signoff | HOLD POINT
| section | SECTION 4 - IN-PROCESS INSPECTIONS
| checkpoint | 4.1 - Trench Excavation
0e61c345-756e-5b6a-880f-ea58638ca6e4 | note | Inspection Point: Quality Control Activity - Excavate to acheive required depth to invert as per drawing C4500
c1e6df37-3058-50df-9a08-e80d142f2cd8 | note | ○ Floor of trench to be even across width and length
cea94ee6-ec87-5ab5-a2b9-fdc4d191a6df | note | Acceptance Criteria - Allow 100mm for bedding
6f04a03c-6ed7-53f7-9515-f1a6b3a561de | note | ○ Allow for minimum cover of 750mm. Max cover not exceeding 1000mm unless shown on Drawings C4500
61c232e1-4be1-55ca-a956-f06ea936a3c1 | note | Verifying Document - Photos
4251ad0f-a1a5-5ce3-bc01-df379f5125b4 | note | Frequency - During Installation
3759decc-3445-5c6c-a501-1234b1685534 | note | Inspection Type (Visual, other) - Visual
eb7e49ed-4f12-570c-9fa1-dde834716dbf | note | Inspection: Key - V
| checkpoint | 4.2 - Foundation
ad5eb550-15dc-56cf-ace7-ab9a959a30f5 | note | Inspection Point: Quality Control Activity - Scala tests on base of trench
61ccfc23-29cc-551b-b0ad-c99158fc1679 | note | Acceptance Criteria - minimum of 2 blows per 100mm
38b92c67-1b58-5259-9164-83fd0c1d9cd0 | note | Verifying Document - test results
636e9912-a1ec-5d7e-a283-bcccc04da6df | note | Frequency - During installation, per 20m
72aa5685-db82-5c87-848f-90f2f58b2f86 | note | Inspection Type (Visual, other) - Visual, On site test
72d3e610-6bf4-5f9d-8f0b-c0714cc59497 | note | Inspection: Key - H
| signoff | HOLD POINT
| checkpoint | 4.3 - Pipe Installation
28c9ca0a-f8cc-5a59-9cb5-2cc5009916fc | note | Inspection Point: Quality Control Activity - Pipes installed and positioned as per design
77affdb4-367f-5448-bb0a-ce3f82baea4e | note | Acceptance Criteria - Pipe not damaged during installation
801c4c87-d32c-55f5-b98e-38ed7551e50e | note | ○ Pipe is centrally located within trench
8a37136d-6e12-59e3-87eb-0b96df871a55 | note | ○ Pipe levels are within tolerance and according to the drawings
ec1537b4-baf7-541b-ae01-35e230dd7b19 | note | Verifying Document - Photos, weld records (if required), Survey of position for asbuilt
d914efd2-344e-5f29-b0ac-643a116cb1d2 | note | Frequency - During installation
0d892a48-e70a-5a4f-ae68-d4ba83a99eb3 | note | Inspection Type (Visual, other) - Visual
17d84d09-354c-57fd-9460-425db729d5f5 | note | Inspection: Key - V
| checkpoint | 4.4 - Embedment zone
14662422-d3ab-5a21-9f78-c1b5fb118de8 | note | Inspection Point: Quality Control Activity - Embedment material shall be AP20 or approved by the Engineer in writing
5b6f5399-560a-5b3f-b398-8770fe3088c3 | note | Acceptance Criteria - Min 100mm bedding
4cfcc987-3a20-5b9a-ab89-6f10fa9e251b | note | ○ 100mm overlay
13553891-0ce7-59f7-905f-f0f4e45f9c12 | note | Verifying Document - Photos
b777e6ad-f4e2-551b-9780-4747ddb5f39d | note | Frequency - During Installation
369c27a6-6265-5c04-8c8c-a17f09a6aca1 | note | Inspection Type (Visual, other) - Visual
b1a317ae-c537-5434-8d9a-1d168d1c0e96 | note | Inspection: Key - V
| checkpoint | 4.5 - Backfill and Compact
c4ed0ba1-45cd-5f87-8bb3-a94300e5252c | note | Inspection Point: Quality Control Activity - Backfill in 200mm layers of compacted material
58d78ea6-92a5-55e3-aa6b-5fdf5c91c0fa | note | ○ Compaction testing one test every two layers as required
1bbadaa9-d47c-52a7-abd6-5ab1b3e4dec3 | note | ○ Conductive signal strip to be laid at 300mm above pipe
90381076-357d-5bcd-9ee2-36d58687dedc | note | Acceptance Criteria - Passing compaction results - 95% MDD backfill - basecourse
c5049d5f-1bb7-5dbb-8328-190ea949f82d | note | Verifying Document - Photos, Compaction test results
3baf512e-9911-52c9-a9d1-bdcfe7f5cbd8 | note | Frequency - During Installation, compaction testing per 50m of pipeline
c612634a-2179-55f9-91c8-3d02e8d3c816 | note | Inspection Type (Visual, other) - Visual, On Site test
8b5d4dc5-63e7-5441-a5b1-90c8de84d468 | note | Inspection: Key - H
| signoff | HOLD POINT
| section | SECTION 5 - FINAL INSPECTION AND HANDOVER
| checkpoint | 5.1 - Pressure Testing (PE pipeline)
78f58bde-a020-5fab-840f-9364074a50cc | note | Inspection Point: Quality Control Activity - PE pipelines to be tested in accordance with specifications
ea419330-966f-526e-b149-d37a363f0816 | note | Acceptance Criteria - Specification WM 4.7.5: No Thrust block failures, No visible leaks, Do not exceed make-up water limit
d31629db-bf4d-5c9c-83b7-9aa4b43dcf26 | note | Verifying Document - Test Records
444a8ca3-e6b1-581a-9461-77721794adcf | note | Frequency - Before commissioning
dfab7f7f-dfc7-5e06-8561-e54abde1ac1e | note | Inspection Type (Visual, other) - On-Site Test
c2779745-08bd-5ff9-8f8f-3621200b77db | note | Inspection: Key - H
| signoff | HOLD POINT
| checkpoint | 5.2 - Disinfection
31ebd585-0600-5105-a55b-2efd3787d67d | note | Inspection Point: Quality Control Activity - Disinfection to be completed in accordance with specifications
2bbfa808-d004-5f10-8a6a-31c5bedfb862 | note | Acceptance Criteria - Specification WM 4.11:
2abac563-d9f5-5145-bf24-61cd054ac670 | note | Verifying Document - Test Records
8b17f466-8d64-5152-9282-1658bc07d7de | note | Frequency - Before commissioning
c3590ca3-9c03-56a8-a50d-ca3b707cae79 | note | Inspection Type (Visual, other) - On-Site Test
1e13bf72-aa7c-5db8-8dcf-de1c896152d5 | note | Inspection: Key - H
| signoff | HOLD POINT
| checkpoint | 5.3 - As-Built
9a06dea4-21a5-59c5-8a35-4e8a1d37d7fe | note | Acceptance Criteria - Engineer Approval
854cd6d9-9402-5cb7-a6b8-60693d45e3bb | note | Verifying Document - QA records
d2df897d-a9a9-5d38-abc9-e9df67d3be24 | note | Frequency - At completion
e8e231ce-2b20-5bb7-b87d-863efc08f0e3 | note | Inspection: Key - H
| signoff | HOLD POINT
| section | SECTION 6 - COMMENTS
| checkpoint | Customer Release Granted
24df9a0f-dd3c-547f-865e-fd17b03e5273 | textbox | Certificate Number:
dfba6ae7-ce54-54b8-a22c-0c151a65217e | date | Date:
| checklist | ITP-0003 - Ducting | itp | ITP-0003 - Ducting | 782dd239-3b1b-42bc-b629-248808801d0c
| section | SECTION 3 - RECEIVING INSPECTIONS
| checkpoint | 3.1 - Material Delivery
8d902c4c-affa-553e-9f08-490e6074f82d | note | Inspection Point: Quality Control Activity - Inspect for damage and wear, Confirm items are correct as per drawings and Specifications
cf5edf52-5433-5344-905e-168289730e73 | note | Acceptance Criteria - Items are approved as per contract specification or as agreed by the engineer
07112d89-e4fb-5f9b-8cd2-45b02ce7fd54 | note | ○ DCC approved
8120143a-a2fd-5c99-97e9-fa8f5dc84740 | note | Verifying Document - Photos, delivery docket, MDD results for backfill materials (if required)
48af411d-411d-5d79-994f-ea06e949c798 | note | Frequency - On Delivery
51064610-ff9c-5dd1-8d53-210c81058b6f | note | Inspection Type (Visual, other) - Visual
91a0b025-3ca9-5e95-b207-8deed9e4b330 | note | Inspection: Key - C
| checkpoint | 3.2 - Set out
ae066ef9-0984-5cd8-a226-1fc349b21f53 | note | Inspection Point: Quality Control Activity - Set out completed by an approved surveyor marked allignment
29a471bc-026e-50ef-bfdd-82a1f17be599 | note | Acceptance Criteria - Allignment set out matches drawings, 2D data and linework provided or aggreed with the Engineer
d03b60bd-7a6a-5b8a-8f2a-261c3bb411e1 | note | Verifying Document - Survey marks, photos
8115acc6-0430-526a-bcd2-b522390e4e72 | note | Frequency - Prior to commencement of works
5a6f757d-64bf-50f1-b34e-b4a64b39b801 | note | Inspection Type (Visual, other) - Visual, Instrumental
da13be71-93e6-5c68-9559-99a4695e54ac | note | Inspection: Key - H
| signoff | HOLD POINT
| section | SECTION 4 - IN-PROCESS INSPECTIONS
| checkpoint | 4.1 - Trench Excavation
a2397ccb-6c99-525b-a9c5-b77cfec8b051 | note | Inspection Point: Quality Control Activity - Excavate to achieve required depth as per Drawing C4600,C4500
ebace46e-95ae-5388-8b10-adda14a6199d | note | ○ Floor of trench to be even across width and length
8b0f67a7-d71c-5c93-9f07-078b21ad0f88 | note | Acceptance Criteria - Allow 100mm for bedding
00c359b0-3f65-53fc-abcb-f815b8c6eec6 | note | ○ Allow for minimum cover of 600mm.
5f50eb37-df33-5a14-b10f-cbf3d6104142 | note | Verifying Document - Photos
02ae92e1-e99d-592d-b198-7379398e529b | note | Frequency - During Installation
f4505258-4ef3-5dd1-8377-5e73e51ca6ac | note | Inspection Type (Visual, other) - Visual
81c8f8e2-28db-58c2-8f50-781bc18966f2 | note | Inspection: Key - V
| checkpoint | 4.2 - Foundation
7c4cb71d-a4ba-52d9-ace5-d5d5ef95ecc1 | note | Inspection Point: Quality Control Activity - Scala tests on base of trench
e0953abd-7b7a-5a52-826b-9e5353cf1095 | note | Acceptance Criteria - minimum of 2 blows per 100mm
0b64e85b-26ac-5da8-82ff-a10d18c9758c | note | Verifying Document - test results
5e476bbe-174e-5db4-8a61-817c23738ced | note | Frequency - During installation, per 20m
89391e0a-cd85-5ee2-a490-c202c0328502 | note | Inspection Type (Visual, other) - Visual, On site test
1d9e19ed-acc9-5672-9229-1126fbfc2a3c | note | Inspection: Key - H
| signoff | HOLD POINT
| checkpoint | 4.3 - Install Duct
d3140c32-17e8-519c-8d33-1bf7e6de6e55 | note | Inspection Point: Quality Control Activity - Ducting installed and positioned as per design
7c056b31-b6c5-517c-9d15-c274c7de8440 | note | Acceptance Criteria - Duct not damaged during installation
1accd5ae-0db7-59b9-ba98-629af29a31c4 | note | ○ Minimum of 150mm horizontal and vertical clearence from other services or as specified on Drawings C4600, C4500
a5bc5895-9ab6-5634-a130-3e5d30dd835f | note | Verifying Document - Photos, Survey of position for asbuilt, weld records (if required)
313b1e98-e95e-577d-a6fe-68886d893217 | note | Frequency - During installation
5b80d755-722e-5988-9dd0-c84e17d1ad16 | note | Inspection Type (Visual, other) - Visual
decf6a22-76b6-5ccd-8261-2ee0f90b82d0 | note | Inspection: Key - V
| checkpoint | 4.4 - Embedment zone
f76f3a6c-a88d-54ef-9698-d9cdae1da0d1 | note | Inspection Point: Quality Control Activity - Embedment material shall be AP20 or approved by the Engineer in writing
59a6202a-5885-5d77-849a-34dbe244afc5 | note | Acceptance Criteria - Min 100mm bedding
fc25305e-7973-546a-b8e1-a0f45f8b2303 | note | ○ 100mm overlay
4c335cb2-e8ef-5997-ae01-12952b650974 | note | Verifying Document - Photos
fe7ddae4-2304-52d4-aea7-85e2fa9796f8 | note | Frequency - During Installation
436864b6-e3e0-5ae9-8a61-ce30229de621 | note | Inspection Type (Visual, other) - Visual, measurement check
b8c9868d-7396-5851-a703-0eefd4b14fb1 | note | Inspection: Key - V
| checkpoint | 4.5 - Backfill and Compact
6f28239d-0725-58b0-9012-60710954e9a3 | note | Inspection Point: Quality Control Activity - Backfill in 200mm layers of compacted material
bc2bfa89-42ac-5ab9-b44b-c749bdcbc8bc | note | ○ Compaction testing one test every two layers as required
4f37897e-2756-5699-aa29-e1da630280d6 | note | ○ Conductive signal strip to be laid at 300mm above duct
b6d636d5-f794-5b49-b270-bfee37df99ee | note | Acceptance Criteria - 95% MDD in roads, paths, and pavements
224ee362-8bfc-57ae-9d94-e9608d14e307 | note | Verifying Document - Photos, Compaction test results
7d9f6647-3a2f-5542-83a4-8ede136a128b | note | Frequency - During Installation, compaction testing per 50m of pipeline
529d52b2-3d85-56ab-a4b3-e9b03517687e | note | Inspection Type (Visual, other) - Visual, On Site test
a77e93be-b2af-5473-91ba-e40b7b14b420 | note | Inspection: Key - H
| signoff | HOLD POINT
| section | SECTION 5 - FINAL INSPECTION AND HANDOVER
| checkpoint | 5.1 - As built
9d816568-a130-5295-b70d-6ef281625964 | note | Acceptance Criteria - Engineer Approval
6f746184-a1ff-5f91-bca3-b1dd4a4d46b5 | note | Verifying Document - QA records
c9f0114c-dd6e-509a-bdde-4dedb0b9b521 | note | Frequency - At completion
61e8da25-482b-5c7a-96a2-b5aa94691a7a | note | Inspection: Key - H
| signoff | HOLD POINT
| section | SECTION 6 - COMMENTS
| checkpoint | Customer Release Granted
c6bfe258-5cf9-5e9c-8e2a-a2346511d9ee | textbox | Certificate Number:
d99bfeec-2811-5b92-95aa-00c28d2a820e | date | Date:
| checklist | ITP-4001 - Brick Barrel Corbel Connection | itp | ITP-4001 - Brick Barrel Corbel Connection | e2e83650-14ec-4676-8a85-5d05c37c2771
| section | SECTION 3 - RECEIVING INSPECTIONS
| checkpoint | 3.1 - Material Delivery
df6a6cb8-4f95-51c2-be51-1aceeb681998 | note | Inspection Point: Quality Control Activity - Inspect for damage and wear, Confirm items are correct as per drawings and Specifications
586907b7-5ab2-589c-8f35-0b9c5853c9b0 | note | Acceptance Criteria - Pipes shall be DN750 Class 4 RCRRJ
6a6315a6-276b-568a-84bd-092d52ae19c7 | note | ○ Items are approved as per contract specification
088fb763-f7e4-56a7-b925-82904c7ba48b | note | ○ DCC approved
3180f4f7-5c5f-5f42-9488-c8ecf3166c7a | note | Verifying Document - Photos, delivery docket, MDD results for backfill materials (if required)
aff52395-af05-54b6-8492-db24467d282f | note | Frequency - On Delivery
2e2e8ddb-6ee6-5fc8-ad4f-c0e2eb927738 | note | Inspection Type (Visual, other) - Visual
4f4e092f-2a67-5643-be02-876c17b8058c | note | Inspection: Key - C
b35713ac-9921-564d-94c5-590a47271b61 | note | Inspection: By (Role Key) - SV/QE
| checkpoint | 3.2 - Set out
225acd77-0423-50c7-9fe0-2a79ffc2fa29 | note | Inspection Point: Quality Control Activity - Set out completed by an approved surveyor marked allignment
58562ff4-07d7-5a9e-8b3a-98b486d37d32 | note | Acceptance Criteria - Allignment set out matches drawings, 2D data and linework provided or aggreed with the Engineer
44c9ff24-e2f7-5a09-8494-30cfe6936470 | note | Verifying Document - Survey marks, photos
71beee53-1c7c-5185-9fac-4e8cd82317d2 | note | Frequency - Prior to commencement of works
14fca69e-c4e1-5626-a156-3fcc914cf4df | note | Inspection Type (Visual, other) - Visual, Instrumental
d44b69f3-c640-5fcd-8286-6388d6ad17e4 | note | Inspection: Key - H
b18a2c94-16da-5305-ba2a-6345a5a6dc83 | note | Inspection: By (Role Key) - SV/SP/QE/CM
| signoff | HOLD POINT
| section | SECTION 4 - IN-PROCESS INSPECTIONS
| checkpoint | 4.1 - Trench Excavation
b7e4ff50-ff5e-51b9-bf9a-033f2cb7d274 | note | Inspection Point: Quality Control Activity - Excavate to achieve required depth to invert as per C4200, C4300, C4301
df4c971a-caff-50f1-b84d-1d6f7ba02975 | note | ○ Trench width to allow for 300mm seperation between springline of the pipe and trench wall or an adjacent pipe
b6149933-2d60-5b43-906c-3e91bdbc1913 | note | ○ Floor of Trench to be even across width and length
2b94477e-f9c6-5b5d-a509-7f1d1a3fec41 | note | Acceptance Criteria - Allow 100mm for bedding
681feb7b-91a1-570b-a656-e919ce52372b | note | ○ Allow for minimum cover of 750mm.
713bd5a6-e50a-57ce-a93c-03af39277527 | note | Verifying Document - Photos, measurement checks
2271ab2c-1eb8-588c-ac46-439046d9bb34 | note | Frequency - During Installation
ed10fbc7-f530-5520-adf0-632dabd1a2c8 | note | Inspection Type (Visual, other) - Visual
26f93781-3cc6-55fd-a5e9-33d2d084424e | note | Inspection: Key - C
5e8a2d28-3e55-5549-accc-27c9401cac79 | note | Inspection: By (Role Key) - SP/QE/CM
| checkpoint | 4.2 - Foundation
019d366e-d262-5769-9e01-6c02ffcef3a9 | note | Inspection Point: Quality Control Activity - Scala tests on base of trench
77277469-fdb4-52cb-8a31-f7beb95702d4 | note | Acceptance Criteria - minimum of 2 blows per 100mm
3636cfd1-b513-5eae-8b2f-2d247baa54a2 | note | Verifying Document - test results
27f1245c-e4b7-510c-b3fe-8835df6f7734 | note | Frequency - During installation, per 20m
20f44909-0a5b-500b-825b-44ef19c7d5ca | note | Inspection Type (Visual, other) - Visual, On site test
a7737c7f-e457-5683-921c-ac2b7584507b | note | Inspection: Key - H
b2cee8ec-bd49-5a23-a473-4c66f7c0b5fd | note | Inspection: By (Role Key) - SP/QE
| signoff | HOLD POINT
| checkpoint | 4.3 - Install corbell
572abdee-4a99-5882-b0a5-48525bcf1eed | note | Inspection Point: Quality Control Activity - pre pour inspection
241ad6b3-0569-5d1b-96e8-0890d56db9d9 | note | Acceptance Criteria - Engineers approval to proceed
560bbe87-6fbb-5480-854d-2868bdd8d75f | note | Verifying Document - Pre pour inspection form
c506e4d2-6527-5655-b277-02cc6cade40d | note | Frequency - Prior to pour
9930c6d3-a850-5a83-8d22-2ebed0880616 | note | Inspection Type (Visual, other) - Visual
74ddb0fe-1ae3-5887-b969-3676cc54038d | note | Inspection: Key - I
f358af24-db3b-566e-a5e1-412f10ade309 | note | Inspection: By (Role Key) - CR
| checkpoint | 4.4 - Install Pipe
bd419529-1ae9-5538-b903-c2c30d8d60c4 | note | Inspection Point: Quality Control Activity - Pipe installed to grade as per drawing C4200, C4300, C4301
19d88ea5-5e3c-5502-bb84-d786f304eda1 | note | Acceptance Criteria - Pipe not damaged during installation
d0ae15ac-ad5c-5c38-98c6-1257cf696152 | note | ○ Pipe installed to grade within tolerances specification GP 3.1.8
9ef0c3b8-4bb8-572c-9bf4-202eab54d55b | note | ○ Pipe installed at approved angle
e7460f0a-2048-5e09-980b-4caecb6d770d | note | Verifying Document - Photos, Grade check sheet, Survey of position for asbuilt
a9643693-70b9-527a-b6ce-e32117949c9f | note | Frequency - During installation
94f92a24-7547-5f02-9b4d-c2f6fa7ea38d | note | Inspection Type (Visual, other) - Visual, instrumental
e8df5b1c-0441-5279-ab90-2238db549453 | note | Inspection: Key - C
6f475b95-b9ee-510e-b8ca-6ac7a107d924 | note | Inspection: By (Role Key) - SP/QE
| checkpoint | 4.5 - Embedment zone
bd716f95-4b33-5c53-8b08-15cef9ecc057 | note | Inspection Point: Quality Control Activity - Embedment material shall be AP20 or approved by the Engineer in writing
64533a30-3800-5889-b164-c0bc8e781443 | note | Acceptance Criteria - min 100mm bedding
a5c4c4cf-f373-53c4-b164-e06f23981bb3 | note | ○ 150mm overlay
3e23554d-c91b-55c9-819b-45f3185f16a6 | note | Verifying Document - Photos
85d4ff2a-5ad9-50d9-95e1-e0f20919e92f | note | Frequency - During Installation
5c56996c-74db-5ae8-af52-bcee11199049 | note | Inspection Type (Visual, other) - Visual, measurement check
b79421e2-e43c-5ed2-a862-dde20c27f2dc | note | Inspection: Key - C
f1f3f54b-b7de-5009-87f8-77ff40042b71 | note | Inspection: By (Role Key) - SP/QE
| checkpoint | 4.6 - Backfill and Compact
7d48c4fe-feb9-51cf-be3f-b91585d6826f | note | Inspection Point: Quality Control Activity - Backfill in 200mm layers of compacted material
396778eb-09bc-58f8-86dc-83c81be956cc | note | ○ Compaction testing one test every two layers as required
f85be66b-af91-5cbf-95ac-cf81b4f4df88 | note | ○ Conductive signal strip to be laid at …mm cover
2987fc39-3716-5ace-bdc8-966f37d1cf92 | note | Acceptance Criteria - 95% MDD in roads, paths, and pavements
41405a61-90f6-5085-b988-63edff3a1c9c | note | Verifying Document - Photos, Compaction test results
ae468b6a-3865-557f-898e-fcb2e02da7bd | note | Frequency - During Installation, compaction testing per 50m of pipeline or per straight section of pipeline
fd2d5433-4ac0-5808-aece-62607c897a32 | note | Inspection Type (Visual, other) - Visual, On Site test
6677f2f7-7ff1-5ca7-9bca-b6a9b2967cb4 | note | Inspection: Key - H
ec24dab7-9b5f-52ec-a312-b58ae892f41a | note | Inspection: By (Role Key) - SP/QE
| signoff | HOLD POINT
| section | SECTION 5 - FINAL INSPECTION AND HANDOVER
| checkpoint | 5.1 - As built
eb3c23bd-396c-5a7c-817e-78cd93a84fda | note | Acceptance Criteria - Engineer Approval
72915a9a-98b4-5c94-a884-64dffc7aebfb | note | Verifying Document - QA records
9debece8-6676-5674-9aad-577bcb23380b | note | Frequency - at completion
2d4c15ad-2980-506d-be93-ceb95d50afcf | note | Inspection Type (Visual, other) - H
bbf6b9ee-735e-5025-88f8-adf4e2234a73 | note | Inspection: Key - CM/PM
| signoff | HOLD POINT
| checklist | ITP-4002 - WCMH-5 | itp | ITP-4002 - WCMH-5 | 9288ffc6-0ed4-4be6-b70d-0bb793bcd661
| section | SECTION 3 - RECEIVING INSPECTIONS
| checkpoint | 3.1 - Material Delivery
38603c8f-a73c-5d3d-82f1-28b95910bac8 | note | Inspection Point: Quality Control Activity - Inspect for damage and wear, Confirm items are correct as per drawings and Specifications
9c267aa9-0cf7-5ce5-84c5-061a05ab0636 | note | Acceptance Criteria - Items are approved as per contract specification
07635d10-95b8-5590-8a3b-78d90300b01c | note | ○ DCC approved
68703632-508d-5e5d-954d-ce925de00a15 | note | Verifying Document - Photos, delivery docket, MDD results for backfill materials
e79ca831-2d9d-5c32-95f2-e0cc09660e08 | note | Frequency - On Delivery
f65e4f50-fbc7-5114-b934-12ba70cc876c | note | Inspection Type (Visual, other) - Visual
e03b5b46-05ea-57a1-abb6-130c5cbfcccb | note | Inspection: Key - C
65de8343-ad37-5854-9247-8f0f72e39085 | note | Inspection: By (Role Key) - SP/QE
| checkpoint | 3.2 - Set out
bfc82637-aaf4-5433-8c1a-408b5acaf4bd | note | Inspection Point: Quality Control Activity - Set out completed by an approved surveyor marked allignment
89ac8ef3-7f5a-5e88-8bf9-a3f875988828 | note | Acceptance Criteria - Allignment set out matches drawings or aggreed with the Engineer
e5a14dd7-3629-55b7-b396-dda6dac09c4b | note | Verifying Document - Survey marks, photos
8d03c984-cae6-545e-81f9-c5fd949e1c9b | note | Frequency - Prior to commencement of works
a97224c6-c592-5809-a764-70600471ae60 | note | Inspection Type (Visual, other) - Visual, Instrumental
da82f296-0062-59fd-b461-65eab2d4bc44 | note | Inspection: Key - H
3c3c0e11-54bf-5a9d-bd5b-18b3487a3c57 | note | Inspection: By (Role Key) - SV/SP/QE/PE
| signoff | HOLD POINT
| section | SECTION 4 - IN-PROCESS INSPECTIONS
| checkpoint | 4.1 - Trench Excavation
8261be8e-3b86-5fe8-9e6b-db454c71faaf | note | Inspection Point: Quality Control Activity - Excavate to required depth to invert as per C4200
994c45d7-2f1b-5ef6-8094-e9598e4e6bc2 | note | ○ Trench width to allow for 300mm seperation between springline of the pipe and trench wall or an adjacent pipe
4b9898c5-242a-59f1-a4b2-c3afaa7455a3 | note | ○ Floor of Trench to be even across width and length
0e3b8cb1-8106-5f6e-b1e2-95bd2c6c778b | note | Verifying Document - Photos, measurement checks
6a299a39-c994-5c6b-bbda-5e01b757a357 | note | Frequency - During Installation
dbb2364c-9356-5d6a-ba4a-9de963d3bac6 | note | Inspection Type (Visual, other) - Visual
1f515b94-1bc0-50b4-800b-acd76aed6fbe | note | Inspection: Key - V
4639a0bc-8afe-5e70-b44d-2c89026711b8 | note | Inspection: By (Role Key) - SP/QE/PE
| checkpoint | 4.2 - Foundation
bedd57af-f748-5622-ab50-bc09b56e7f26 | note | Inspection Point: Quality Control Activity - Scala tests on base
a5a9c327-6b92-5386-9837-7d85367045ca | note | Acceptance Criteria - minimum of 2 blows per 100mm
5daf8c44-62c9-5d5d-af5e-597f07cb2f48 | note | Verifying Document - test results
1bdac60f-976c-5d3a-8f8e-b85af7a0a9da | note | Frequency - One off
031b4f8e-d70b-558c-9fe3-0e2beaebe73d | note | Inspection Type (Visual, other) - Visual, On site test
85d9d35b-aa6a-516e-97ae-79ff198602d6 | note | Inspection: Key - C
ce6a87c3-bea1-51eb-aa81-a8e80422a68f | note | Inspection: By (Role Key) - SP/QE
| checkpoint | 4.3 - Bedding
9b7be36a-4d29-5381-b326-3ae29434cf20 | note | Inspection Point: Quality Control Activity - Bedding minimum 75mm compacted material
9b117924-f2fc-5dec-8892-8369b9c6f17b | note | Acceptance Criteria - Bedding to comply with requirements
d1fa6168-e255-52d7-bf49-6cea3eb08aa3 | note | Verifying Document - Photo
5778ed11-0cce-56c3-9d8a-7204219c1b49 | note | Frequency - During installation
ad94ef2e-1f9f-5aa2-9c15-ac75da3dbd35 | note | Inspection Type (Visual, other) - Visual, Measurement Check
1c643703-4893-5e4b-8924-1438ac282e91 | note | Inspection: Key - C
29b35aa2-e61d-5d02-b15d-535273317b10 | note | Inspection: By (Role Key) - QE/SP
| checkpoint | 4.4 - Chamber Installation
8fa3e48e-fcea-5e18-886f-6da1c9b22b6f | note | Inspection Point: Quality Control Activity - Chambers installed true to the design level
8e7e29a8-d04e-5c66-bdde-cdcfa0202099 | note | Acceptance Criteria - Final levels are in accordance with the drawings or within tolerance and agreed with the Engineer
49e59276-ffec-5798-a96f-f90e3827b361 | note | Verifying Document - Photos
005763f4-aba0-56b3-a823-bf70212a06bf | note | Frequency - During installation
30da20b8-85ab-5e07-a4b2-9bf402e9e1d3 | note | Inspection Type (Visual, other) - Visual, instrumental
d9651a06-241a-5264-ab38-76add105648f | note | Inspection: Key - C
2a0a209f-be3f-55f6-af65-c6dc81a5bf16 | note | Inspection: By (Role Key) - SP/QE
| checkpoint | 4.5 - Benching
5004ff03-0b46-5519-90ec-18dfd4bc3858 | note | Inspection Point: Quality Control Activity - Benching concrete shall have a crushing strength of 20MPa at 28 days. All benching and sloping surfaces on manhole floor shall be rendered in 20mm thick 1:3 mortar
b76e848b-6fc8-53fe-bcec-d3782e58347c | note | ○ Benching shape to have smooth transitions at bends and junctions
4860b592-5293-5da4-89df-6e9e0441aa52 | note | Acceptance Criteria - Benching built up to the specifications
d9e719b5-8a10-5050-80be-c503d0085b3d | note | Verifying Document - Photos
98c10eea-6d73-520e-8b13-c92526597efc | note | Frequency - During benching contruction
7ffb771d-3810-5af2-9c03-8af3e7babc23 | note | Inspection Type (Visual, other) - Visual, measurement check
c1344bc6-bc2b-57b8-a74b-682bdc3b19c4 | note | Inspection: Key - H
5308cc01-12e1-5a76-ac3f-8b34b0dec9c0 | note | Inspection: By (Role Key) - SP/QE/CR
| signoff | HOLD POINT
| checkpoint | 4.6 - Backfill and Compact
ffb18f72-2e7e-5229-bca1-ccac49a0e930 | note | Inspection Point: Quality Control Activity - Backfill in 200mm layers of compacted material
61b74aea-25a8-528e-8edb-dd8b128c052b | note | ○ Compaction testing one test every two layers as required
855cf8a1-5bac-59dd-a8b6-c89df0dab385 | note | Acceptance Criteria - 95% MDD in roads, paths, and pavements
d609b4d9-4a9b-5bcb-8c39-5497aa3d0669 | note | Verifying Document - Photos, Compaction test results
90518fb7-7b58-5a35-8957-c77127c90408 | note | Frequency - During Installation
7317b953-c5df-509e-a83c-abb29536cd4c | note | Inspection Type (Visual, other) - Visual, On Site test
1561bf6a-ce61-5c95-82cc-e72f9bf8526b | note | Inspection: Key - H
f69cb71b-3f9e-5b17-81f0-ec5d5b8ebfa3 | note | Inspection: By (Role Key) - SP/QE
| signoff | HOLD POINT
| section | SECTION 5 - FINAL INSPECTION AND HANDOVER
| checkpoint | 5.1 - Leak Testing
85871b29-7e2b-53af-9055-c7a5939fe7d0 | note | Inspection Point: Quality Control Activity - Manholes to be water tested up to within 150mm of the concrete lid level.
02dfb382-218b-5265-bec7-14042d01f6ed | note | Acceptance Criteria - The amount of water leakage from chamber under test shall not exceed 1/300 of the volume of the chamber during a 30 minute period
836e8631-b378-5042-960e-d5888427bf20 | note | Verifying Document - Photos, test records
c1ff320f-a793-52da-bd22-55f1a9c9a5e9 | note | Frequency - For every manhole
91dc5f95-d488-5bab-b5fd-a08345a6ea50 | note | Inspection Type (Visual, other) - Test, visual
57774758-f600-59c4-9e2d-3088a547c5b5 | note | Inspection: Key - H
8000a74d-ae72-5c21-b7de-fcf1d76b22e7 | note | Inspection: By (Role Key) - SP/QE/PE/CR
| signoff | HOLD POINT
| checkpoint | 5.2 - As built
0d089f0a-1f73-554b-8f41-6abc17237ee8 | note | Acceptance Criteria - Engineer Approval
924fa07a-a0d7-5c8c-8d10-a3ab51d55132 | note | Verifying Document - QA records
b1045636-68e5-5afa-8560-f907829ad853 | note | Frequency - at completion
282d2a98-a19f-52ba-b676-62f80d90217b | note | Inspection Type (Visual, other) - Asbuilt drawings
5e8866e2-f29d-5476-ac1e-55fdbc99ce68 | note | Inspection: Key - H
c63bbce1-2a68-52e1-b8dd-26f7d75f1068 | note | Inspection: By (Role Key) - PE/PM/SV
| signoff | HOLD POINT
| checklist | ITP-4003 - DN750 WC main WCMH-5 to WCMH-4 | itp | ITP-4003 - DN750 WC main WCMH-5 to WCMH-4 | 59b9401e-e477-4206-8eed-a125cb4292ae
| section | SECTION 3 - RECEIVING INSPECTIONS
| checkpoint | 3.1 - Material Delivery
fd6945ee-161e-528f-a7ba-18671463b1f4 | note | Inspection Point: Quality Control Activity - Inspect for damage and wear, Confirm items are correct as per drawings and Specifications
30500143-ffbe-5e6f-b61b-3f02c8de8a97 | note | Acceptance Criteria - Pipes shall be DN600 Class 4 RCRRJ
25a84a91-46b6-5297-bd5a-7c2e359cc295 | note | ○ Items are approved as per contract specification
872e47c9-deec-5ace-9b6e-bf29fab0b698 | note | ○ DCC approved
4cbd8926-a97c-5e69-9c28-12c208e9b94e | note | Verifying Document - Photos, delivery docket, MDD results for backfill materials (if required)
c638e561-52bc-5cc6-940d-97426bc3270f | note | Frequency - On Delivery
32412e66-96ea-5503-a4bd-fd012de17507 | note | Inspection Type (Visual, other) - Visual
0e3de0f6-fbf7-5689-9c59-a9a488b72514 | note | Inspection: Key - C
37a5d4d0-ae36-5598-b6ae-d0c128a6a6e6 | note | Inspection: By (Role Key) - SV/QE
| checkpoint | 3.2 - Set out
1d025ba7-84f8-5a68-80aa-f546c3e476fe | note | Inspection Point: Quality Control Activity - Set out completed by an approved surveyor marked allignment
a18a71b7-f5b3-55da-9a42-315f8a3fb085 | note | Acceptance Criteria - Allignment set out matches drawings or aggreed by the Engineer
c438f1ca-ca49-573a-a728-98d9b23df8fc | note | Verifying Document - Survey marks, photos
145385a7-3c62-5568-8c18-f5d74aebe421 | note | Frequency - Prior to commencement of works
b53b2af4-9ec3-5597-820f-1b1844e48c44 | note | Inspection Type (Visual, other) - Visual, Instrumental
907002a6-abe7-5234-a401-c5411967045c | note | Inspection: Key - H
5170a963-0ce3-5629-898f-7773978a3e51 | note | Inspection: By (Role Key) - SV/SP/QE/PE
| signoff | HOLD POINT
| section | SECTION 4 - IN-PROCESS INSPECTIONS
| checkpoint | 4.1 - Trench Excavation
876c492a-569c-5cad-af49-b1f4a14d0982 | note | Inspection Point: Quality Control Activity - Excavate to achieve required depth to invert as per C4200
f726ae62-5fc4-55d1-b510-9bdece611fba | note | ○ Trench width to allow for 300mm seperation between springline of the pipe and trench wall or an adjacent pipe
2e968e45-52fd-5eca-91d4-f9f0f9cdbd9b | note | ○ Floor of Trench to be even across width and length
3b577317-9241-5e89-8610-01d9fe1b0b35 | note | Acceptance Criteria - Allow 100mm for bedding
06794c26-132e-5aee-8dc1-d514aead8a3c | note | ○ Allow for minimum cover of 750mm.
57e0e33f-08ae-5ce0-84ca-228614e7049f | note | Verifying Document - Photos, measurement checks
1cb1a6e3-29a6-59ac-8117-1e241067659e | note | Frequency - During Installation
13749fcb-6ec8-5dcb-8f20-5c27a7ca0a79 | note | Inspection Type (Visual, other) - Visual
58cbc2ee-2495-5961-9a85-2385c3b78aff | note | Inspection: Key - C
1bf9adb5-fc40-5a40-af5c-8530adc1e7da | note | Inspection: By (Role Key) - SP/QE/CM
| checkpoint | 4.2 - Geotextile
a01e27da-3e23-5b0d-8e39-cde180bf65b8 | note | Inspection Point: Quality Control Activity - Install Bidim A29 or approved equivalient around bedding, haunch, overlay zone and trench fill up to the subbase.
a4e4ff19-b865-52d0-a713-267a182ce132 | note | Acceptance Criteria - Geotextile not damged during pipe installation and backfilling
0864ed3d-5d0b-55f7-9d86-da2dedd9d448 | note | Verifying Document - photos
f865fed2-061a-549e-b998-657a685eb152 | note | Frequency - During Installation
9d442d0d-e9cf-5a89-a5f9-0bccfa4ca9f2 | note | Inspection Type (Visual, other) - Visual
3c852204-1ad1-5825-8b23-c8338d5c19b8 | note | Inspection: Key - C
fb694baf-9510-5682-9be8-cd6c79bb6041 | note | Inspection: By (Role Key) - SP/QE
| checkpoint | 4.3 - Foundation
6c32f554-45a8-5982-b71d-dca3d103fcb3 | note | Inspection Point: Quality Control Activity - Scala tests on base of trench
5ec6f3c9-66ec-5521-8443-fe515516bc0d | note | Acceptance Criteria - minimum of 2 blows per 100mm
3fe36b72-c1c3-538d-959b-e45ea6bc8401 | note | Verifying Document - test results
ed36a9ca-a1bc-528e-aa48-9e7e4a9ae34d | note | Frequency - During installation, per 20m
44ef94b6-f5d4-554e-bbf4-5b0310580a0f | note | Inspection Type (Visual, other) - Visual, On site test
d4f55b18-cbcd-5461-aa31-b605fd390874 | note | Inspection: Key - H
bedcb70b-88f8-579c-8759-7988b37c23f7 | note | Inspection: By (Role Key) - SP/QE
| signoff | HOLD POINT
| checkpoint | 4.4 - Install Pipe
01774be6-7dc1-5c81-b86a-e4bf082451e0 | note | Inspection Point: Quality Control Activity - Pipe installed to grade as per drawing C4200
e3885ae4-8036-572c-abc6-f8802c2bd193 | note | Acceptance Criteria - Pipe not damaged during installation
794e737a-2ee8-5ac6-b649-813a5ceab51b | note | ○ Pipe installed to grade within tolerances specification GP 3.1.8
005e0fb5-bc55-5c1d-9353-eb2af465a1d4 | note | Verifying Document - Photos, Grade check sheet, Survey of position for asbuilt
5f6b8ad9-7595-5489-b523-045227f15a4a | note | Frequency - During installation
0fb163fd-01ae-5e8c-838f-52ef56dbdb84 | note | Inspection Type (Visual, other) - Visual, instrumental
be2be8c5-4579-5558-b01e-23e65b49783d | note | Inspection: Key - C
218d0fd8-0a90-5908-b041-ef93fb4df668 | note | Inspection: By (Role Key) - SP/QE
| checkpoint | 4.5 - Embedment zone
635df6bc-2169-5075-9217-3ee8d00a7d28 | note | Inspection Point: Quality Control Activity - Embedment material shall be AP20 or approved by the Engineer in writing
bbd42304-d1c1-5a05-bd03-efb6f7749b8a | note | Acceptance Criteria - min 100mm bedding
9e8031c2-4766-5977-a396-fead57d2b48a | note | ○ 150mm overlay
d8b9e474-727f-5ee5-8691-0bb3131de80c | note | Verifying Document - Photos
2696b515-34d1-5d3e-be54-4061b38c961f | note | Frequency - During Installation
3259ebe2-d38a-531c-824a-f1f258940d2d | note | Inspection Type (Visual, other) - Visual, measurement check
18dbfcc2-4a89-541f-9ea3-9e611a4e10c3 | note | Inspection: Key - C
de3b6d4a-fa11-5e69-9ce7-aae5376e159d | note | Inspection: By (Role Key) - SP/QE
| checkpoint | 4.6 - Bacfill and Compact
5acfd24f-c4b3-5a56-8afa-017a6cd382ce | note | Inspection Point: Quality Control Activity - Backfill in 200mm layers of compacted material
96405d46-6e1a-5c33-86d3-d93a5fbd2dde | note | ○ Compaction testing one test every two layers as required
58f08d5f-b76a-5af5-947b-54470eef25ce | note | ○ Conductive signal strip to be laid at 300mm above pipe
3f878185-066f-5194-88ab-ea20381b2f1d | note | Acceptance Criteria - 95% MDD in roads, paths, and pavements
1825faef-0a26-55b7-83b1-c69af9b159fa | note | Verifying Document - Photos, Compaction test results
7dc98ecd-1581-5e8f-b7a3-4a0ab66d8a18 | note | Frequency - During Installation, compaction testing per 50m of pipeline or per straight section of pipeline
65acd8ea-4631-5acb-814d-cd26fd5fc915 | note | Inspection Type (Visual, other) - Visual, On Site test
75a8bf67-1ef5-5ac7-87d7-505aacc93b2c | note | Inspection: Key - H
6de8bec6-504c-512a-a402-c398fbe2f3d5 | note | Inspection: By (Role Key) - SP/QE
| signoff | HOLD POINT
| checkpoint | 4.7 - Reinstatement - 326 Floor
a295dbdf-f5c5-57b8-abad-47ad06c1750e | note | Inspection Point: Quality Control Activity - DPM inplace
2862edf5-2db4-5161-af16-02037e63d3db | note | ○ HD12 @ 250 ctrs, 600mm lond embedded 150mm.
c2eae84e-cf7f-5573-8188-e05f9036bd2d | note | ○ Place SE72 mesh
f4e8f871-6d7d-53b6-a386-2d5612c2f3c7 | note | ○ Follow detail 33 at change in floor level.
22232a40-5b53-5031-ac17-40d2adb1b3b9 | note | ○ Pour 25mPa concrete
9f996c43-d9ed-5476-aec3-28a5f18fc222 | note | Acceptance Criteria - steel installed and poured in accordance with drawings.
8d82f5f5-502e-5569-8d79-4215f13f4ff7 | note | Verifying Document - Site Report
33f9463a-4f3b-5e6e-80a4-b963d1b77ebe | note | Frequency - During installation, prior to pours.
0068c42a-cd0b-5797-9f6f-913d15857ba0 | note | Inspection Type (Visual, other) - Engineers Inspection
c4c14247-943a-507e-93e2-f142ac5ebfb6 | note | Inspection: Key - H, I
822b3fbc-b64b-5a0a-a620-cdccfad0ecd9 | note | Inspection: By (Role Key) - CR/PE
| signoff | HOLD POINT
| checkpoint | 4.8 - Reinstatement - Carrigeway
0454e4f3-a6bb-5eb3-9cb1-6e32d01bc76f | note | Inspection Point: Quality Control Activity - Match existing pavement thickness or minimum of 35mm.
c0997346-9187-573d-98ed-e1c17c1580c9 | note | ○ Minimum depth of 250mm 28 day strength 20MPa concrete, R20 steel installed at 500mm ctrs, 250mm embedment and 250mm into excavation, placement of 665 steel mesh, coarse broom finish.
7c216b16-68dd-5c02-a321-088a00852a2d | note | ○ Place a tack coat.
3332c608-fba8-53cb-a423-037a4ca8317c | note | ○ Mix to be NZTA M/10: AC10
744b5eba-aa8f-510b-b0fd-80b16b6768a1 | note | ○ Bandage seal
4cdf20e6-b003-59ac-8683-ba9e7b3d1bf7 | note | Acceptance Criteria - Asphalt installed as per the design
0c1f3c53-d3b5-5ff5-978a-d5065bb3b9fc | note | Verifying Document - Photos
53de95be-dab4-537e-a393-20ce3940355b | note | Frequency - During Installation
af25c8b2-f749-5ffe-b391-8ffab5b24bc7 | note | Inspection Type (Visual, other) - Visual, Prepour inspection
3c14fdf9-2906-5c67-afe6-32783e8036b9 | note | Inspection: Key - C
e8b6dcb4-5bf8-5288-920b-6062fdbb08d8 | note | Inspection: By (Role Key) - PE/SP/QE
| checkpoint | 4.9 - Reinstatement - Footpath
e46bfda0-573f-59d7-9f54-3f76e1407163 | note | Inspection Point: Quality Control Activity - Match existing pavement thickness or minimum of 35mm.
aed541f3-beb1-514b-ac45-2eba1cc022b6 | note | ○ Minimum 75mm of basecourse.
89ebab7e-6bf4-5912-bfb3-99dec716524d | note | ○ Place a tack coat of 0.2-0.5 L/m².
42bdc910-cb80-5177-91c9-19e8efeb9c4d | note | ○ Mix to be DG7 Asphaltic Concrete.
233f666c-b13f-59a5-a883-0605d8cc8c35 | note | ○ Bandage Seal
b5f27022-def1-5231-95d0-b1b3a0745b0e | note | Acceptance Criteria - Asphalt installed as per the design
7fd12387-8500-582e-a978-7d3a98730a27 | note | Verifying Document - Photos
fa269829-0213-5669-8d90-62127574b592 | note | Frequency - During Installation
263b5951-6e65-50e3-9ee0-d7e84ddb5191 | note | Inspection Type (Visual, other) - Visual
10b1e1a7-e5f2-59cb-976e-370d244b5a26 | note | Inspection: Key - C
78fdc4df-2e7e-5266-9410-1dbef20daf8c | note | Inspection: By (Role Key) - PE/SP/QE
| checkpoint | 4.10 - Reinstatement - Kerb and Channel
d3db036a-414d-56f3-8190-bb94063c88d3 | note | Inspection Point: Quality Control Activity - Length a minimum of 1m.
7e58fa5a-faf9-5efb-808a-8e6266749f04 | note | ○ Match existing grade.
79702115-329c-5bf1-9ba0-facd94d56812 | note | ○ Concrete strength 20MPa
1cb2de81-0dec-5ae3-8eb4-769672088b54 | note | ○ Vertical joints at 3m intervals.
12625a68-117b-504a-8fc1-261376625ee4 | note | Acceptance Criteria - Tolerances for kerb and channel and paving edge beam shall be +5mm vertically and E16+3mm horizontally. The deviation from a 4m straight edge shall not exceed 3mm
49efb441-9535-5cf3-b040-30f18d30c0e1 | note | Verifying Document - Photos
0344cfad-cbc9-5e0d-96b3-ab1db9c4a5c0 | note | Inspection Type (Visual, other) - Visual, Pre Pour inspection
31e27d77-405e-575e-82cf-76c58adad59c | note | Inspection: Key - C
b8196527-75df-56e0-a1a1-b055de6ac206 | note | Inspection: By (Role Key) - PE/SP/QE
| section | SECTION 5 - FINAL INSPECTION AND HANDOVER
| checkpoint | 5.1 - CCTV
626aa881-27ba-59a2-82b1-9365e8b3f93c | note | Inspection Point: Quality Control Activity - CCTV inspection to confirm pipeline conforms with specification
56d851cd-d52e-5b44-9782-c820003a2728 | note | Acceptance Criteria - Pipeline will fail is any of the following is visible:
d62af583-43b3-5825-88a9-9e19923c3f2f | note | ○ Pipe misalignment or deformation more than 5% of the pipe diameter
9c38fdfb-3666-52f4-87a9-9724124be89f | note | ○ Dips or ponding of water inside the pipe
1575af2c-bf99-564a-b95a-643631d0d42d | note | ○ Defects such as open joints, potruding laterals, cracked barrels, or similar
b2ac9c90-0f8d-544c-9b2a-1cf6e61120b8 | note | Verifying Document - Test Records, CCTV footage
1fc07a43-648f-5765-bb1a-fbb32620c000 | note | Frequency - Every section of pipe completed
d4ffe9d1-9cc4-5358-bb32-940fc63a731f | note | Inspection Type (Visual, other) - On-Site Test
670e48e7-7035-584d-a4b7-539ce0478048 | note | Inspection: Key - H
a74729c6-6813-560c-a502-dda72f882b23 | note | Inspection: By (Role Key) - SP/QE/CM/CR
| signoff | HOLD POINT
| checkpoint | 5.2 - Leak Testing
d6681634-7294-527f-8e31-05ec4baf8649 | note | Inspection Point: Quality Control Activity - Tested in the presence of the Engineer or their representative testing in accordance with AS/NZS 2566.2 Section 6.4
3b8806c2-3ac1-5058-a26c-02271ab79ba5 | note | Acceptance Criteria - Engineer Approval
fc9740a0-2050-5c5f-9784-b07cd6cd5e42 | note | Verifying Document - Test Records
5db85558-8b9d-57d0-a926-b7bc5887cb60 | note | Frequency - Every section of pipe installed
147407a2-a6a2-5132-8b77-2855588ff1ac | note | Inspection Type (Visual, other) - On-Site Test
bc0bfb46-5276-528d-89cb-6ee202faf965 | note | Inspection: Key - H
f8fad0e0-8e0e-5707-b7a5-654fe9bc88cb | note | Inspection: By (Role Key) - SP/QE/CM/CR
| signoff | HOLD POINT
| checkpoint | 5.3 - Red pen markups
b7859528-d948-54ce-aeb9-29d8eb672c80 | note | Inspection Point: Quality Control Activity - Complete mark up of any changes from supplied drawings
bc228714-ca29-537f-9188-731a14e8f7ca | note | Frequency - After completion of pipe section
293a5856-2300-56e3-afef-d9469d25f14f | note | Inspection Type (Visual, other) -
f5f0fc6a-51b8-581e-a72d-7f77e4e2bd84 | note | Inspection: By (Role Key) - SP/QE/CM
| checkpoint | 5.4 - As built
a080f463-13fb-547e-ab99-95e877eb407a | note | Acceptance Criteria - Engineer Approval
7629ddab-d5e6-5881-8c26-f38602705d7b | note | Verifying Document - QA records
7a7d1b44-0f34-5b2c-85bb-636589345f36 | note | Frequency - at completion
179452ed-7c4b-5bca-bf88-28a26a8892d8 | note | Inspection Type (Visual, other) - Asbuilt drawings
3ff4bf4d-396e-5457-af8d-359b6a03b7fc | note | Inspection: Key - H
a7da4251-21b4-57ce-b991-01fb006cb615 | note | Inspection: By (Role Key) - PE/PM/SV
| signoff | HOLD POINT