## General
Modify template as required prior to use, e.g. to accommodate project or customer specific requirements, then delete this instructional text when complete.
SECTION 1 – GENERAL DETAILS
Project Name: | Bath Street Stormwater Renewal |  |  |  |  | Inspection Key Use in sections 3, 4 and 5. |  | Responsibilities Use in sections 3, 4 and 5.
Project Number: | 561467 |  |  |  |  | A | Action | Role Key |  | Name | Signature/ Initial
Customer: | Dunedin City Council |  |  |  |  | B | Report by Breach | CM | Construction Manager
Contract Number: | 9240 |  |  |  |  | C | Check | CR | Cust. Representative
Area/ Sub-System: | Bath Street Stormwater Renewal |  | Lot ID Number: |  |  | D | Dimension Inspection | IP | Inspection Personnel
[6 empty] | E | Examine | MC | Material Controller
ITP Number: | ITP-1004 |  | Version: | 2 |  | H | Hold Point | OP | Operations Manager
ITP Description: | Installation of Manhole- WCMH-2B |  |  |  |  | I | Inspection | PM | Project Manager
Discipline: | Utilities |  |  |  |  | M | Monitor on Random Basis | PS | Project Supervisor
Specification: | DCC code of subdivision and Project Specification |  |  |  |  | O | Operation | QE | Quality Engineer
[6 empty] | R | Review | QM | QA Manager
Drawings: | C4200 |  |  |  |  | S | Subcontractor | SP | Supervisor
[6 empty] | V | Visual Verification | ST | Superintendent
Prepared By: (Name) | Calisa Mcleary / Kaps Mayekar |  | Date: | 2024-07-05 |  | W | Witness Point | SV | Surveyor
Quality Specified: | [7 empty] | WS | Welding Supervisor
SECTION 2 – SIGNATURES – CLOSE-OUT & APPROVAL
ITP Close-Out by Downer |  | Name: |  |  | Signature: |  |  |  |  | Date:
Downer Approval |  | Name: |  |  | Signature: |  |  |  |  | Date:
Customer Approval |  | Name: |  |  | Signature: |  |  |  |  | Date:

## Receiving Inspection
SECTION 3 – RECEIVING INSPECTIONS Insert additional or delete unused rows as required. Include reference to specification.
Item No. | Activity/ Task Description | Inspection Point: Quality Control Activity | Acceptance Criteria | Verifying Document | Frequency | Inspection Type (Visual, other) | Inspection
[7 empty] | Key | By (Role Key)
3.1 | Material Delivery | Inspect for damage and wear, Confirm items are correct as per drawings and Specifications | - Items are approved as per contract specification - DCC approved | Photos, delivery docket | On Delivery | Visual | C | SP/QE
3.2 | Set out | Set out completed by an approved surveyor marked allignment | - Allignment set out matches drawing C4200-2 or aggreed with the Engineer | Survey marks, photos | Prior to commencement of works | Survey | H | SV/SP/QE
3.3 | Backfill / Bedding Material | Approved Material, AP20 as per DCC code of subdivision 10329. | -As per DCC code of subdiviison 10329 | Delivery dockets, photos | On Delivery | Visual | C | SP/QE
3.4
3.5
3.6

## In Process Inspections
SECTION 4 – IN-PROCESS INSPECTIONS Insert additional or delete unused rows as required. Include reference to specification.
Item No. | Activity/ Task Description | Inspection Point: Quality Control Activity | Acceptance Criteria | Verifying Document | Frequency | Inspection Type (Visual, other) | Inspection
[7 empty] | Key | By (Role Key)
4.1 | Trench Excavation | - Excavate to required depth to invert as per C4200 - Trench width to allow for 300mm seperation between springline of the pipe and trench wall or an adjacent pipe - Floor of trench to be even across width and length | - As per 561467-TW-04-DRW-001 | Photos, measurement checks | During Installation | Visual | V | SP/QE
4.2 | Foundation | Scala tests on base of trench | - Minimum of 2 blows per 100mm | Test results | During installation, per 20m | Visual, On site test | H | SP/QE
4.3 | Bedding | Bedding minimum 150mm compacted material | - Bedding to comply with requirements | Photo | During installation | Visual, Measurement Check | C | QE/SP
4.4 | MH Installation | MHs to be installed true to the design level | -Final levels are in accordance with the C4200 or within tolerance and agreed with the Engineer | Photos, As-built | During installation | Survey | H | SP/QE
4.5 | Benching | Benching concrete shall have a crushing strength of 20MPa at 28 days. Benching shape to have smooth transitions at bends and junctions | - Benching built up to the specifications | Photos | During benching contruction | Visual, Test Results | H | SP/QE
4.6 | Backfill and Compact | - Backfill in 200mm layers of compacted material - Compaction testing one test every two layers as required | - 95% MDD in roads, paths, and pavements | Photos, Compaction test results | During Installation | Visual, On Site test | H | SP/QE

## Final Inspection and Handover
SECTION 5 – FINAL INSPECTION AND HANDOVER Insert additional or delete unused rows as required. Include reference to specification.
Item No. | Activity/ Task Description | Inspection Point: Quality Control Activity | Acceptance Criteria | Verifying Document | Frequency | Inspection Type (Visual, other) | Inspection
[7 empty] | Key | By (Role Key)
5.1 | Leak Testing | Manholes to be water tested up to within 150mm of the concrete lid level. | The amount of water leakage from chamber under test shall not exceed 1/300 of the volume of the chamber during a 30 minute period | Photos, test records | For every manhole | Test, visual | H | SP/QE/CM/CR
5.2 | Red pen markups | Complete mark up of any changes from project drawings | Signed ITP | Red pen markup drawings | After installation of FSMH | Document | H | SP/QE/CM
5.3
5.4
5.5
5.6
5.7
5.8
5.9
5.10
SECTION 6 – COMMENTS
|  |  | Customer Release Granted: | ☐ Yes | ☐ No | Date:
Certificate Number: