## res
type | name | values | prefix | postfix | usage count | user addable | template name | Resource ID
checklist | ITP-191-CIV-SSB-Lighting-MTM Carpark | itp |  |  |  |  | ITP-191-CIV-SSB-Lighting-MTM Carpark Rev 0
section | Referenced Documentation
checkpoint | Referenced Documentation
label | Document Title: ITP-191-CIV-SSB-Lighting-MTM Carpark
label | ITP Description: SSB-Lighting-MTM Carpark
label | Discipline (e.g. CIV/STR/RAIL): 191-CIV
label | Revision Number: 0
label | Revision Date: 21/08/2024
label | ITP created by: VM
label | ITP approved for use by: VM
label | 1.1 Non Dependent
label | Reference: L1-CHE-STD-059
label | 1.2 Non Dependent
label | Reference: L1-CHE-STD-035
label | 1.3 Non Dependent
label | Reference: L1-CHE-SPE-155
label | 1.4 Non Dependent
label | Reference: AS/NZS 3000
label | 1.5 Non Dependent
label | Reference: AS/NZS 1158.3.1 (2020)
label | 1.6 Non Dependent
label | Reference: A9819
section | Preliminaries-Materials
checkpoint | 2.1 Obtain and review manufacturer documentations for the supply of materials
label | REFERENCE: L1-CHE-STD-035, AS/NZS 2053, IFC Drawings
label | – – – – – – – – – – – – – – – – –
label | ACCEPTANCE CRITERIA: Materials comply with MTM Engineering stadard Lighting and Powerrelevant specifications.
label | ○ All materials shall comply with the standards and specifications shown on the drawings. All structural steel, associated components and welding consumables shall be manufactured by companies that hold quality systems certification to AS/NZS ISO 9001.
textbox | * Enter: Teambinder Material Approval number
label | – – – – – – – – – – – – – – – – –
label | METHOD: Document Review
label | – – – – – – – – – – – – – – – – –
label | FREQUENCY: Each Lot
label | – – – – – – – – – – – – – – – – –
label | CATEGORY: HP
label | – – – – – – – – – – – – – – – – –
label | RESPONSIBILITY: Nominated Authority
label | – – – – – – – – – – – – – – – – –
label | VERIFYING DOCUMENTS: ConQA Hold Point Release
date | Date Completed:
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 2.2 Concrete
label | REFERENCE: IFC Drawings
label | – – – – – – – – – – – – – – – – –
label | ACCEPTANCE CRITERIA: Concrete complies mix complies with VR 400/40.
label | ○ Pile Concrete Grade at 28 days shall be 40 Mpa.
textbox | * Enter: Teambinder Material Approval number
label | – – – – – – – – – – – – – – – – –
label | METHOD: Document Review
label | – – – – – – – – – – – – – – – – –
label | FREQUENCY: Each Lot
label | – – – – – – – – – – – – – – – – –
label | CATEGORY: HP
label | – – – – – – – – – – – – – – – – –
label | RESPONSIBILITY: Nominated Authority
label | – – – – – – – – – – – – – – – – –
label | VERIFYING DOCUMENTS: ConQA Hold Point Release
date | Date Completed:
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 2.3 Reinforcement (Cage)
label | REFERENCE: IFC Drawings VR 611.05
label | – – – – – – – – – – – – – – – – –
label | ACCEPTANCE CRITERIA: Reinforcement cages shall be according to IFC Drawings
label | ○ Reinforcement complies with VicRoads Section 611.05 (a) & (b), and AS4671 (ACRS)
textbox | * Enter: Teambinder Material Approval number
label | – – – – – – – – – – – – – – – – –
label | METHOD: Document Review
label | – – – – – – – – – – – – – – – – –
label | FREQUENCY: Each Lot
label | – – – – – – – – – – – – – – – – –
label | CATEGORY: HP
label | – – – – – – – – – – – – – – – – –
label | RESPONSIBILITY: Nominated Authority
label | – – – – – – – – – – – – – – – – –
label | VERIFYING DOCUMENTS: ConQA Hold Point Release
date | Date Completed:
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 2.4 HD Bolts assemblies
label | REFERENCE: A9819, VR 630.20
label | – – – – – – – – – – – – – – – – –
label | ACCEPTANCE CRITERIA: HD bolt assemblies as per IFC drawings
label | ○ All HD bolts are grade 4.6/S, galvanised
label | ○ All nuts and washers to be galvanised
textbox | * Enter: Teambinder Material Approval number
label | – – – – – – – – – – – – – – – – –
label | METHOD: Document Review
label | – – – – – – – – – – – – – – – – –
label | FREQUENCY: Each Lot
label | – – – – – – – – – – – – – – – – –
label | CATEGORY:
label | – – – – – – – – – – – – – – – – –
label | RESPONSIBILITY:
label | – – – – – – – – – – – – – – – – –
label | VERIFYING DOCUMENTS:
date | Date Completed:
checkpoint | 2.5 Inspect supplied items upon delivery
label | REFERENCE: QMP, L1-CHE-SPE-155
label | – – – – – – – – – – – – – – – – –
label | ACCEPTANCE CRITERIA: Supplied items are to correct spec, class, size and undamaged
label | ○ Luminaires: At the time of delivery, the supplier shall provide three hard copies of the following:
label | – Installation Instruction Manual
label | – Operation Instruction Manual
label | – Storage, handling, loading and off–loading instructions
label | – Test Certificates
label | – Warranty Information
label | – – – – – – – – – – – – – – – – –
label | METHOD: Visual /Site Inspection & Document Review
label | – – – – – – – – – – – – – – – – –
label | FREQUENCY: Each Lot
label | – – – – – – – – – – – – – – – – –
label | CATEGORY: HP*
label | – – – – – – – – – – – – – – – – –
label | RESPONSIBILITY: SE/PE/SPE
label | – – – – – – – – – – – – – – – – –
label | VERIFYING DOCUMENTS: This ITP, Attach records required
date | Date Completed:
section | Preliminaries-Related Works
checkpoint | 3.1 Conduit & pit installation
label | REFERENCE: L1-CHE-STD-035, IFC Drawings
label | – – – – – – – – – – – – – – – – –
label | ACCEPTANCE CRITERIA: Conduit and Pit Installation works are to be recorded under ITP-183-CIV-SSB-Conduits and Pits-MTM Carpark lighting in addition to Subcontractors Checklist.
label | – – – – – – – – – – – – – – – – –
label | METHOD: Document Review
label | – – – – – – – – – – – – – – – – –
label | FREQUENCY: Each Lot
label | – – – – – – – – – – – – – – – – –
label | CATEGORY: IP
label | – – – – – – – – – – – – – – – – –
label | RESPONSIBILITY: SE/PE/SPE
label | – – – – – – – – – – – – – – – – –
label | VERIFYING DOCUMENTS: This ITP
date | Date Completed:
section | Pre-Construction Works
checkpoint | 4.1 Survey Set Out
label | REFERENCE: IFC Drawings,
label | – – – – – – – – – – – – – – – – –
label | ACCEPTANCE CRITERIA: Survey to set out position of piles.
label | Attach: Lot Map
label | – – – – – – – – – – – – – – – – –
label | METHOD: Visual, Documen Review
label | – – – – – – – – – – – – – – – – –
label | FREQUENCY: Each bore
label | – – – – – – – – – – – – – – – – –
label | CATEGORY: HP*
label | – – – – – – – – – – – – – – – – –
label | RESPONSIBILITY: SE/PE/SPE
label | – – – – – – – – – – – – – – – – –
label | VERIFYING DOCUMENTS: Attached Geotechnical Report, Attached Lot Map
date | Date Completed:
section | Construction
checkpoint | 5.1 Prepare the footing foundation (Excavation & levels)
label | REFERENCE: IFC Drawings, Manufacturer specifications
label | – – – – – – – – – – – – – – – – –
label | ACCEPTANCE CRITERIA: Check levels and diameter conform to manufacturer drawings depending on type of pole to be installed. Foundations to be installed as per manufacturer specification and requirements.
label | ○ Pile holes to be inspected by Geotechnical Engineer.
label | Attach: Geotechnical Report
label | – – – – – – – – – – – – – – – – –
label | METHOD: Visual, Document Review
label | – – – – – – – – – – – – – – – – –
label | FREQUENCY: Each bore
label | – – – – – – – – – – – – – – – – –
label | CATEGORY: IP
label | – – – – – – – – – – – – – – – – –
label | RESPONSIBILITY: SE/PE, Geotechnical Engineer
label | – – – – – – – – – – – – – – – – –
label | VERIFYING DOCUMENTS: Attached Geotechnical Report
date | Date Completed:
checkpoint | 5.2 Installation of reinforcement cage
label | REFERENCE: IFC Drawings, Manufacturer specifications A9819
label | – – – – – – – – – – – – – – – – –
label | ACCEPTANCE CRITERIA: cage shall have enough clearance to the bore to maintain coverage as per IFC.
label | ○ Spacers and supports placed at intervals no more than 2m
label | – – – – – – – – – – – – – – – – –
label | METHOD: Measure
label | – – – – – – – – – – – – – – – – –
label | FREQUENCY: Each bore
label | – – – – – – – – – – – – – – – – –
label | CATEGORY: IP
label | – – – – – – – – – – – – – – – – –
label | RESPONSIBILITY: SE/PE
label | – – – – – – – – – – – – – – – – –
label | VERIFYING DOCUMENTS: this ITP
date | Date Completed:
checkpoint | 5.3 Cast in items
label | REFERENCE: IFC Drawings
label | – – – – – – – – – – – – – – – – –
label | ACCEPTANCE CRITERIA: Cast in items (conduits, hold down bolts, etc.) are installed in correct orientation and position.
label | ○ Hold down bolts have enough projection out side of the pile to accommodate for grout and base plate installation.
label | – – – – – – – – – – – – – – – – –
label | METHOD: Measure
label | – – – – – – – – – – – – – – – – –
label | FREQUENCY: Each bore
label | – – – – – – – – – – – – – – – – –
label | CATEGORY: IP
label | – – – – – – – – – – – – – – – – –
label | RESPONSIBILITY: SE/PE
label | – – – – – – – – – – – – – – – – –
label | VERIFYING DOCUMENTS: This ITP
date | Date Completed:
checkpoint | 5.4 Pre-pour inspection
label | REFERENCE: IFC Drawings, MRPA Construction Management plan
label | – – – – – – – – – – – – – – – – –
label | ACCEPTANCE CRITERIA: Pre-pour inspection to be conducted. Check the reinforcement cage as per manufacturer spec and IFC.
label | ○ Cast in items (e.g. bolts and conduits) positions to be installed as per IFC drawings/manufacturer drawings. Projection of items to be installed as per IFC drawings. Position and projection to be confirmed during inspection.
label | – – – – – – – – – – – – – – – – –
label | METHOD: Measure
label | – – – – – – – – – – – – – – – – –
label | FREQUENCY: Each Lot
label | – – – – – – – – – – – – – – – – –
label | CATEGORY: HP
label | – – – – – – – – – – – – – – – – –
label | RESPONSIBILITY: Nominated Authority
label | – – – – – – – – – – – – – – – – –
label | VERIFYING DOCUMENTS: ThisITP
date | Date Completed:
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 5.5 Concrete placement and Compaction
label | REFERENCE: IFC Drawings, MRPA Construction Management
label | – – – – – – – – – – – – – – – – –
label | ACCEPTANCE CRITERIA: The temperature of concrete, measured immediately prior to placing, shall not be less than 10°C or greater than 32°C.
label | ○ All concrete batches are traceable.
label | ○ All concrete batches are from approved mix
label | ○ Concrete shall be placed through either a tremie pipe or concrete pump and not dropped freely from a height exceeding 2m.
label | ○ The initial discharge is pumped to waste until a consistent workable mix is discharged.
label | ○ The ends of the discharge pipe shall not be lifted off the base of the excavation until a 2m head is created, which shall be maintained until the completion of the pour.
label | Attach: Concrete Pour Record
label | Attach: Concrete Dockets
label | – – – – – – – – – – – – – – – – –
label | METHOD: Document Review
label | – – – – – – – – – – – – – – – – –
label | FREQUENCY: Each Lot
label | – – – – – – – – – – – – – – – – –
label | CATEGORY: HP*
label | – – – – – – – – – – – – – – – – –
label | RESPONSIBILITY: SE/PE
label | – – – – – – – – – – – – – – – – –
label | VERIFYING DOCUMENTS: This ITP, Attached Pour Records, Attached Dockets
date | Date Completed:
checkpoint | 5.6 Concrete Sampling
label | REFERENCE: IFC Drawings
label | – – – – – – – – – – – – – – – – –
label | ACCEPTANCE CRITERIA: Concrete cast in one continuous operation to be tested at a frequency as shown below:
label | ○ 0m³ to 10m³ = 1 sample
label | ○ 10m³ to 25m³ = 2 samples
label | ○ 25m³ to 50m³ = 3 samples
label | ○ 50m³ to 100m³ = 4 samples + 2 no. VPV cylinders.
label | – For each additional 50m³ and additional sample shall be taken.
label | – Where the time interval between the end of discharge of one truckload of concrete and the beginning of discharge of the next truckload exceeds 45 minutes, the minimum number of test samples shall be one (1) per truckload of concrete
label | – Each sample shall consist of 1 no. slump or spread test and 3 no. compressive strength cylinders minimum.
label | – Compressive strength cylinders = 1 no. 7 day strength, 2 no. 28 day strength.
label | Note: Additional cylinders may be required for other purposes such as early strength determination of adjacent piles.
label | Record: Required information on the Concrete Pour Record.
label | – – – – – – – – – – – – – – – – –
label | METHOD: Visual
label | – – – – – – – – – – – – – – – – –
label | FREQUENCY: Each lot
label | – – – – – – – – – – – – – – – – –
label | CATEGORY: IP
label | – – – – – – – – – – – – – – – – –
label | RESPONSIBILITY: SE/PE, Concrete Tester
label | – – – – – – – – – – – – – – – – –
label | VERIFYING DOCUMENTS: This ITP
date | Date Completed:
checkpoint | 5.7 Pile Integrity Testing
label | REFERENCE: VR 606.07 (a, d & e), AS2159 Clause 8.8, A9819
label | – – – – – – – – – – – – – – – – –
label | ACCEPTANCE CRITERIA: Pile integrity testing shall be conducted after the concrete strength has reached 25MPa but not less than 7 days from casting.
label | ○ Cross-sectional area = ≥95%
label | ○ If any test fails, all piles shall be tested.
label | Attach: Pile Integrity Test Report
label | – – – – – – – – – – – – – – – – –
label | METHOD: Document Review
label | – – – – – – – – – – – – – – – – –
label | FREQUENCY: Piles #1 - #6. Reduced to 1 test per 3 piles if the first 6 tests pass.
label | – – – – – – – – – – – – – – – – –
label | CATEGORY: IP
label | – – – – – – – – – – – – – – – – –
label | RESPONSIBILITY: Testing Consultant, SE/PE
label | – – – – – – – – – – – – – – – – –
label | VERIFYING DOCUMENTS: This ITP
date | Date Completed:
checkpoint | 5.8 Installation lighting pole bases & columns
label | REFERENCE: IFC Drawings, L1-CHE-STD-035
label | – – – – – – – – – – – – – – – – –
label | ACCEPTANCE CRITERIA: Free standing platform lighting poles shall be at earth potential as mounted in ground or on structure. Light fittings shall be earthed by the earth cable from
label | ○ Concrete and metallic poles at all new installations and station extensions that support low voltage equipment shall be earthed by an underground conductor that is connected to the earth at the origin from which the circuit is supplied in accordance with AS/NZS 3000.9.5.2
label | ○ Lighting installations shall be LED and comply with L1-CHE-SPE-155
label | ○ Car park poles shall be located as per IFC Drawings.
label | ○ Pole access hatches shall be orientated to allow unobstructed access.
label | ○ Level formed ground shall be at each pole for access by ladder or EWP.
label | – – – – – – – – – – – – – – – – –
label | METHOD: Visual /Site Inspection & Document Review
label | – – – – – – – – – – – – – – – – –
label | FREQUENCY: Per Pole
label | – – – – – – – – – – – – – – – – –
label | CATEGORY: IP
label | – – – – – – – – – – – – – – – – –
label | RESPONSIBILITY: SE/PE/SPE
label | – – – – – – – – – – – – – – – – –
label | VERIFYING DOCUMENTS: This ITP
date | Date Completed:
checkpoint | 5.9 Assembly of outreaches and luminaires
label | REFERENCE: L1-CHE-STD-035, IFC Drawings
label | – – – – – – – – – – – – – – – – –
label | ACCEPTANCE CRITERIA: Outreach bracket to be installed to the pole spigot using the clamping bolt assemble
label | ○ Bracket and luminaire to align at right angles to vehicle path on road
label | – – – – – – – – – – – – – – – – –
label | FREQUENCY: Per Pole
label | – – – – – – – – – – – – – – – – –
label | CATEGORY: IP
label | – – – – – – – – – – – – – – – – –
label | RESPONSIBILITY: SE/PE/SPE
label | – – – – – – – – – – – – – – – – –
label | VERIFYING DOCUMENTS: This ITP
date | Date Completed:
checkpoint | 5.10 Installation of lighting distribution cabinet
label | REFERENCE: L1-CHE-STD-035, IFC Drawings
label | – – – – – – – – – – – – – – – – –
label | ACCEPTANCE CRITERIA: The switchboard or distribution board shall be designed and manufactured from suitable materials appropriate to the location in accordance with AS/NZS 3439.1.
label | – – – – – – – – – – – – – – – – –
label | METHOD: Visual
label | – – – – – – – – – – – – – – – – –
label | FREQUENCY: Per lot
label | – – – – – – – – – – – – – – – – –
label | CATEGORY: IP
label | – – – – – – – – – – – – – – – – –
label | RESPONSIBILITY: SE/PE/SPE
label | – – – – – – – – – – – – – – – – –
label | VERIFYING DOCUMENTS: This ITP
date | Date Completed:
checkpoint | 5.11 Installation of cabling
label | REFERENCE: IFC Notes
label | – – – – – – – – – – – – – – – – –
label | ACCEPTANCE CRITERIA: All electrical cabling to be in accordance with the requirements of AS/NZS 3000: (Australian/New Zealand Wiring Rules)
label | ○ Each pole to be cables from the pole circuit breaker
label | – – – – – – – – – – – – – – – – –
label | METHOD: Visual & Document Review
label | – – – – – – – – – – – – – – – – –
label | FREQUENCY: Per Lot
label | – – – – – – – – – – – – – – – – –
label | CATEGORY: IP
label | – – – – – – – – – – – – – – – – –
label | RESPONSIBILITY: SE/PE/SPE
label | – – – – – – – – – – – – – – – – –
label | VERIFYING DOCUMENTS: Test Certificate, This ITP
date | Date Completed:
checkpoint | 5.12 Commissioning & testing
label | REFERENCE: L1-CHE-STD-035
label | – – – – – – – – – – – – – – – – –
label | ACCEPTANCE CRITERIA: Upon final acceptance, the Contractor shall switch on the lighting installation at the distribution cabinet in automatic mode, and record the time, date and meter reading for contractual, warranty and power supply purposes and supply this record to the Superintendent within 48 hours
label | – – – – – – – – – – – – – – – – –
label | METHOD: Commissioning & testing
label | – – – – – – – – – – – – – – – – –
label | FREQUENCY: Upon completion of each section
label | – – – – – – – – – – – – – – – – –
label | CATEGORY: HP*
label | – – – – – – – – – – – – – – – – –
label | RESPONSIBILITY: SE/PE/SPE, Services Engineer
label | – – – – – – – – – – – – – – – – –
label | VERIFYING DOCUMENTS: This ITP, Attach Certificate
date | Date Completed:
checkpoint | 5.13 Labelling of Assets
label | REFERENCE: L1-CHE-STD-035, MTM Standard
label | – – – – – – – – – – – – – – – – –
label | ACCEPTANCE CRITERIA: Labels fixed to poles as per MTM standard. Pole numbering
label | ○ Labelling of switchboards, distribution boards, circuit breakers, RCDs and all control devices shall be labelled as per Appendix B in MTM standard.
label | ○ Indelible Labelled srawings shall be permanently displayed at the point of supply. Permanent field markers shall clearly identify the extent of the EPZ locations.
label | – – – – – – – – – – – – – – – – –
label | METHOD: Visual /Site Inspection & Document Review
label | – – – – – – – – – – – – – – – – –
label | FREQUENCY: Per pole
label | – – – – – – – – – – – – – – – – –
label | CATEGORY: IP
label | – – – – – – – – – – – – – – – – –
label | RESPONSIBILITY: SE/PE/SPE
label | – – – – – – – – – – – – – – – – –
label | VERIFYING DOCUMENTS: This ITP
date | Date Completed:
checkpoint | 5.14 Grouting
label | REFERENCE: IFC Drawings A9819
label | – – – – – – – – – – – – – – – – –
label | ACCEPTANCE CRITERIA: Install 50mm Grout as per IFC Drawings.
label | ○ Grout completely fills void between op of pile and structure by ramming against fixed support.
label | – – – – – – – – – – – – – – – – –
label | METHOD: Visual, Measure
label | – – – – – – – – – – – – – – – – –
label | FREQUENCY: Per pole
label | – – – – – – – – – – – – – – – – –
label | CATEGORY: IP
label | – – – – – – – – – – – – – – – – –
label | RESPONSIBILITY: SE/PE
label | – – – – – – – – – – – – – – – – –
label | VERIFYING DOCUMENTS: This ITP
date | Date Completed:
checkpoint | 5.15 Earth electrode or mat
label | REFERENCE: IFC Drawings A9819
label | – – – – – – – – – – – – – – – – –
label | ACCEPTANCE CRITERIA: Must be one installed per each lighting and power installation.
label | ○ The minimum distance between Earth electrodes or mats of lighting and power supply systems and rail tracks shall be based on the earthing design but shall be a minimum distance of 3.0 metres from the nearest running rail.
label | ○ Earth mats shall be bonded into a continuous electrical grid using a welded connection in accordance with AS 1554 or approved crimp connection from the MTM Engineering A1215 Remove covered Approved Product List.
label | ○ A certificate of compliance to AS 2832.5 and test results shall be provided for all bonding connections.
label | – – – – – – – – – – – – – – – – –
label | METHOD: Visual
label | – – – – – – – – – – – – – – – – –
label | FREQUENCY: per pole
label | – – – – – – – – – – – – – – – – –
label | CATEGORY: IP
label | – – – – – – – – – – – – – – – – –
label | RESPONSIBILITY: SE/PE
label | – – – – – – – – – – – – – – – – –
label | VERIFYING DOCUMENTS: This ITP
date | Date Completed:
section | Post Constrution
checkpoint | 6.1 Attached and verify Subcontractor conformance records/signed ITP including relevant verification sheets
label | REFERENCE: IFC Drawing Note
label | – – – – – – – – – – – – – – – – –
label | ACCEPTANCE CRITERIA: Check conformance report against project conformance criteria
label | – – – – – – – – – – – – – – – – –
label | METHOD: Doc. Review
label | – – – – – – – – – – – – – – – – –
label | FREQUENCY: Each lot
label | – – – – – – – – – – – – – – – – –
label | CATEGORY: IP
label | – – – – – – – – – – – – – – – – –
label | RESPONSIBILITY: SE/Site Supervisor
label | – – – – – – – – – – – – – – – – –
label | VERIFYING DOCUMENTS: Sign ITP, Attach documents
date | Date Completed:
checkpoint | 6.2 Compressive Strength Test Results
label | REFERENCE: IFC Drawings, Table VR 610.05.051, VR 610.16 (g)
label | – – – – – – – – – – – – – – – – –
label | ACCEPTANCE CRITERIA: 7 day compressive strength to comply with table 610.051 for early indication that the strength is tracking correctly.
label | ○ 28 day compressive strength (average of the 2 no. cylinders) per sample comply with the design strength.
label | Note: 1 of the 2 no. 28 day cylinders per sample may be as low as 90% of the required strength, so long as the average meets the required strength.
label | Attach: Compressive Strength Test Results
label | – – – – – – – – – – – – – – – – –
label | METHOD: Document Review
label | – – – – – – – – – – – – – – – – –
label | FREQUENCY: Each cylinder
label | – – – – – – – – – – – – – – – – –
label | CATEGORY: IP
label | – – – – – – – – – – – – – – – – –
label | RESPONSIBILITY: SE/PE
label | – – – – – – – – – – – – – – – – –
label | VERIFYING DOCUMENTS: This ITP
date | Date Completed:
checkpoint | 6.3 As-Constructed Plans
label | REFERENCE: IFC Drawing Note
label | – – – – – – – – – – – – – – – – –
label | ACCEPTANCE CRITERIA: The Contractor shall supply to the Superintendent two copies of ‘As-Constructed’ plans along with a USB drive or other approved storage medium containing the CADD drawing files, and the same shall be supplied by the Contractor to the local distribution company if appropriate.
label | – – – – – – – – – – – – – – – – –
label | METHOD: Document Review
label | – – – – – – – – – – – – – – – – –
label | FREQUENCY: Upon completion/ Work area
label | – – – – – – – – – – – – – – – – –
label | CATEGORY: HP*
label | – – – – – – – – – – – – – – – – –
label | RESPONSIBILITY: SE/PE/SPE
label | – – – – – – – – – – – – – – – – –
label | VERIFYING DOCUMENTS: Sign ITP, Attach As Constructured Plans
date | Date Completed:
checkpoint | 6.4 Non-conformance Report (NCR) Closure
label | REFERENCE: MRPA Quality Management Plan
label | – – – – – – – – – – – – – – – – –
label | ACCEPTANCE CRITERIA: Ensure that any NCRs pertaining to the lot / element / Work area that this ITP covers, have been closed in CAMs.
label | – – – – – – – – – – – – – – – – –
label | METHOD: Document Review
label | – – – – – – – – – – – – – – – – –
label | FREQUENCY: Once, prior to closure of this lot / element / Work area
label | – – – – – – – – – – – – – – – – –
label | CATEGORY: HP*
label | – – – – – – – – – – – – – – – – –
label | RESPONSIBILITY: SE/PE/SPE
label | – – – – – – – – – – – – – – – – –
label | VERIFYING DOCUMENTS: This ITP
date | Date Completed:
checkpoint | Final Inspection
label | On behalf of Metropolitan Roads Program Alliance, it is hereby certified that the Works represented by the item of work listed have been tested in accordance with the Project Quality Plan and conform in all respects with the requirements of the Contract.
text | Name:
text | Position:
date | Date Completed:
holdpoint | Sign ITP