## Project Checklist Templates
Id | Type | Name | Values | Prompting Name
6ea77dee-f62f-4461-8aeb-477e9e6b4ee4 | checklist | Commissioning |  | Commissioning
cef0bf8a-2bad-4b07-b29e-477c9665d453 | section | Commissioning
35e76c16-2730-4556-b112-0ff01efb67f7 | checkpoint | SCV-Locks/chain/labels/pipework stickers/sprinkler spares & spanner/block plans
fb20111b-e1e2-4bd3-9546-f5980dfbe80a | checkpoint | Booster Cupboard-Signage/Locks/chain/labels/plan sleeve+block plans label/block plans
36fc2f65-10ea-414a-8058-d5a540fbff6f | checkpoint | Hydrant Mains/Isolation Valves-Locks/chain/labels/pipework stickers
5bf48bb1-7809-45a0-aed4-2b54401f65a1 | checkpoint | Water Meter Assembly-Locks/chain/labels
9822cbf6-9668-4808-8c7e-318b33f97e5a | checkpoint | Check sluice valves & water meter valves are open
aef77fa7-99ea-4639-a8a0-a6c4e29681c4 | checkpoint | Fire Pump/Tank-Fuel full, Exhaust piped, Mains power, Drains/Relief Valve piped, Water Supply on, Locks/chain/labels/pipework stickers
a38c0587-d6f5-4c38-a6b1-fb9d6b6ef4b9 | checkpoint | Adjust Bermads & float Valves to fire tanks
6bb0b6bc-fd24-486c-9977-955b272a1b03 | checkpoint | Pump Room-Block Plans
115734e0-21d9-4ec6-b3a2-526fab87cc42 | checkpoint | FIP-Block plans/test all alarm devices
2cf29c06-f71d-4699-8338-51d7f6ee6375 | checkpoint | Test all Valves & Flow switches to ensure correct operation
4551b15c-a554-499a-8bb0-94189df33e72 | checkpoint | Set Pressure switches to Jacking pump & alarm line
5f9cb784-9d21-48b9-83cf-a32897145996 | checkpoint | Block plans/Tactical Fire plans/FRV way finding plan
c11bdf61-6d84-4e2f-91a0-a4b88f13befb | checkpoint | FRV Shortfall drawings & FRV stat signage ie: x2 30m hose
a5c127fc-50de-4567-9499-db000ab240f2 | checkpoint | Individual Floor Block plans (If applicable)
f34a0140-098b-4b88-8642-49158702ce39 | checklist | ESM ITP |  | ESM ITP
ad8796d1-9094-4469-9ec9-4f73e22faa6b | section | ESM ITP
3899b9a9-108e-49d5-9d2a-16b135000d6a | checkpoint | Isolate FIP & Drain down sprinkler system
f9df62e1-e0d0-40a7-a8b5-40289857a4d6 | checkpoint | Lay down drop sheets/floor protection & move any furniture as required.
6b11f1fc-8853-4e5c-9b1e-195a170152ed | checkpoint | Replace all sprinkler heads/sprinkler plates and record quantity replaced
ccd758f0-b1bd-44e4-9981-816f70276cf7 | checkpoint | Re-instate water on completion and walk around and ensure no leaks present
fac06362-ea6a-4641-8e5e-53d5f0e54e0a | checkpoint | Remove drop sheets/floor protection & move furniture back in place.
233a051c-477e-4716-a727-416d18c304a8 | checkpoint | Record any holes cut for removal of sprinklers and document their locations
49a18251-d1df-4acf-a03d-2df42e1335fc | checkpoint | Record any further action required; ie; sprinkler head heights need adjusting etc.
448714b7-3c5c-4024-89a4-19591d126c3b | checkpoint | Any other information required to know please add in comments
6444ae9f-3303-4740-a6bd-45c099dc201d | checklist | Fire Booster Cupboard checklist |  | Fire Booster Cupboard checklist
76ec6974-8637-4ced-ba65-1236383e4f92 | section | Fire Booster Cupboard
949d16e5-e9af-4988-ab09-f954b053a173 | checkpoint | Install Suction/ Millcocks & Hydrant, Sprinkler Boosters
bddb52a2-8303-4c6c-92ff-3878dc91c282 | checklist | Fire Extinguishers/Blankets |  | Fire Extinguishers/Blankets
436a2c3f-b019-4d69-972f-b11a6ed24ce5 | section | Fire Extinguishers/Blankets
55e60997-23a2-4a05-9c4a-4318ee274194 | checkpoint | Install Extinguishers
0d5651ca-0c7a-4a83-9d36-065dcdaea5de | checkpoint | Install appropiate signage
6ec812b7-8cb6-4c8a-9059-904fb1a55ee4 | checkpoint | Install Fire Blankets
73da6fa0-32a4-472a-aa53-708951dc30c2 | checkpoint | Fire Hose Reel signs
c823284f-16f7-4bd1-ab48-8491edfd03d0 | checklist | Fire Penetrations checklist |  | Fire Penetrations checklist
1359b021-6afa-4e62-9db3-24ffc800d767 | section | Fire Penetrations
e3cf7371-f895-4f49-a994-2c3f95e00b43 | checkpoint | Fire Penetration labelled & caulked in accordance with AS 4072.1 Drawing Reference No.
6ba39d2e-5053-47fa-ae7e-5f2c067c7377 | checklist | Fire Pumps/Tanks checklist |  | Fire Pumps/Tanks checklist
d3852541-c27d-47dd-a954-0ba92ef52b42 | section | Fire Pumps/Tanks
f007ec9d-0f84-40dc-9937-bf880aecd5a5 | checkpoint | Install Plinth & secure
eba413ff-c9ca-456a-8001-bd566f7cc2b7 | checkpoint | Install Pumps & secure to plinths
36c5c067-4620-4d42-9d99-6c6ba74c4688 | checkpoint | Install all pipework/isolation valves to pumps
431672fb-c3d2-400d-b588-991852b95330 | checkpoint | Install Annubar/coolant drains
d1df2db1-a2a5-496c-9eba-d1d551cd7a5d | checkpoint | Install Pump Exhaust to designated point
a566370e-496c-40ae-b731-4b694f6f438b | checkpoint | Water Test all Pipework to pumps
39077041-9e24-4491-9b74-6b81f321a0e3 | checkpoint | Install all Pipework and Valves to Fire Tank
797c01c2-19ca-4040-b3f7-b1e614d3273a | checkpoint | Water test all pipework to and from Water Tank
6ec40865-eae1-4f90-8776-e638f296c084 | checklist | Hydrant/Sprinkler Mains/Risers/Hose Reel checklist |  | Hydrant/Sprinkler Mains/Risers/Hose Reel checklist
a814b0ca-1ad3-4e95-9ea0-adc2c249839f | section | Hydrant/Sprinkler Mains/Risers/Hose Reel
9157f8eb-b466-46d2-9837-4ddefc278047 | checkpoint | Rough In: All Mains & isolation valves installed
2d6bfe39-7a96-4c3c-b767-7ea0ab52b728 | checkpoint | Install Hydrant/ Sprinkler/Test Drain Risers & Mill Cocks
c5a99de5-6935-4a98-b3dc-c2313298f714 | checkpoint | Sprinkler Floor Control Valves installed and secured
4c473a6b-0deb-4cdd-a40c-3b93fe847746 | checkpoint | Fit Off: Check all millcock clearances/angles/Mill cocks in closed position & Install 2400kPa pressure gauge to top of risers
4ee318c3-25dd-4eab-a919-2f2f46573255 | checkpoint | Install Fire Hose Reels & pipework
e79b3040-877f-45cf-86eb-6ca5eadc0e61 | checkpoint | Air Test: Pressurized air test for a period of 30 mins (if applicable)
faf35c1d-b74b-54cb-8c89-ea1ee1269ce1 | textbox | Start time:
07d0d9b0-d4bb-53e2-b492-899103ba2b51 | textbox | Completion time:
2b50b8a3-c9ad-4629-b16f-37f8df85f575 | checkpoint | Water Test: Pressure test to 1700Kpa for duration of 2 hours
48a52acc-4eb5-5d8c-b0ce-198a4660e2f7 | textbox | Start time:
6d3d9ec5-61b1-5460-a107-70675c077bdb | textbox | Completion time:
7a30af75-c3da-4e91-b000-961ad41caafd | checkpoint | FHR: All FHR been bled from excess air & proof of water
6da38afb-24cd-4610-9aec-dd6033df6ed7 | checkpoint | PFP Foreman signature
e5e0fd22-cdd0-4488-8abf-9b53a0430690 | checklist | Incident Reports |  | Incident Reports
d88ca85d-c67d-40b4-8c8d-bfc1450eab6f | section | Details of accident/incident
24c3a7c2-4451-4f90-9d06-4ec994e0d372 | checkpoint | Please attach any relevant photos & documents
c473689c-3a02-563f-bb4b-a42736d6467e | textbox | Date of incident
ed82957f-13c3-5f76-baac-0e6fca6fd78d | textbox | Time of incident:
d60d8ca9-0051-53bf-8ffb-e16049e3dba4 | textbox | Time of report:
f0226883-d255-4d59-8fe3-615f44910ee0 | checkpoint | Nature of incident
eeb6da0a-d924-5555-b8e7-a221946a5dd8 | tickbox | injury (attach completed WHSE Form 01 Injury report)
dc40f2c2-c11e-5ed5-803e-988a89958bc7 | tickbox | environmental (pollution)
79267ec8-9b21-5962-8c25-638e95765453 | tickbox | damage to property/assets/services
008c72b4-1e01-5158-a831-935caf70c8b9 | tickbox | incident
4f11bf42-4a35-4b89-bf3c-df8391d669be | section | Names of person(s) involved
ec3f3452-e530-4f25-a0a8-fa9063126594 | checkpoint | Please attach any relevant photos & documents
dd4cc67e-a320-558b-ab5c-599afe65e223 | textbox | Name
a25d880a-7361-5968-85f6-d673fa37331e | textbox | Phone Number
83901529-11a4-5f2e-b156-7016c240fd51 | note | (home, mobile & work)
9995bc8a-e92b-5611-92c1-10cbfea81219 | textbox | Address
c39d9f90-9b9a-5612-b8d1-c6b17906495e | textbox | D.O.B
3539a924-707c-51b4-afc1-7c13f09b4b6d | textbox | Email
2957ce93-d685-5721-b75b-5ade8f432f76 | textbox | Activity in which the person(s) was engaged at the time:
62a0266e-7da6-54bc-a87a-5966047b9433 | textbox | Exact site location where injury/incident occurred:
74f39ede-3d5f-5bc5-92eb-44fd63404dd6 | textbox | Type of injury/pollution/damage/ incident:
f09cb6ee-4e55-51af-bfd1-846cd51ae078 | textbox | Describe the accident/incident in detail:
8de0590c-996c-4d8b-930c-168bb6ddef99 | section | Witness to incident (each witness may need to provide an account of what happened
ce8aee8e-3c2d-45af-a2ad-29f9a5e847f0 | checkpoint | Please attach any relevant photos & documents
b6be2ae5-a705-5fb7-a75f-9c212e851df9 | textbox | Witness Name
ff813c6b-bc50-5d38-b392-4431d0cee508 | textbox | Witness Contact
bf6f56ab-f264-53f0-b475-9b8aa05f9b96 | textbox | Witness Name
48e91dee-af45-5478-a099-19cb3b266b1a | textbox | Witness Contact
5f3b5c83-07a5-4136-9e7a-7b2aaafd2e08 | section | Are there any notable/significant factors relevant to the accident/incident?
35e82f0d-6e7f-48cc-a088-ec77da6b2549 | checkpoint | Please attach any relevant photos & documents
93d6c7ca-4b55-55a3-92c8-5c22cbae92a1 | textbox | Details
127ea952-7e31-482b-9c2d-f7eee91a9260 | section | Arrangements made to store any equipment that believed to have contributed to injury/incident?
c1849a30-574e-42a7-ad10-e1894512e501 | checkpoint | Please attach any relevant photos & documents
a3981ecb-527f-50e3-93c6-2702f2eeaed9 | textbox | Details
11ef9140-c999-45ac-911e-b6445d356967 | section | Did any third parties (subcontractors, visitors, etc.,) contribute to the incident? If so, how?
5975d8c8-499c-4221-985c-59c29ba05bbb | checkpoint | Please attach any relevant photos & documents
a456289e-a93c-5525-a192-41ec62cdddd5 | textbox | Details
c2ac4a52-b089-4d9d-bfa0-c374ac84d5a6 | section | Immediate corrective actions taken? (e.g., works ceased, area made safe, barriers erected, etc.,)
0d12694c-ea9e-4285-9b5a-787ccd678397 | checkpoint | Please attach any relevant photos & documents
19e79e34-e050-5681-a785-985da0524a53 | textbox | Details
61e96fa7-8b5d-400c-9350-73cfdda22a0b | section | Future actions taken (e.g., engineering solutions, training, toolbox talk, etc.,)
e4c98516-2e23-402a-b10b-0556a0ce6ac9 | checkpoint | Please attach any relevant photos & documents
0c77c719-6102-5688-b433-dbc935209bed | textbox | Details
cb50b49e-4468-45d0-bcf4-fa76d35d68a2 | section | Review & Sign off
42201632-7db1-49c5-b4ac-d15b2bcba763 | checkpoint | Have all actions been completed and reviewed as effective?
02c18653-6f2f-4327-93ec-3f7f76b40a4c | checkpoint | Have all documents relating to the incident, including corrective action evidence been completed
856140e3-ae21-4f97-81ca-edf207208045 | signoff | Signed Off
d64d3ac8-0286-45ce-bdf6-454dc1b1ac4c | checklist | Project Drawings |  | Project Drawings
3325ddb9-77a0-4c73-910f-89aed3d17bdb | section | Details
7985a7ed-f888-49b9-a899-21093a52ff16 | checkpoint | Upload project drawings
20aad76f-d751-4572-8f63-2bed4910d588 | checklist | Site Diary Checklist |  | Site Diary Checklist
5cb4918e-e6f5-4f44-8fb2-fab99993f947 | section | Details
3cf6d0ed-6d0b-489b-8a13-d978476d5a15 | checkpoint | Comment/notes
84aa3a62-45d4-4e5a-8c5d-60abe39a9ea6 | checklist | Sprinkler Control Valves checklist |  | Sprinkler Control Valves checklist
ad443116-088a-4d7b-ad34-47d0ef68c60d | section | Sprinkler Control Valves
04870a87-7e94-4e38-9085-76ef690b1902 | checkpoint | Install Sprinkler Control Valves/ Jacking Pump
27789763-7b94-44dc-b534-d32f12914901 | checkpoint | Test full operation of Control Valves
d078d728-22c2-43ed-8bb7-133dfcba7e12 | checkpoint | Install Sprinkler Spares box, spare sprinklers & spanner
bdc2437b-c995-4cc1-b5c5-b9c9405d14e4 | checkpoint | Set Jacking Pump pressure switch min 150 kPa above towns main/manifold pressure
2e188754-be78-482a-a5b2-f0b4f2dc0dbc | checkpoint | Install Gong/Electric Bell & test operation
07d5c77c-9b2b-4c27-9b8c-e851de3950ef | checkpoint | Check for adequate drainage and test
e52bbf37-e522-4ede-91d7-706e4e3826ab | checklist | Sprinkler Fit Off checklist |  | Sprinkler Fit Off checklist
37600394-0f6b-44ab-a653-79418b38ef8b | section | Sprinkler Fit Off
66eb7724-bec9-4773-8353-a1b2364d45e3 | checkpoint | Fit Off: Check all sprinklers have been fit off
af9c3717-6631-4ba4-929e-79be112ac6b4 | checkpoint | Check sprinkler heights pre paint
21801c8c-77c2-4f8f-9d02-60e1819ddac1 | checkpoint | Fit off Escutcheon plates
6dd5acb3-048a-42a2-814d-e83dc91c774b | checkpoint | Air Test: Pressurized air test for a period of 30 mins (if applicable)
95cbf16a-fdce-5692-9983-09bf80404b5c | textbox | Start time:
0ba56ae6-d6ce-54fb-8171-851b00fb4965 | textbox | Completion time:
9a64ef86-eefa-4480-90ff-6719093878de | checkpoint | Water Test: Pressure test to 1600Kpa for duration of 2 hours
15823c9c-896a-5d70-97f4-8c02b5f43d18 | textbox | Start time:
eca762d4-c034-5ed5-95a0-c105288e116c | textbox | Completion time:
970bacf9-6a7b-43de-b763-d4742d056fae | checkpoint | PFP Foreman signature
4e5b3809-3209-46a1-b929-5ab00726d345 | checklist | Sprinkler Rough In checklist |  | Sprinkler Rough In checklist
512e208e-a8a8-45d9-87d1-aa44b4029e21 | section | Sprinkler Rough In
89946401-3e29-4b77-97e0-c5071009b535 | checkpoint | Rough In: All Mains, range pipes, clips installed & secured
046bff76-2650-4413-8172-aa0445322afe | checkpoint | Concealed Space Sprinklers & Flexible droppers Installed
028be181-58d0-4a80-994f-74722946bca0 | checkpoint | Arm pieces / Under Duct pipework installed and secured
ebcd6828-794c-4f3c-bd76-812ff588a60c | checkpoint | Balcony Sprinklers installed
ec2b4851-933b-4f1c-a211-b5cd5b84acc4 | checkpoint | Car Park Sprinklers Installed
2217c1c3-41a1-4ba2-bcb5-f95fa4143a85 | checkpoint | Car Stackers pipework installed & secured (if applicable)
fcb9efc6-3e56-4f77-8cac-1290fbd1a97c | checkpoint | Install Remote Test drain pipework
a34960e3-5b5d-4e42-8072-76eda8a1e350 | checkpoint | Air Test: Pressurized air test for a period of 30 mins (if applicable)
fc12fc66-d71c-53a3-b71b-b6d74e995590 | textbox | Start time:
1e9e2adf-c80b-596a-9cdf-80ef8c924178 | textbox | Completion time:
2bb243df-b371-4cc9-b450-72e7b90a387c | checkpoint | Water Test: Pressure test to 1600Kpa for duration of 2 hours
1c2bba8e-e3d2-5719-8c10-8d0c095d0d23 | textbox | Start time:
8bd50700-5983-51db-9570-2bde54c24d56 | textbox | Completion time:
a801e7bc-ef6c-4bd0-9296-56f6451f1011 | checkpoint | PFP Foreman signature
33663909-3c07-418f-a31b-e1e24837eed2 | checklist | Toolbox Meeting Checklist |  | Toolbox Meeting Checklist
2cc23176-e4ba-4f7a-81f6-13654028f0bc | section | Attendance
539135a6-10ba-42ea-81c0-87818ba82db3 | checkpoint | Attendance - list of attendees added below
40a61c52-376a-403d-808c-7d1da22436f2 | section | Minutes
98a2076b-a3f2-4605-a33c-1f1a6a5c787d | checkpoint | Actions from last meeting
4c0a18a1-9400-403f-988e-4ee1d0475264 | checkpoint | Safety: (including hazards / near misses / controls / site specific)
662d6e36-bc4e-450f-8f04-26871a4eedbc | checkpoint | Plant, tools & Equipment all in good working order?
183183ae-6f75-43df-90a6-66307601bfa5 | checkpoint | PPE-ensure everyone has PPE
60f8f281-a8de-4449-ae7a-0521e6f6b65f | checkpoint | Housekeeping to be maintained
c1f01933-ad8b-4161-bcc8-d64ab71942c8 | checkpoint | Ensure Electrical equipment test and tagged
0eeb659d-4711-4ab9-aa69-c470f5512a8c | section | New Business / Other
d26a0882-08cd-4e78-987d-d203cc2ebb14 | checkpoint | Any new business / other comments added below
05662017-c9c0-4f53-824c-8523135917f9 | section | Meeting Closure
277e0d51-d452-4540-9e2a-5c26ec2262f0 | checkpoint | Meeting Closed
444db2f2-1d16-5b1e-9a59-3b737e89dde5 | textbox | Meeting Closed time
4ffb8ffa-d462-575a-812e-d04f8f3e0e04 | textbox | Minutes taken by (Name)
46171f10-eb05-4c8b-b8e7-fabad251c58e | checkpoint | Employee sign off
16d61236-7d3d-43b8-b2eb-7071d5fa91c7 | checklist | Undocumented Variations |  | Undocumented Variations
45204150-143a-4804-81d6-743e5caff407 | section | Details
86280eec-2617-4946-8728-029464203ee3 | checkpoint | Attach relevant details
b217374e-5fd4-4083-912e-2f6d581ef508 | checklist | Variations |  | Variations
c8cbf6fd-32e3-4c9f-a3bf-4ae4d41054d9 | section | Payer Details
867b8ab7-3bab-425f-9754-cdc9348a5d36 | checkpoint | Payer Details entered below
196b2e5e-48c8-5e4c-a115-3e90a04ace50 | textbox | Contact
f9e3ce0b-ebc3-5234-86ee-33bce2cce9cd | textbox | Company
63e0efe3-6bc1-5def-9f05-fa688183b411 | textbox | Contact No.
d0fa9f6f-5aef-496d-9e45-ff82f99a9a76 | section | Variation Details
ab639483-32b6-4536-8057-bbc9049c254e | checkpoint | Variation Details Entered
189d396e-3e30-508a-a04c-5db95f303c0e | textbox | Description of work
e90d9931-a425-5be0-93a6-bd2a9778b642 | textbox | Reason for variation (unless stated in instruction)
0d158af2-38f3-5377-ba65-1227255d0b07 | textbox | Area/Location
17cd4cc8-10f1-55ca-8ff1-c668c0779a34 | textbox | As directed and requested by
8a6b450c-b3bf-5d96-bb9c-248b736e7306 | textbox | Date
6e64dc4f-9f96-52b0-816d-0f569b358cf0 | textbox | Normal Hours
d6aa119f-77ef-501f-ad15-010af053c571 | textbox | Overtime Hours
6d5fd792-df59-54aa-a861-1565d543838a | textbox | Material used to complete task
bc2ed93f-3c9e-4b2b-8fce-644d875d3e88 | checkpoint | Variation Completed
c18d9902-7612-446d-965d-8642f5d86bc2 | section | Sign Off
214e801a-0315-41bb-8a29-3cdb37f1980d | checkpoint | Variation signed
ce668f7c-6775-5487-b91b-1d656724b966 | note | I hereby authorise you to carry out the extra work detailed above and I agree that the same shall be paid as an addition to your original contract order
2c1701c2-bd15-45ac-aec8-16de321d06ef | signoff | Builder / Client signature