## BRANZ- QA Documentation
BRANZ
Section | Quality Management Plan
Section | Drawings
AE Smith Construction Drawing
X
Y
Z
Consultant
X
Y
Z
Seismic
X
Y
Z
Section | Producer Statement Design
Building / Area
PS 1
PS 3
PS 4
Section | BMS
Building / Area
X
Y
Z
Section | Electrical
Building / Area
COC's
X
Y
Z
Section | Specifications Document
HTM_02-01_Part A
Section | General
X
Y
Z
Section | Photos
X
Y
Z

## Admin Block
BRANZ
Admin Block
AB- MD100 Ventilation
Mechanical QA
|  |  |  | AB-IU1 | Fan Coil Units | External Acoustic Insulation (FCU's) | Condensate Insulation
|  |  |  | AB-IU1 - S/A Ducting | Mechanical Duct | Internal Duct Work Insulation | Labeling of Equipment | External Duct Work Insulation
|  |  |  | AB-IU2 | Fan Coil Units | External Acoustic Insulation (FCU's) | Condensate Insulation
|  |  |  | AB-IU2 - S/A Ducting | Mechanical Duct | Internal Duct Work Insulation | Labeling of Equipment | External Duct Work Insulation
|  |  |  | AB-IU3 | Fan Coil Units | External Acoustic Insulation (FCU's) | Condensate Insulation
|  |  |  | AB-IU3 - S/A Ducting | Mechanical Duct | Internal Duct Work Insulation | Labeling of Equipment | External Duct Work Insulation
|  |  |  | AB-IU4 | Fan Coil Units | External Acoustic Insulation (FCU's) | Condensate Insulation
|  |  |  | AB-IU4 - S/A Ducting | Mechanical Duct | Internal Duct Work Insulation | Labeling of Equipment | External Duct Work Insulation
|  |  |  | AB-IU5 | Fan Coil Units | External Acoustic Insulation (FCU's) | Condensate Insulation
|  |  |  | AB-IU5 - S/A Ducting | Mechanical Duct | Internal Duct Work Insulation | Labeling of Equipment | External Duct Work Insulation
|  |  |  | AB-IU6 | Fan Coil Units | External Acoustic Insulation (FCU's) | Condensate Insulation
|  |  |  | AB-IU6 - S/A Ducting | Mechanical Duct | Internal Duct Work Insulation | Labeling of Equipment | External Duct Work Insulation
|  |  |  | AB-IU6 - R/A Ducting | Mechanical Duct | Internal Duct Work Insulation | Labeling of Equipment | External Duct Work Insulation
|  |  |  | AB-IU7 | Fan Coil Units | External Acoustic Insulation (FCU's) | Condensate Insulation
|  |  |  | AB-IU7 - S/A Ducting | Mechanical Duct | Internal Duct Work Insulation | Labeling of Equipment | External Duct Work Insulation
|  |  |  | AB-IU7 - R/A Ducting | Mechanical Duct | Internal Duct Work Insulation | Labeling of Equipment | External Duct Work Insulation
|  |  |  | AB-SF3 Fan | Fans |  | Labeling of Equipment
|  |  |  | AB-SF3 O/A Ducting | Mechanical Duct | Internal Duct Work Insulation | Labeling of Equipment | External Duct Work Insulation
|  |  |  | AB-HRV-1 | Fan Coil Units | External Acoustic Insulation (FCU's) | Condensate Insulation
|  |  |  | AB-HRV-1 - O/A Ducting | Mechanical Duct | Internal Duct Work Insulation | Labeling of Equipment | External Duct Work Insulation
|  |  |  | AB-HRV-1 - R/A Ducting | Mechanical Duct | Internal Duct Work Insulation | Labeling of Equipment | External Duct Work Insulation
|  |  |  | AB-SF1 Fan | Fans |  | Labeling of Equipment
|  |  |  | AB-HRV-2 | Fan Coil Units | External Acoustic Insulation (FCU's) | Condensate Insulation
|  |  |  | AB-HRV-2- O/A Ducting | Mechanical Duct | Internal Duct Work Insulation | Labeling of Equipment | External Duct Work Insulation
|  |  |  | AB-HRV-2 - R/A Ducting | Mechanical Duct | Internal Duct Work Insulation | Labeling of Equipment | External Duct Work Insulation
|  |  |  | AB-SF1 Fan | Fans |  | Labeling of Equipment
|  |  |  | AB-HRV-3 | Fan Coil Units | External Acoustic Insulation (FCU's) | Condensate Insulation
|  |  |  | AB-HRV-3 - O/A Ducting | Mechanical Duct | Internal Duct Work Insulation | Labeling of Equipment | External Duct Work Insulation
|  |  |  | AB-HRV-3 - R/A Ducting | Mechanical Duct | Internal Duct Work Insulation | Labeling of Equipment | External Duct Work Insulation
|  |  |  | AB-SF1 Fan | Fans |  | Labeling of Equipment
|  |  |  | AB-EF1 Fan | Fans | Duct / Equipment Cleaning | Labeling of Equipment
|  |  |  | AB-EF2 Fan | Fans | Duct / Equipment Cleaning | Labeling of Equipment
|  |  |  | AB -EF 1 & 2 Toilet Exhaust Duct | Mechanical Duct | Labeling of Equipment
AB- MP302 Hydronic
Piping QA
|  |  |  | AB-IU1 | CHW & HHW Piping ( WELDING ) | CHW & HHW Insulation | Labeling of Equipment | Braze Bench Test
|  |  |  | AB-IU2 | CHW & HHW Piping ( WELDING ) | CHW & HHW Insulation | Labeling of Equipment | Braze Bench Test
|  |  |  | AB-BC1 | DX Units | Labeling of Equipment | Braze Bench Test
|  |  |  | AB-IU3 | CHW & HHW Piping ( WELDING ) | CHW & HHW Insulation | Labeling of Equipment | Braze Bench Test
|  |  |  | AB-IU4 | CHW & HHW Piping ( WELDING ) | CHW & HHW Insulation | Labeling of Equipment | Braze Bench Test
|  |  |  | AB-IU5 | CHW & HHW Piping ( WELDING ) | CHW & HHW Insulation | Labeling of Equipment | Braze Bench Test
|  |  |  | AB-IU6 | CHW & HHW Piping ( WELDING ) | CHW & HHW Insulation | Labeling of Equipment | Braze Bench Test
|  |  |  | AB-IU7 | CHW & HHW Piping ( WELDING ) | CHW & HHW Insulation | Labeling of Equipment | Braze Bench Test
|  |  |  | AB-BC2 | DX Units | Labeling of Equipment | Braze Bench Test
|  |  |  | AB-IU8 | DX Units | Labeling of Equipment | Braze Bench Test
AB-MP300 Heating
Piping QA Boiler House
|  |  |  | Boiler House Heating Pipework | CHW & HHW Piping ( WELDING ) | CHW & HHW Insulation | Labeling of Equipment | Braze Bench Test
|  |  |  | Buffer Tank | Chillers / Buffer Tank / Dosing Pod / Pumps | E4M QA | Labeling of Equipment
|  |  |  | AB-HEX1 | Chillers / Buffer Tank / Dosing Pod / Pumps | E4M QA | Labeling of Equipment
|  |  |  | Boiler | Chillers / Buffer Tank / Dosing Pod / Pumps | E4M QA | Labeling of Equipment
|  |  |  | MCC Panel | E4M - Mechanical Board ( MSSB )
|  |  |  | Pump | Chillers / Buffer Tank / Dosing Pod / Pumps | E4M QA | Labeling of Equipment
AB- MP100 Heating
|  |  | Piping QA | Main HHW Piping for Radiant Heaters | CHW & HHW Piping ( WELDING ) | CHW & HHW Insulation | Labeling of Equipment | Braze Bench Test
|  |  |  | AB-RH1 | Radiant Heaters
|  |  |  | AB-RH1 | Radiant Heaters
|  |  |  | AB-RH1 | Radiant Heaters
|  |  |  | AB-RH1 | Radiant Heaters
|  |  |  | AB-RH1 | Radiant Heaters
|  |  |  | AB-RH1 | Radiant Heaters
|  |  |  | AB-RH1 | Radiant Heaters
|  |  |  | AB-RH1 | Radiant Heaters
|  |  |  | AB-RH1 | Radiant Heaters
|  |  |  | AB-RH1 | Radiant Heaters
|  |  |  | AB-RH1 | Radiant Heaters
|  |  |  | AB-RH1 | Radiant Heaters
|  |  |  | AB-RH1 | Radiant Heaters
|  |  |  | AB-RH1 | Radiant Heaters
|  |  |  | AB-RH1 | Radiant Heaters
|  |  |  | AB-RH2 | Radiant Heaters
|  |  |  | AB-RH2 | Radiant Heaters
|  |  |  | AB-RH2 | Radiant Heaters
|  |  |  | AB-RH2 | Radiant Heaters
|  |  |  | AB-RH2 | Radiant Heaters
|  |  |  | AB-RH3 | Radiant Heaters
|  |  |  | AB-RH3 | Radiant Heaters
|  |  |  | AB-RH3 | Radiant Heaters
|  |  |  | AB-RH3 | Radiant Heaters
|  |  |  | AB-RH3 | Radiant Heaters
|  |  |  | AB-RH3 | Radiant Heaters
|  |  |  | AB-RH4 | Radiant Heaters
|  |  |  | AB-RH4 | Radiant Heaters
|  |  |  | AB-RH4 | Radiant Heaters
|  |  |  | AB-RH4 | Radiant Heaters
|  |  |  | AB-RH4 | Radiant Heaters
|  | SW-MP-01 | Trench Piping
|  |  |  | Main Trench Heating pipework | CHW & HHW Piping ( WELDING ) | CHW & HHW Insulation | Labeling of Equipment | Braze Bench Test
|  |  |  | Main Trench Refrigeration pipwork | DX Units | Labeling of Equipment | Braze Bench Test

## Structural Lab
BRANZ
Structural Lab
SL- MP100 Pipework Layout
Piping QA
|  |  |  | Main HHW Piping for Radiant Heaters | CHW & HHW Piping ( WELDING ) | CHW & HHW Insulation | Labeling of Equipment | Braze Bench Test
|  |  |  | SL-RH1 | Radiant Heaters
|  |  |  | SL-RH1 | Radiant Heaters
|  |  |  | SL-RH1 | Radiant Heaters
|  |  |  | SL-RH1 | Radiant Heaters
|  |  |  | SL-RH1 | Radiant Heaters
|  |  |  | SL-RH1 | Radiant Heaters
|  |  |  | SL-RH1 | Radiant Heaters
|  |  |  | SL-RH1 | Radiant Heaters
|  |  |  | SL-RH1 | Radiant Heaters
|  |  |  | SL-CF2 | Radiant Heaters
|  |  |  | SL-CF2 | Radiant Heaters
SL-MP101 - Office ceiling
Mechanical QA
|  |  |  | SL-SF1 Fan | Fans |  | Labeling of Equipment
|  |  |  | SL-SF1 O/A Duct | Mechanical Duct | Labeling of Equipment
|  |  |  | SL-IU1 | DX Units | Labeling of Equipment | Braze Bench Test
|  |  |  | SL-IU2 | DX Units | Labeling of Equipment | Braze Bench Test
Piping QA
|  |  |  | Trench Piping Ref | DX Units | Labeling of Equipment | Braze Bench Test
|  |  |  | Trench Piping Heating | CHW & HHW Piping ( WELDING ) | CHW & HHW Insulation | Labeling of Equipment | Braze Bench Test
SL-MD300 - Shematic
Piping QA
|  |  |  | SL-HEX1 | Chillers / Buffer Tank / Dosing Pod / Pumps | E4M QA | Labeling of Equipment | CHW & HHW Piping ( WELDING )

## Fire Lab
BRANZ
Fire Lab
FL- MD101 - Open Burn Hood layout
Mechanical QA
|  |  |  | Open Burn Hood Ducting | Mechanical Duct | Fire Rated Duct Insulation
|  |  |  | Open Burn Hood | Radiant Heaters
FL- MD105 - ISO Hood layout
Mechanical QA
|  |  |  | ISO Hood Ducting | Mechanical Duct | Fire Rated Duct Insulation
|  |  |  | ISO Hood | Radiant Heaters

## Shared Storage
BRANZ
Shared Storage
SS- MD100 - Transformer room
Mechanical QA
|  |  |  | SS-EF2 | Fans | Labeling of Equipment

## Check Sheet( ITP's)
Check Sheet | Mechanical Duct
| Section | First Fix QA
Checkpoint
Check-off Shop Drawings. Is it all installed correctly: i.e.., each run complete.
Ducting / equipment connections including flexibles, nuts, bolts and washers correct and tight.
U/S of duct heights correct as per Workshop Drawings.
Ducts to be removed relocated / relocated as per drawings
Duct Hangers (is spacing correct, installed level etc)
Duct jointing (Joints sealed, cleats fitted etc)
Fire Dampers installed in open position c/w access panel.
Sound attenuators installed
Filter box installed
Transfer ducts installed
| Section | Second Fix QA
Checkpoint
Motorized dampers orientation to be installed correct way for sealing purpose
Access Panels to be installed as per drawing
All volume control dampers set fully open.
Butterfly and outlet dampers installed as per drawing and in open position.
Seismic bracing installed as per Drawing
|  |  |  | Section | Drawing Referance number
Pressure testing ( 10% of overall Ducted system ) ( Sudeshan please recent updated Leak test report Ilyas updated and add to this section )
| Section | Fit Off QA
Checkpoint
Flexible ducting installed c/w supports.
Correct Equipment / Correct Grills / Diffuser Installed
Check Sheet | Lab Gas Piping
| Section | Medical Gas QA
Checkpoint
Pipework Installed as per drawing ( CO2 , O2 , N2 , HE , ZA )
|  |  |  | Section | Installation done by
Name of person
|  |  | Pipe Brackets installed |  |  |  | Name of person
Pipe sizing is correct as per drawing / schematic
|  |  |  | Section | Schematic markup drawings
Valve arangment installed as per Detail specified drawing
Seismic Installation
|  |  |  | Section | Drawing Referance number
Gas cylinders installed as per drawing ie ( CO2 , O2 , N2 , HE , ZA )
Form B1 - Leak Test ( Sudeshan please use previous job "Hastings or Wellington " sheet that is in your library and add to this section )
Form B2 - Cross Connection Test ( Sudeshan please use previous job "Hastings or Wellington " sheet that is in your library and add to this section)
Form B3 - Total Compressed Gas system Test ( Sudeshan please use previous job "Hastings or Wellington " sheet that is in your library and add to this section)
Contractors Test reports
Check Sheet | Fire Dampers
| Section | First Fix QA
|  | Checkpoint | Correct FD Installed
Access Panel installed
| Section | Second Fix QA
Checkpoint
Drop Tested ( Sudeshan please use previous job sheet that is in your libary)
Track is Clear
Builder to Fire Sealed
Check Sheet | E4M - Mechanical Board ( MSSB )
| Section | E4M - Mechanical Board ( MSSB )
Checkpoint
Correct Equipment / plant installed
Switch Board Mounted in correct position and level
Switch Board terminations complete
Board Tested
COC's Complete
Check Sheet | Fans
| Section | Fans
Checkpoint
Correct Equipment / plant installed
Mountings / springs installed
Check-off Shop Drawings. Is it all installed correctly: i.e.., each run complete.
U/S of Fan heights correct as per Workshop Drawings.
| Section | E4M QA
|  | Checkpoint | Wiring First Fix Complete
Cable Tray Installed Correctly
Electrical Isolators installed in Correct location
Units Terminated
Temp Sensors and Controllers Installed
Units Tested and Running
Check Sheet | Fan Coil Units
| Section | Unit First Fix QA
|  | Checkpoint | Correct Unit Installed
u/s of Unit at correct height
Mounting and Springs Installed
Correct Hanger Spacing
Unit Secondt Fix QA
|  | Checkpoint | Unit Plenum Boxes to be installed
Filters installed
Siesmic Bracing Installed
|  |  |  | Section | Drawing Referance number
P - trap installed
Driptray installed
Condensate Drains installed
Tundish provided by others
Correct Fall to tundish , and water flow tested
| Section | E4M QA
|  | Checkpoint | Wiring First Fix Complete
Cable Tray Installed Correctly
Electrical Isolators installed in Correct location
Units Terminated
Temp Sensors and Controllers Installed
Units Tested and Running
Check Sheet | VAV's Boxes Ducted
| Section | Unit First Fix QA
|  | Checkpoint | Correct Unit Installed
u/s of Unit at correct height
Correct Hanger Spacing
Siesmic Bracing Installed
|  |  |  | Section | Drawing Referance number
| Section | E4M QA
|  | Checkpoint | Wiring First Fix Complete
Cable Tray Installed Correctly
Electrical Isolators installed in Correct location
Units Terminated
Temp Sensors and Controllers Installed
Units Tested and Running
Check Sheet | CHW & HHW Piping ( WELDING )
| Section | CHW & HHW Piping Welding
Checkpoint
Pipework installed as per Drawing
|  |  |  | Section | Installation done by
Name of person
All fabricators/welders are qualified and have current tickets
Pipe sizing is correct and valving in correct location
Valve arangment installed as per Detail specified drawing ie Chiller/ AHU / Pump / FCU / VAV / Buffer tank /Exspansion tank / Dosing Pod
Insulation blocks installed where required
Correct hanger spacing
Isolating and Control valve installed correctly
Hose piping installed
Air vents installed at all high points
All materials are in accordance with applicable AS/NZ standard
Welding procedure spectification to be applied as per attached
Steel is primed and weld painted after works are completed (PA10)
Welding of pipework
|  |  |  | Section | Photo of weld's
Pipework Seismic to be installed ( Exspantion joints , loops ect. )
|  |  |  | Section | Photo
Seismic Bracing Installed
|  |  |  | Section | Drawing Referance number
| Section | Pressure test
Checkpoint
Pressure Tested CHW & HHW pipe ( Sudeshan please use previous job sheet that is in your library and add to this section)
Check Sheet | CHW & HHW Piping ( VICTAULIC )
| Section | CHW & HHW Piping VICTAULIC
Checkpoint
Pipework installed as per Drawing
|  |  |  | Section | Installation done by
Name of person
All fabricators/welders are qualified and have current tickets
Pipe sizing is correct and valving in correct location
Valve arangment installed as per Detail specified drawing ie Chiller/ AHU / Pump / FCU / VAV / Buffer tank /Exspansion tank / Dosing Pod
Insulation blocks installed where required
Correct hanger spacing
Isolating and Control valve installed correctly
Hose piping installed
Air vents installed at all high points
All materials are in accordance with applicable AS/NZ standard
The pipe OD and groove dimensions are within tolerance range as per victaulic specification
The corect coupling has been used for the correct joint i.e flexible or rigid
All fitting are vicataulic approved
Victaulic grease has been applied to the gasket and OD of pipe
Couplings are tightened by alternating sides equally
Bolt pads havefirm metal to metal contact
Steel is primed and weld painted after works are completed (PA10)
Pipework Seismic to be installed ( Exspantion joints , loops ect. )
|  |  |  | Section | Photo
Seismic Bracing Installed
|  |  |  | Section | Drawing Referance number
| Section | Pressure test
Checkpoint
Pressure Tested CHW & HHW pipe ( Sudeshan please use previous job sheet that is in your library and add to this section)
Check Sheet | CHW & HHW Insulation
| Section | CHWH & HHP Insulation
Checkpoint
Approved material thickness has been used (Thermobreak®).
Insulation is installed as per the manufacturers recommendations, as well as per any additional requirements set out in the project specificaiton
Pipe sections firmly abutted to Insulation Blocks within the pipe supports, and Blocks have been glued
Insulation is glued to the pipe with a 50mm wide band of adhesive (Ados F2®) at both ends of section to form the vapour barrier
Adhesive is applied along all longitudional and circumferential joints
A 50mm wide strip of pressure sensitive tape reinforced aluminium tape is applied to the insulation facing, along and around all joints
Mitre cut elbows have been used on all bends.
Check Sheet | Condensate Insulation
| Section | Condensate Insulation
Checkpoint
Approved materials have been used (e.g. Elastomeric closed cell insulation), min 9m thick
Entire surface of pipe is covered from the indoor units' condensate trap, for a distance of 2m down the line
Adhesive is applied to any longitudional and circumferential joints, as well as to the ends of the insulaiton to the pipe
Finish circumferential joints by wrapping with 50mm wide pressure-sensitive pre-adhered PVC tape.
Check Sheet | External Duct Work Insulation
| Section | External Duct Work Insulation
Checkpoint
Insulate ducting as per drawing
Using Approved Insulation Ductwrap materials - Multitel 18kg Density foiled 1-side 25mm thick
Cover entire surface with insulation including all flanges,stiffeners and support angles.
Provide 50mm over lapping at all joints.
Tape all joints with 75mm width (72mm on the Market) Aluminium foiled tape.
Fixing for all Duct size 375mm to 750mm steel weld pins on centreline at 400mm spacing bottom surface only.
Fixing for all Duct size 750mm and greater steel weld pins at 400mm spacing maximum.
Fixing for all Duct riser steel weld pins at 400mm spacing maximum.
Using additional polypropylene fixing Bands 600mm centres.
Provide an overlap of atleast 300mm where insulation changes from the inside of the duct to the outside.
Check Sheet | Fire Rated Duct Insulation
| Section | Fire Rated Duct Work Insulation ( Fire Rated )
Checkpoint
Insulate ducting as per drawing
Using Approved Insulation Fire rated Ductwrap materials - 38mm thick Fyrewrap Elite 1.5 (FRL 120/120/120)
Install as per Manufacturer's Standards: (Trafalgar-Fyrewrap)
Fyrewrap duct wrap must completely covered the duct and there must not be any exposed sections or gaps.
A 100mm miniimum overlap must be used on all joints. Only the Three specified methods (telescope, checkerboard and butt splice methods.) of overlap may be used when adjoining Fyrewrap duct wraps.
Cut edges must be completely sealed with the specified pressure-sensitive aluminium foiled tape.
≤600 x600 duct size Steel banding only spacing 40mm from edges over the overlap and one additional between overlaps.
≤1200 x1200 duct size Steel banding and pins bottoms only spacing 40mm from edges over the overlap and one additional between overlaps. Pre-welded Pins grid 200mm centres.
≥1200 x1200 duct size pins only all sides of duct pre-welded Pins grid 200mm centres.
Wall penetrations up to 1600mm duct size 75mm x 75mm x1.6mm steel angle 100mm width x 60mm thick maxilite board.
Length of second layer from the fire barrier FRL 60/60/60
Duct size 600mm x 600mm or less -second layer 1350mm
Duct size 600mm x 1200mm or less -second layer 1600mm
Duct size 600mm x 600mm -second layer 1900mm
Duct size 200mm x 2400mm -second layer 2500mm
Duct size 2400mm x 3600mm -second layer 2700mm
Used only Trafalgar Access Panels -must be fitting directly over the existing duct access panels fixed with rivets and fyreflex fire rated sealant, with a second local layer of Fyrewrap.
Check Sheet | Internal Duct Work Insulation
| Section | Internal Duct Work Insulation
Checkpoint
Insulate ducting as per drawing
Using Approved Insulation Duct materials - Fibreglass
Fixed with Adhesive weld pins and speed clips located not more than 75mm from the edges of the ducts and spaced not more than 300mm centres.
Longitudinal corner joints fixed with:
duct dimensions less than 300mm -25mmx25mm angles
duct dimensions 300mm and greater -50mmx50mm angles
Joints taped between adjacent of insulation with a 75mm wide strip of reinforced aluminium foil laminate tape.
Tape joints protected with 75mm wide sheet metal cover strip, pop riveted to the corner angles.
Check Sheet | External Acoustic Insulation (FCU's)
| Section | External Acoustic Insulation (FCU's)
Checkpoint
Insulate ducting as per drawing
Using Approved Insulation Acoustic wrap materials - 50mm Polyester sheet cover with 5kg wave bar
Cover all surface of the FCU units with insulation excluding the Vents and pipe outlet area.
fixing using self adhesive pins and polypropylene Bands with with buckles .
Tape all joints with 50mm width reinforced Aluminium foiled tape.
Check Sheet | Metal Cladding
| Section | Metal Cladding
Checkpoint
Insulate ducting as per drawing
Approved materials have been used - 0.6mm galvanised sheet metal, or 0.8mm stucco embossed aluminium
Min. 40mm overlap has been provided on longitudional and circumferential joints
Coned down ends of sheathing have been provided where insulation has been specified as being coned down
All bends have been neatly cut and formed into lobster-back segments
In applications not involving a vapour barrier, pop rivets are provided through pre-drilled holes
In applications involving vapour barrier, 12mm wide straps of 0.4mm sheet metal are used to secure cladding
Straps on straight lengths are no fewer than 3 on each section, c/w locking buckles
Suitcase Clips' are used for all readily removable items such as evaporator heads, strainers, etc which require access for routine maintenance
Penetraitons are sealed for gauges, instruments, and drain vents (silicone)
Check Sheet | Braze Bench Test
| Section | Braze Bench Test
Checkpoint
Test Sheet ( Sudeshan please use previous job sheet that is in your library and add to this section)
Med Lab Results
Checkpoint
Document of Results
Check Sheet | DX Units
| Section | DX Units
|  | Checkpoint | Correct Unit Installed
Out door Unit Installed
u/s of Unit at correct height
Mounting and Springs Installed
Pipe Cable Tray Installed Correctly
Correct Hanger Spacing
Unit Plenum Boxes to be installed
Refrigeration Pipework installed as per drawings
|  |  |  | Section | Installation done by
|  |  |  | Section | Pipework Installed from DX unit box to Outdoor unit
Schematic markupsdrawings
Condensate Piping installed
Tundish installed by others and connected up
Pressure Tested
|  |  |  | Section | Signed off By AE Smith
[7 empty] | Name of person | Date
|  |  |  | Section | Photo's of Pressure test
[7 empty] | Start of Pressure test |  | Time / Date
[7 empty] | Pressure test after recored Duration |  | Time / Date
Vacuum system down below 500 Microns
Triple Evacuation procedure to be done
Refrigeration ( Scale ) charge unit completed - According to Calculatio for Pipe Size & Length
Insulation Complete for Piping and Condensate lines
Siesmic Bracing Installed
|  |  |  | Section | Drawing Referance number
| Section | Unit Second Fix QA
|  | Checkpoint | Filters Installed
Grilles Installed
Commissioning Complete
| Section | E4M QA
|  | Checkpoint | Wiring First Fix Complete
Cable Tray Installed Correctly
Electrical Isolators installed in Correct location
Units Terminated
Temp Sensors and Controllers Installed
Units Tested and Running
Do not energize DX unit until commisioning , otherwize all solinoid will close resulting in no evacuation of Moisture from Indoor units
Check Sheet | Cowls
| Section | Cowls
|  | Checkpoint | Outside Air Roof Cowl Installed
Builder - Waterproof and Seal to be installed
Check Sheet | Heater banks
| Section | Heater banks
Checkpoint
Correct Equipment / plant installed
Mountings / springs installed
Check-off Shop Drawings. Is it all installed correctly: i.e.., each run complete.
U/S of Equipemnt heights correct as per Workshop Drawings.
| Section | Second Fix QA
|  | Checkpoint | Fire rated insulation installed as per spec
| Section | E4M QA
|  | Checkpoint | Wiring First Fix Complete
Cable Tray Installed Correctly
Electrical Isolators installed in Correct location
Units Terminated
Temp Sensors and Controllers Installed
Units Tested and Running
Check Sheet | Radiant Heaters
| Section | Radiant Heaters
Checkpoint
Correct Equipment / plant installed
Mountings / springs installed
Check-off Shop Drawings. Is it all installed correctly: i.e.., each run complete.
U/S of Equipemnt heights correct as per Workshop Drawings.
| Section | E4M QA
|  | Checkpoint | Wiring First Fix Complete
Cable Tray Installed Correctly
Electrical Isolators installed in Correct location
Units Terminated
Temp Sensors and Controllers Installed
Units Tested and Running
Check Sheet | AHU's
| Section | AHU's
Checkpoint
Check if plinth site is correct
Correct Unit Installed
Setting out point correct
Anti Vibration pads to be installed
Condensate Piping installed
Tundish installed by others and connected up
Insulation Complete for Piping and Condensate lines
Siesmic Bracing Installed
|  |  |  | Section | Drawing Referance number
| Section | Unit Second Fix QA
|  | Checkpoint | Filters Installed
Commissioning Complete
| Section | E4M QA
|  | Checkpoint | Wiring First Fix Complete
Cable Tray Installed Correctly
Electrical Isolators installed in Correct location
Units Terminated
Temp Sensors and Controllers Installed
Units Tested and Running
Check Sheet | Chillers / Buffer Tank / Dosing Pod / Pumps
| Section | Equipment QA
Checkpoint
Check if plinth site is correct
Correct Unit Installed
Setting out point correct
Anti Vibration pads to be installed if required
Corrrect Springs installed ( If required )
| Section | Unit Second Fix QA
Checkpoint
Condensate Piping installed ( If required )
Tundish installed by others and connected up ( If required )
Siesmic Bracing Installed
|  |  |  | Section | Drawing Referance number
Check Sheet | E4M QA
| Section | E4M QA
|  | Checkpoint | Wiring First Fix Complete
Cable Tray Installed Correctly
Electrical Isolators installed in Correct location
Units Terminated
Temp Sensors and Controllers Installed
Units Tested and Running
Check Sheet | Labeling of Equipment
| Section | Labeling of Equipment
Checkpoint
Corect label installed as per referance on Equipment / Drawing
|  |  |  | Section | Photo
Label visable
Correct directional arrows / colour coding installed on system
|  |  |  | Section | Photo
Check Sheet | Duct / Equipment Cleaning
| Section | Duct / Equipment Cleaning ( Air Restore )
Checkpoint
Specialized Cleaning contractor to clean Outdoor / Supply and Return air Ducting and equipment in accordance with HVCA Guide TR/19 or NADCA Standard 1992-01
Verification of ductwork cleanliness shall be by vacuum test ( gravimetric analysis ) in accordance with HVCA Guide TR/19 or NADCA Standard 1992-01
Undertake a second vacuum test immediately prior to handover.