## Resources
Rich Type | Id | Warnings | type | name | values | prefix | postfix | Usage Count | User Addable | Template Name | Template Id
checklist-flat |  |  | checklist | Defect ITP |  |  |  |  | Yes | Defect ITP | 20b308ee-fde2-4780-997b-aa8df66cb877
checkpoint-status |  |  | checkpoint | Take photos or documents & comment where applicable
select | 106fe0e4-45a6-5cdf-9eba-e660716986c3 |  | dropdown | Dilap | Existing Cracks in ceiling, Existing Damage in cabinetry, Existing Damage in gyprock walls, Existing Stains/damage to carpets, Existing damage to benchtops, Existing damage to stove/oven, Other
text | b315f4c3-2ad7-59d1-a6b8-3cb5fdfe26d5 |  | textbox | FD/Penetration No
select | 5f93ea9b-655b-59dc-9551-cc76b8baee61 |  | dropdown | Ceiling Access Panel | Pass - Accessible, FAIL - Not accessible, FAIL - Relocate Ceiling AP, FAIL - Install NEW Ceiling AP, Other
select | 5ba4e49b-4460-5c96-aab7-945707295505 |  | dropdown | Duct Access Panel | PASS - Not Required, PASS - Existing Duct AP is COMPLIANT, FAIL - Relocate Existing Duct AP, FAIL - Install new Duct AP, Other
select | bd7b4fba-efa1-5ae4-8689-20b16dbb2336 |  | dropdown | Damper Type | Intumescent FD, Mechanical Curtain FD, Slab FD, Ventilation Damper, Other
select | 2ea3c58e-61c3-5979-94fe-9484412f6477 |  | dropdown | Wall type | Masonry/Concrete, Hebel, Speed Panel, FR Plasterboard, Other
select | 8fa19d67-a7f8-559b-81c8-602a8344bfbc |  | dropdown | Shape | Round, Rectangle, Other
select | 70f98dd7-0432-5992-a9fd-7715816de68a |  | dropdown | Tested System Ref # | Yes - attach system number, Not known, Other
select | b7a8e6b6-9fc2-5cc3-b03c-4fe785731893 |  | dropdown | Angle System | Square - 2 sides, Square - 3 sides, Square - 4 sides, V- shape, Other
select | ea0db552-7ba7-5574-a945-ffc08da37860 |  | dropdown | Angle Installation | Obstructed- behind Gyprock, Pass - clear unobstructed view, Angles CORNERS within 5mm gap, Angle FLUSH to wall, Other
select | cf4ea085-cedf-5a28-b47e-5709df546fcf |  | dropdown | Mastic | Manufacturer approved Mastic - YES, Mastic type UNKNOWN, Manufacturer approved Mastic - NO, Bead complete - No gaps/ shrinkage, Mastic Bead - FAIL, Depth of Mastic 25mm - PASS, Depth of Mastic 25mm - FAIL, Other
select | 0965343a-7eb8-5135-a745-8120a1067d09 |  | dropdown | Breakaway joint | PASS - less than 150mm from walls, FAIL - More than 150mm from walls, PASS - Nylon bolts/Rivets, FAIL - BOLTS non compliant, Other
select | 8864f915-772e-5e10-914a-40d59c119063 |  | dropdown | Actuators | PASS - Accessible, FAIL - Not accessible, PASS - ROTATE Actuator, Other
select | 54795467-fabe-5eef-baf0-0868bc69a008 |  | dropdown | Bathroom - Airflow Reading L/sec | Test 1# Pass, Test #1 Fail, Other
select | 068268b2-233a-52ba-bacf-e894f26ad344 |  | dropdown | Ensuite - Airflow Reading L/sec | Test 2# Pass, Test #2 Fail, Other
select | 68c24e2b-a7ed-57a5-b965-19988303881e |  | dropdown | Laundry - Airflow Reading L/sec | Test 3# Pass, Test #3 Fail, Fail - Laundry - FILTER BLOCKED, PASS - Laundry FILTER OPEN, Other