## Commissioning
AE-ITCX-XXX - ELECTRICAL SERVICES COMMISSIONING
Documentation to proceed with commissioning
Notes
AE-FORM-006 - Builders Works Completion Notice' been completed? | O Yes | Photo/Upload of AE-FORM-006
AE-FORM-011 - Notice of Intent to Energise Electrical Installation' been completed? | O Yes | Photo/Upload of AE-FORM-011
AE-FORM-009 - Start card been filled out by all workers within the commissioning crew? | O Yes | Photo/Upload of AE-FORM-009
Rough In/ Fit Off QA been reviewed and utilised for commissioning QA? | O Yes O No
HOLD POINT
Switchboard
Notes
All screw terminations tight, with copper not visibly out of terminal? | O Yes
Neutrals correspond with actives? | O Yes
Pole fillers installed? | O Yes
DB door and eschucheon scratch and defect free? | O Yes
Switchboard labelled and cleaned? | O Yes
Cable entry points fire sealed? | O Yes O NA
All circuits RCD protected? if answer is no confirm in note section the circuit number and reason for no protection. | O Yes
BMU circuits protected by a 100mA RCD? | O Yes O NA
Correct lighting control schematic and schedule installed? | O Yes O NA
Correct lighting control equipment installed? | O Yes O NA
Appselec 'installed by' sticker installed? | O Yes
Warning: Interupting power supply will discharge emergency lighting batteries' installed next to RCBO feeding emergency lighting? | O Yes O NA
Energy Meter been installed with CT metering? | O Yes O NA
Wiring goes through the correct CT, installed in the correct direction and terminated to the correct phase? | O Yes O NA
Wiring neatly loomed internally and externally of the DB? | O Yes O NA
Lighting control and timers set to the documented schedule and labelled? | O Yes O NA
Contactors functioning correctly? | O Yes O NA
Surge arrestors installed and switched on upon completion of commissioning? | O Yes O NA
Cables mechanicaly protected external of DB where applicable? | O Yes O NA
Manual test of ATS/load shedding contactor completed to confirm power drops out to the correct circuits? | O Yes O NA
Fire rating complete to all risers? | O Yes O NA
Air sealing complete under floors? | O Yes O NA
Mandatory Photo 1 - Accurate DB schedule matching installation
Mandatory Photo 2- DB Name (N/A for apartment DB) | O NA
Mandatory Photo 3 - DB Installation and surrounds
Mandatory Photo 4 - DB with eschucheon
Mandatory Photo 5- DB without eschucheon showing wiring
Mandatory Photo 6 - Upload - NP COES
Additional photos
General - Final review
Outlets, switches and other equipment installed straight, level, in the correct location and mounting height? | O Yes
Outlets, switches and other equipment either fit off or made safe? | O Yes
Master switch operates documented items? | O Yes O NA
Electric appliances switching correctly? | O Yes O NA
AC/FCU control functions correctly? | O Yes O NA
Electric cooktop has a visible isolation switch in accordance with AS3000? | O Yes O NA
Exhaust fans function correctly? Where a fan is switched from multiple locations, double pole mechs are installed to prevent the “back feeding” of lights in the other spaces? | O Yes O NA
All outlets labelled correcly? | O Yes O NA
Mandatory photo - Accurate asbuilt drawings upon completion of commissioning including variations, site changes, driver and puk locations?
Additional photos
Variations/Purchaser Changes
Is there variations within zone? (If you are unsure confirm with your Site Manager) | O Yes O NA
All variations captured on an As-Built? | O Yes O NA
Lighting control
General
Lighting control function as per the documented functional description? | O Yes O NA
Dimmers function correctly? Applicable lights dim smoothly without strobing? | O Yes O NA
Lights correctly switching, including 2-ways and intermediates? | O Yes O NA
Neons correctly switching? (plantroom switches etc.) | O Yes O NA
Dali fittings flash tested and confirmed they are in the correct dali zones? | O Yes O NA
Black out test completed for PE cell and fittings functioning correctly? | O Yes O NA
Motion detectors tested independantly of one another? | O Yes O NA
Motion detectors un-obstructed from functioning correctly? | O Yes O NA
Motion detectors switch correct fittings/zones? | O Yes O NA
Motion detectors set to nominated time once commissiong complete? | O Yes O NA
Emergency lighting
Dali emergencies flash tested? | O Yes O NA
120min battery discharge test completed and documented? | O Yes O NA
Exit and emergencies numbered on the asbuilt? | O Yes O NA
Exit and emergencies labelled on the fitting and numbers match the asbuilt drawing? | O Yes O NA
Mandatory photo - Accurate asbuilt drawings upon completion of commissioning including variations, site changes, driver and puk locations?
Additional photos
UPS System
UPS backing up the correct circuits? | O Yes O NA
UPS transfer switch is functioning correctly when power supply is interupted? | O Yes O NA
Circuits backed up by the UPS continue to have power when power is interupted? | O Yes O NA
Load test completed and results recorded? | O Yes O NA
Labelling of outlets complete? | O Yes O NA
Mandatory photo - Accurate asbuilt drawings upon completion of commissioning including variations, site changes?
Additional photos
Documentation
All circuits locked/tagged out been entered into the AE-FORM-010 - Isolation Tag Register? | O Yes O NA
Mandatory photo - Isolation tag register?