## Resources
Rich Type | Id | Warnings | type | name | values | prefix | postfix | Usage Count | User Addable | Template Name | Template Id
checklist-flat | 53828f73-9ec5-4f2c-a3ef-0974975bad18 |  | checklist | Fire Extinguishers |  |  |  |  | Yes | Fire Extinguishers | 19608ce3-cd09-44e4-a79f-3774e1f33f5b
checkpoint-status | 6b62e331-2258-432e-b8a1-9517369644f0 |  | checkpoint | Construction drawings approved for use.
checkpoint-status | 13029b2e-14be-4ef7-8895-f5f002910328 |  | checkpoint | Manufactured &Installed to AS/1841; NZS 4503: 2005
checkpoint-status | bb4c2f3c-ae8d-4307-8bc9-f1556a7803fe |  | checkpoint | Correct Type & Size Installed
checkpoint-status | 39446a93-259c-4fa5-98d4-306df151dee9 |  | checkpoint | Water
boolean | 923e4b44-b050-58ec-9495-6813068de58a |  | tickbox | 4.5kg
boolean | c2cfd916-2e0d-58da-91be-a3d99129e257 |  | tickbox | 9.0 Kg
boolean | 303df58f-8938-5f49-be37-04c6cbc09824 |  | tickbox | Other
checkpoint-status | 3f2a81de-d595-40a5-8676-4b5ab1543c84 |  | checkpoint | Carbon Dioxide
boolean | 323d27b1-772b-535a-98a2-6726221b3053 |  | tickbox | 4.5kg
boolean | e96a2283-8167-5ccf-b316-eb3338f6b4d9 |  | tickbox | 9.0 Kg
boolean | 01f646a2-0533-5fff-b463-c5df16608c35 |  | tickbox | Other
checkpoint-status | 119c53d4-99b6-4830-ac8a-5ad0270f5492 |  | checkpoint | BE Powder
boolean | 6c0944bf-fa64-532b-8cc4-ab4be05e940e |  | tickbox | 4.5kg
boolean | 73759cee-00a5-514c-87bc-cbe5e893f4d9 |  | tickbox | 9.0 Kg
boolean | 7c08aae1-bb4d-50a6-b988-ef7f129ebbba |  | tickbox | Other
checkpoint-status | 421c354f-d974-42a0-bef4-d18402138898 |  | checkpoint | ABE Powder
boolean | ec42e17f-ba34-595b-8cb6-8c53eb1065c1 |  | tickbox | 4.5kg
boolean | 2db6bf1c-3364-5e6d-9da3-881cfddfff79 |  | tickbox | 9.0 Kg
boolean | 7557dde7-3030-5c72-85c5-0a20487c87c2 |  | tickbox | Other
checkpoint-status | a5bd9606-7bf0-4aac-bebc-24d8a7fc8453 |  | checkpoint | Foam
boolean | 5695b9f0-3cad-5116-b2b2-6ecdea003c59 |  | tickbox | 4.5kg
boolean | aefdf009-a7b8-5b6c-abc5-36eff916afd4 |  | tickbox | 9.0 Kg
boolean | 212ee393-c223-5b39-8948-19c98055f27a |  | tickbox | Other
checkpoint-status | 12730e70-a07b-43b1-a943-e8f86157f386 |  | checkpoint | Wet Chemical
boolean | fd8d39e7-41be-5f2f-a768-92c77f98650c |  | tickbox | 4.5kg
boolean | 39a78cfe-798c-5316-96b5-fc4b45dec85f |  | tickbox | 9.0 Kg
boolean | e0521026-c996-52ee-9d88-4bb9bf1e44d0 |  | tickbox | Other
checkpoint-status | 0fecd34c-3c80-477a-b59b-f3dad46c6447 |  | checkpoint | Other
boolean | ff2265c9-9a5a-5f6d-9150-b379193a80a0 |  | tickbox | 4.5kg
boolean | a873e2ad-a6a4-500d-8865-13295022c6a7 |  | tickbox | 9.0 Kg
boolean | 3acfac1a-e0a8-51c0-be43-9671692fbff1 |  | tickbox | Other
checklist-flat | 0e213708-163b-4812-b56a-a628eaf3508a |  | checklist | Fire Alarm First Fix - 202p |  |  |  |  | Yes | Fire Alarm First Fix - 202p | 2af47bad-d9a9-42f7-a763-b9997ac65788
checkpoint-status | c2688e15-6b34-4b4f-8a6b-07fd16062bb8 |  | checkpoint | Ceiling cabling/ In place and secured
checkpoint-status | e12a40f8-3e58-49d0-9d7b-8be6fb5d45fc |  | checkpoint | Wall cabling/ In place and secure
checkpoint-status | 4d53010a-c30a-44a2-b248-c7bbf7df1d06 |  | checkpoint | Detector heads cable loops in approved locations
checkpoint-status | 93489beb-d569-4e41-a386-5ce2c1b1b7ee |  | checkpoint | MCP cable in approved locations
checkpoint-status | 228cf5e8-bdcf-43b5-ae01-a962a4cdfad9 |  | checkpoint | Speaker cable in correct locations
checkpoint-status | 259f03a9-b552-4093-ad28-a78f8d622273 |  | checkpoint | Interface Modules in approved locations
checkpoint-status | cacc027a-06da-4590-aab4-01da68fdabf4 |  | checkpoint | Sign off by AMF
text | 43fe4e3a-c77c-5e3d-a8a8-9efad43768f1 |  | textbox | Witness Name (If Applicable)
checklist-flat | 97831a42-3924-4574-8950-de0d6f935e62 |  | checklist | Fire Alarm Tunnel Commissioning |  |  |  |  | Yes | Fire Alarm Tunnel Commissioning | 43c08b44-c8b0-4f07-8177-e375651ec8b9
checkpoint-status | 18e0fc1b-93db-479c-a674-b743794e7181 |  | checkpoint | Call Service Agent
checkpoint-status | 3ca48a83-7d41-44ae-9686-29f99342e1a6 |  | checkpoint | FACP Notification
checkpoint-status | 4425db06-aa81-499b-adf8-2d0e72348f73 |  | checkpoint | Correct Mimic & LCD indication
checkpoint-status | 4c1a8213-1498-482e-bc91-66ba5b14458e |  | checkpoint | Correct BMS Signal
checkpoint-status | e7fc47d3-a7f5-44dc-b5d1-62af07cccda3 |  | checkpoint | National Train Control Signal
checkpoint-status | 0c485d98-9fbb-48db-afe9-d635170c004f |  | checkpoint | Station Group Control Centre
checkpoint-status | 6369607e-2000-4bbd-abf8-12592db0e486 |  | checkpoint | Paging Notification
checkpoint-status | fec5c1a2-04af-4f46-a8a3-d22fbdefdd1d |  | checkpoint | Staff Investigate Signal
checklist-flat | 113315fe-3270-4912-b6d7-65a7e64b6643 |  | checklist | Gas Flood Alarm Second Fix |  |  |  |  | Yes | Gas Flood Alarm Second Fix | 47a4c7d8-d765-4811-a050-621ccfaab45f
checkpoint-status | cac63487-a548-4c90-872a-26151fd12156 |  | checkpoint | Control Panel Installed
checkpoint-status | 7bd82489-6f93-42cd-9567-3be7a133e0de |  | checkpoint | Detectors Installed
checkpoint-status | 10745b0f-87ba-4437-a78f-2a737712c24c |  | checkpoint | Gas Start/ Stop Override Installed
checkpoint-status | 128b2aea-490a-4f9f-90e1-67d07f0b94ac |  | checkpoint | Visual/ Audio warning signs installed
checkpoint-status | 54cf7e8c-2eb5-4ea0-9b5a-5ba031c9ec92 |  | checkpoint | Pressure Switch & Actuator Connected
checkpoint-status | 97a16889-7b8f-467c-bda6-283b7ad32e03 |  | checkpoint | VESDA Sampling Points Installed
checkpoint-status | 95b1230c-8153-4848-bca0-2b67a0400227 |  | checkpoint | Interface Modules Installed
checkpoint-status | 99342fe9-e1dc-4042-ba1b-7eb31fbaf864 |  | checkpoint | Sign off by AMF
text | b7f328ec-8162-5fa6-9fc8-591493518e10 |  | textbox | Witness Name (If Applicable)
checklist-flat | fce3c4b2-65c0-4293-b97b-8325d5c23d05 |  | checklist | Gas Flood Alarm First Fix |  |  |  |  | Yes | Gas Flood Alarm First Fix | 62ca5240-e179-4666-889d-ca524b496a99
checkpoint-status | aa105980-9524-4f88-8777-f00432a9dc51 |  | checkpoint | Design Complete & Approved
checkpoint-status | b7abc3bc-07fb-41e7-a10d-619f6946c331 |  | checkpoint | Ceiling cabling/ In place and secure
checkpoint-status | 66c2e6d7-5a16-445f-9062-8cd93cceed35 |  | checkpoint | Wall cabling/ In place and secure
checkpoint-status | 310a9c7c-f9e9-44b5-a416-adde4ea20d3d |  | checkpoint | Detector heads cable loops in approved locations
checkpoint-status | 317249cc-987f-43d4-8c33-421011c920c8 |  | checkpoint | Gas Start/ Gas Stop override cable in place
checkpoint-status | a605a191-6ad5-4a1a-ae40-cb5d65d51b52 |  | checkpoint | Visual/ Audio warning signs cable in approved locations
checkpoint-status | 7a5521e0-a390-4dc5-9e06-44ed2aa26ad1 |  | checkpoint | Interface Modules in approved locations
checkpoint-status | ae460104-598d-4a50-bbaf-63c65c82cd8c |  | checkpoint | Pressure Switch & Actuator Cables in correct location
checkpoint-status | 3ea1c05f-bc08-4184-8cfe-c68550969a30 |  | checkpoint | VEDSA Pipe installed correctly in approved locations
checkpoint-status | a5b26f5f-e00f-477a-9970-1aac1964ae4f |  | checkpoint | Sign off by AMF
text | 08bada2d-0331-5446-b34e-fd4bf0843a9f |  | textbox | Witness Name (If Applicable)
checklist-flat | 3a49b43f-3e27-4b2f-a61f-e6517242c49e |  | checklist | Gas Flood Mechanical Second Fix |  |  |  |  | Yes | Gas Flood Mechanical Second Fix | 79732912-e5bf-43cf-b7f7-5280fd4c2037
checkpoint-status | 1e15c01a-6d0f-4b7a-bf62-5e140695b63c |  | checkpoint | All Nozzles positions as per design
checkpoint-status | 182d94fc-1b3c-433d-bb86-17799e719365 |  | checkpoint | Fitted with PTFE tape & correctly tightened
checkpoint-status | 441232dc-5913-4300-8e4c-be355c88ab0b |  | checkpoint | Escutcheon plates or discharge shrouds fitted
checkpoint-status | 7195ccce-fd65-4315-af73-c0a5d071c2b7 |  | checkpoint | Cylinder Frame bolted down securely
checkpoint-status | 04ad3d0e-bddf-45da-bca3-f157c24de4a3 |  | checkpoint | Cylinder Manifold Secured, Hoses Connected & Tightened, End Plug tight (if required)
checkpoint-status | 76e96adf-3b10-4611-a434-437cb2099c35 |  | checkpoint | Cylinders orientation as per design, secured in frame & tightened, discharge caps correct orientation & secure
checkpoint-status | c8a924df-6a39-471c-b6dd-cebe2458cb3b |  | checkpoint | Orifice Unit & Union correct orientation and secure
checkpoint-status | 73d9a2ac-47cd-4f9f-b2b5-b978d8865c68 |  | checkpoint | Mechanical manual gas release installed correctly
checkpoint-status | 37df9947-ca91-4aad-8f49-5cf556cc8fe9 |  | checkpoint | Actuators in place ready to mount on cylinder
checkpoint-status | f47722e6-afea-49dd-b0c3-dcdf1e66f1d1 |  | checkpoint | Sign off by AMF
text | 65505c99-83ef-52ba-9de3-b8a210bd5c01 |  | textbox | Witness Name (If Applicable)
checklist-sectioned | 69e1b2ff-6c3a-412b-8805-f486a458192d |  | checklist | Attendance Point Commissioning |  |  |  |  | Yes | Attendance Point Commissioning | 79e95c4e-af75-42b6-b2f6-12fde5697870
checkpoint-group | 34747bc4-8a6a-4696-906e-b36781721bd9 |  | section | Fire Service Inlet
checkpoint-status | d9944149-6793-46c5-aedc-2e83c917874f |  | checkpoint | FSI
checkpoint-status | 14ffca2f-172a-4d40-ac02-ad919f01ca8f |  | checkpoint | Cabinet Door
checkpoint-status | 1e63dc4a-2bf0-4217-8ba8-7cb5fabb9bcb |  | checkpoint | Backing And Drain Installed
checkpoint-status | b4ab0f2d-6e3b-45ec-b83c-e58c6529625a |  | checkpoint | Door Label Satisfactory
checkpoint-status | 8ab1c731-e5ce-4336-bde9-8cebbd8039b9 |  | checkpoint | Open Before Pumping Sign
checkpoint-status | 0576e7f6-5e64-4ae8-8a58-668b20fb8347 |  | checkpoint | Piped To Above Control Valves
checkpoint-status | 928a05bf-b811-4f7e-bf81-6f6401ac99fc |  | checkpoint | External Drainage Satisfactory
checkpoint-status | 13fb2368-3283-4e83-ac31-6f1e253c673e |  | checkpoint | Remote Gauge Fitted
checkpoint-status | 55054dc8-3c5b-4817-81af-eaee830b34c9 |  | checkpoint | Remote Gauge Shaded
checkpoint-status | c91ae667-17b6-41f6-a17f-9bee15421add |  | checkpoint | Installation Gauge Shaded In Lieu
checkpoint-status | c50ec35a-a664-456f-9bd8-3ad3149230b0 |  | checkpoint | “Boost In Red Zone” Signage
checkpoint-status | 023362b0-d2ad-4ada-a336-c18b92639040 |  | checkpoint | Permanent Outlet > 3500 L/Min
checkpoint-group | a24cc4df-edb1-44cb-a338-902e28d86842 |  | section | Pressure Gauges
checkpoint-status | d22d47f4-98fd-485c-982b-daa6888ab7df |  | checkpoint | Installation Gauge Fitted
checkpoint-status | 7d0c6168-7fe4-4e79-a252-8e9202ef7274 |  | checkpoint | Primary Gauge Fitted
checkpoint-status | 932ced89-5b19-4141-86bd-d55e3f06a6c5 |  | checkpoint | Secondary Gauge Fitted
checkpoint-status | 97ffe55b-8f21-41c1-ba84-62bbc0014fb1 |  | checkpoint | Combined Gauge Fitted
checkpoint-status | 90274459-ab18-4f23-ba5c-f4d0a1a49985 |  | checkpoint | Dba Gauge Fitted
checkpoint-status | bf2bae3b-abd5-4165-9768-e3dd04f9ec90 |  | checkpoint | Dial Marings And Labelling Correct
checkpoint-status | ad476730-95e2-4788-88bf-5be9b71e4be6 |  | checkpoint | Accuracy – ± 3% Full Scale
checkpoint-status | b28136f1-9f54-4fea-8694-8b6ee9492fb0 |  | checkpoint | Gauge Cocks Fitted
checkpoint-group | 027366d2-118e-406d-8d94-aed88b7b04f9 |  | section | Water Supplies
checkpoint-status | 0485b900-119a-4060-a3bd-4ba3bd2e96b9 |  | checkpoint | Town Main Toby Box Accessible
checkpoint-status | afa71bdb-32f4-4643-baa9-d1028a23d9f5 |  | checkpoint | Street Valves Open
checkpoint-status | c11b4952-ad73-4842-922e-a747db336a85 |  | checkpoint | Hose Reel Valve Labelled And Strapped Open
checkpoint-status | 74e7aaa4-f9f5-40ff-a572-e0365b78070c |  | checkpoint | Strainer Installed (> 2300 L/Min) And Pressure Gauge Upstream
checkpoint-status | 42cea928-c5c8-4e2b-8eb8-4dfdaebdfe6c |  | checkpoint | Stored Water Capacity Adequate
checkpoint-status | f9304b7b-cab0-4325-a73b-978bb06422fb |  | checkpoint | Tank/S Crack Free, Water Tight
checkpoint-status | a9268501-5277-4e9e-beba-c63158ca0146 |  | checkpoint | Overflow Adequate
checkpoint-status | a4297c0b-091a-4cc3-82ab-832b2b048854 |  | checkpoint | Level Correct In Tank
checkpoint-status | 2ea40d0e-faf7-4de9-8444-c611b527da8e |  | checkpoint | Level Indicator Correct
checkpoint-status | 8c6aaf2e-ad7d-46d3-bc45-50fe423b616a |  | checkpoint | Water Clean And Clear
checkpoint-status | 5867a512-d85c-40e9-8e7e-6edf6c52cc69 |  | checkpoint | Top Up Inflow Operational
checkpoint-status | 0eb1e212-0269-4054-ab09-3e7a5acbb836 |  | checkpoint | Outlet Stop Valve Strapped Open
checkpoint-status | c9626226-c41d-4001-b10d-631d04aa5726 |  | checkpoint | Strainer Fitted Correctly
checkpoint-group | a5e7c1b6-9018-4c88-b791-d5a4e446fb17 |  | section | Back Flow Prevention
checkpoint-status | e440a490-5975-472d-95d9-3e544479c6ea |  | checkpoint | Isolate Valves Fitted / Anti Interferance
checkpoint-status | ab4a8baa-8670-4ca5-8e9e-6e8eeacdb3ab |  | checkpoint | Testable Unit
checkpoint-status | bbefe704-e443-4424-bb67-5daa3b29bc7e |  | checkpoint | Anti Interference Gear Signals Fire
checkpoint-group | 0e3c18d8-de13-4059-a315-fc5a6a51fc67 |  | section | Fire Hydrant Inlet
checkpoint-status | f802413f-5426-4d6b-8f87-d09286a4280e |  | checkpoint | Inlet Height Between 600mm min – 1350mm max
checkpoint-status | 7bddf866-7001-44e2-80a8-26cda4e7a1bf |  | checkpoint | Inlet Coupling Clearance 75mm min
checkpoint-status | 5118650d-dfb2-4f05-ad66-e0fdd4c50444 |  | checkpoint | Inlet Gauge Installed & Labelled
checkpoint-status | bcb6837c-0a57-40fb-aac6-2d2ca7eca0ab |  | checkpoint | Splash Guard Installed
checkpoint-status | 585cc7fe-7dee-4c3c-9e39-58a72b41f786 |  | checkpoint | Pump Start Switch Installed
checkpoint-group | 4a943992-fcfd-4565-8bd7-393aad207a25 |  | section | Water Supply
checkpoint-status | e3ed72a6-7f9d-4aba-90ff-a4b94d679ec1 |  | checkpoint | Charging Line Installed & Locked Open with water meter.
checkpoint-status | 4dbc75d5-61df-4281-9362-45bb83febaad |  | checkpoint | System Drain Installed & Locked Closed
checklist-flat | 3fe7ad6f-c6d3-41bf-b7e1-e4ccfd501c56 |  | checklist | Fire Sprinkler First Fix |  |  |  |  | Yes | Fire Sprinkler First Fix | 8b6c7cfa-5c6c-4cbf-bca1-513a93809b23
checkpoint-status | 1c264d5a-2ff4-49b0-a4e7-e8be561c39aa |  | checkpoint | Construction drawings approved for use.
checkpoint-status | 28ef3656-07f1-4a71-a59a-f258f2fdba8a |  | checkpoint | Black / Galv. / Primed Mild Steel to:
label | 89c6521e-b057-5c40-8591-67fc9acec6af |  | note | NZS/BS 1387:1387
label | 8f83fdfe-8e24-5235-83f4-d1e7d82c38a3 |  | note | AS1074 Medium
checkpoint-status | 98f3c54f-5127-49a9-a007-487baa496c20 |  | checkpoint | Sprinkler heads As Specified
checkpoint-status | 252b6a37-7c66-48f4-9e7c-f8a4ee07262a |  | checkpoint | Sprinkler heads Type
checkpoint-status | 6f646790-e220-4c24-82ce-544411d1c127 |  | checkpoint | In ceiling sprinklers installed
checkpoint-status | bd092fe5-05c8-4092-a765-138b6053dc0c |  | checkpoint | Flexible Drops installed
checkpoint-status | b55160b1-5f7c-4869-a5ee-430d8f452ea6 |  | checkpoint | Hanger Spacing
checkpoint-status | ee4c3aad-f5fd-45f2-91bf-ea98fab6a013 |  | checkpoint | Seismic restraint’s Hangers
checkpoint-status | a668b4a9-73d3-456f-8965-a3d3cd500b7d |  | checkpoint | Pipework Finish as specified
checkpoint-status | 2c7ec2e2-a0e3-455c-88fc-5400badf4ecb |  | checkpoint | Pipework installed as per drawing.
checkpoint-status | a54d813e-f1e2-4ce8-a7d8-5438608d054e |  | checkpoint | Seismic Breaks
checkpoint-status | 84a35e58-a86d-423d-aca0-d70d9dd65735 |  | checkpoint | Touch up paint
checkpoint-status | 454d9b34-4608-419c-a03b-68d5fe19206a |  | checkpoint | Pipework Tested Air & Water
text | 24d40bc7-6104-5bb8-bbd0-50ef1412506a |  | textbox | Start Time:
text | 7a752225-22b0-5a6f-a144-e93fc97cf84d |  | textbox | Start Pressure:
text | 7b8ee733-5b98-55e6-9e3b-9f1e91355980 |  | textbox | Finish Time:
text | 136c6508-f94c-5932-80ae-bd49cfd2828d |  | textbox | Finish Pressure:
text | e32e8ae6-9d41-5177-8082-075fb10332b6 |  | textbox | Duration:
text | 83dfb27b-bf7e-547a-932e-ca171dd29689 |  | textbox | Pressure Drop:
checkpoint-status | 57d6472b-c92f-4604-8f88-b3486fd4f578 |  | checkpoint | Paint protective cap on sprinkler
checkpoint-status | d1b17f77-743f-442a-86c2-c9707e4eeaa0 |  | checkpoint | Sign off by AMF
text | 5e9e4702-e90e-550a-a79d-9e897cf629a8 |  | textbox | Witness Name (If Applicable)
checklist-flat | 5a7bd6fc-12ce-42e9-ba7e-fb9109620d6d |  | checklist | SYS - K Road Station - Fire Alarm Commissioning |  |  |  |  | Yes | SYS - K Road Station - Fire Alarm Commissioning | 8cd158b1-a252-442f-b663-0c8e02d12beb
checkpoint-status | 09c1a075-ff67-4158-aa2d-fe9fdf91889c |  | checkpoint | Correct Signal to PAVA
checkpoint-status | 912b5994-3838-4e4e-b87d-410d32513fb8 |  | checkpoint | Visual Alarm Strobes
checkpoint-status | e15070f7-f9bc-4370-bc57-56649981a158 |  | checkpoint | FACP Notification
checkpoint-status | d9b28937-eb3e-49e8-96b6-44cc9828e4d2 |  | checkpoint | Correct Mimic & LCD indication
checkpoint-status | c554cf7a-2d72-432b-80a9-0f003bec7f66 |  | checkpoint | Electrical System Control
checkpoint-status | ed2a17b6-e320-485e-a8f5-ef317a18dc40 |  | checkpoint | Access Control
checkpoint-status | 5ea22853-254a-4804-9a50-d406dee338ab |  | checkpoint | Escalator Shutdown
checkpoint-status | 959aa4a2-a45b-4a6d-b697-e5d51cb720b9 |  | checkpoint | HVAC System Shutdown
checkpoint-status | bfe31a93-4055-492e-95bd-976e9a853b11 |  | checkpoint | Lift Recall
checkpoint-status | 9c1722f2-2ddd-476a-b340-a9fe8c4cac5d |  | checkpoint | Correct BMS Signal
checkpoint-status | badae093-ad2a-417c-9c7f-aedda09e2c89 |  | checkpoint | National Train Control Signal
checkpoint-status | 03a4fad5-fe1f-4cb2-b159-1ec2952456ec |  | checkpoint | Station Group Control Centre
checkpoint-status | 8cf34e7b-4159-4d70-bc3a-5a7edd8f12a6 |  | checkpoint | Platform information Displays
checkpoint-status | e22cb67b-db89-4616-b216-42f0b85d6d97 |  | checkpoint | Stair Pressurization
checkpoint-status | 9ee8e9f5-c8ec-4a57-a896-09f7dcb42059 |  | checkpoint | Paging Notification
checkpoint-status | bbf33da0-b3ed-458f-b5fc-9bf1c4451197 |  | checkpoint | Staff Investigate Signal
checklist-flat | 902e2a9a-3ce1-4b7f-bef7-a1023b22dc96 |  | checklist | Fire Hydrant Installation |  |  |  |  | Yes | Fire Hydrant Installation | 8d7c75d6-f14c-481f-8bf3-6f120188361a
checkpoint-status | ec670108-58f3-43f0-aec8-1cf2f2403dad |  | checkpoint | Construction drawings approved for use.
checkpoint-status | 18db85f6-d31f-4a65-bf43-7c5816368d3a |  | checkpoint | Black / Galv. / Primed Mild Steel to
boolean | 4928d57b-a50a-50c5-81b7-8db3bf13407f |  | tickbox | NZS/BS 1387:1387
boolean | d42924f2-a8ae-5967-b2d7-3885f313a3f5 |  | tickbox | AS1074 Medium
checkpoint-status | 9e4333f5-9394-4777-b257-f960059b3b60 |  | checkpoint | Main size Risers
checkpoint-status | 0e3e59ed-d2c2-4bcb-9dbb-acb19a2295c5 |  | checkpoint | Hanger Spacing
checkpoint-status | 1a0c6ed8-dcf9-4302-a0bd-7c37e8cc1428 |  | checkpoint | Seismic restraints Hangers
boolean | ab020ebf-7468-5a46-8422-6661d150abe5 |  | tickbox | Valves Locked
checkpoint-status | aec9823e-7047-495b-bdef-5375519fedc8 |  | checkpoint | From FFL to centre (600mm min – 1350mm MAX)
checkpoint-status | 9d1ac232-1a60-4235-bee2-4da91677bb9a |  | checkpoint | Pipework Tested Air & Water
text | ff3f01b5-bcce-4466-ac65-f80bf2340a4e |  | textbox | Start Time:
text | ca3c35a1-fc5c-4068-8c40-e8f9241dcc1e |  | textbox | Start Pressure:
text | 086ff17e-e824-4e50-966a-051542a6dba7 |  | textbox | Finish Time:
text | 70bb21df-4f9c-4193-a29f-af297cf8b378 |  | textbox | Finish Pressure:
text | 37f6dd71-1c0b-4779-9a4e-0fff5a843ed0 |  | textbox | Duration:
text | 77076241-23bf-48fa-80a6-ffc9b47e5a27 |  | textbox | Pressure Drop:
checkpoint-status | a22dbe72-33f7-4065-8023-abb7cd3f36a6 |  | checkpoint | Pipework signage
checkpoint-status | 224d8c05-3cc2-4609-a9be-3477f979676d |  | checkpoint | Hydrant charged
checklist-flat | be2c0b46-cc5d-460d-a325-bf5a2e7a9ac0 |  | checklist | Fire Alarm Commissioning - Timer |  |  |  |  | Yes | Fire Alarm Commissioning - Timer | a2982aee-b02d-47a0-933b-2f885ed06ec0
checkpoint-status | 358de09e-e7d7-4e97-add8-d4a749f6141b |  | checkpoint | 60 second Timer Initiated
checkpoint-status | cfff1b7a-95bb-43c6-86e2-1981b1132f38 |  | checkpoint | ON acknowledge - Timer Extended to 8 minutes
checkpoint-status | 7c52ace5-e0a8-434f-9d51-690dfd08f8f6 |  | checkpoint | Timer not acknowledged - Stage 2 Alarm (after 60 seconds)
checkpoint-status | 3a2cd4dc-ae61-4377-95ce-d3fcc1cfe60f |  | checkpoint | 8 minute Timeout - Escalate to Stage 2
checkpoint-status | 43700a7d-eeea-494f-8313-6e37ac7c406c |  | checkpoint | Second Smoke Detector Activated - Escalate to Stage 2
checklist-flat | bcbe3a91-7ff6-46a3-b1e8-8f4c7777e091 |  | checklist | Fire Alarm Second Fix |  |  |  |  | Yes | Fire Alarm Second Fix | bc74fc83-80fe-4a3e-91bd-d1104316a4b4
checkpoint-status | 310fc472-5501-4fe3-b9c1-8b5c36e2f09f |  | checkpoint | Latest RCP drawings approved for use
checkpoint-status | ba222ac3-7711-4490-9f5e-0ee43e84328b |  | checkpoint | Control & Index Panels Installed
checkpoint-status | 22cba3d5-081a-4035-b874-3d6dff2c23c2 |  | checkpoint | Detectors Installed
checkpoint-status | 98be25e8-289f-409d-b1fc-ee692f349524 |  | checkpoint | Manual Call Points Installed
checkpoint-status | a2cec806-f28d-41d4-9402-07d87f02d636 |  | checkpoint | Strobe Lights installed
checkpoint-status | 6e24b7ab-fbbf-4be2-847b-c34c2b9aac92 |  | checkpoint | Interface Modules Installed
checkpoint-status | 7268c08b-2c16-45f5-aa17-b4a3b5d91f6c |  | checkpoint | VESDA Sampling Points Installed
checkpoint-status | 448198da-9f75-448c-b691-73080037b3e9 |  | checkpoint | Linear Fire Wire EOL installed
checkpoint-status | 83c1cf62-4b3b-4454-bc1f-76c1e2d50402 |  | checkpoint | Sign off by AMF
text | b5534351-0b38-5e1c-aecd-ca717260ca5b |  | textbox | Witness Name (If Applicable)
checklist-flat | 117c58f0-4602-433c-a490-d804e816935f |  | checklist | Gas Flood Mechanical First Fix |  |  |  |  | Yes | Gas Flood Mechanical First Fix | e8a96982-efd2-4cf3-b638-3cad2f848bf8
checkpoint-status | 8e2001ab-4d78-49cd-afad-8e07d7e7aa8f |  | checkpoint | Design Complete & approved
checkpoint-status | 8c1f40e1-1eff-4afd-8590-a0fd81d78ba6 |  | checkpoint | Pipes Checked Internally for swarf
label | 7b664f55-d831-5429-a4f6-423afd482d69 |  | note | All pipes & fittings degreased with solvent, blow through with compressed air to check that no oil or swarf remains
checkpoint-status | ed5e1efc-ddfb-41c6-8c9a-66393c46a2b2 |  | checkpoint | Pipe work installed as per installed as per design
checkpoint-status | 40c2c0f1-3b4a-48d7-b627-c207c05fa690 |  | checkpoint | Brackets Installed as per design
checkpoint-status | fdd561ac-d009-4818-9d48-b3ae00f7b8f9 |  | checkpoint | All fittings tightened & installed with thread tape
checkpoint-status | 90298f74-faa1-494a-912f-6adb4529d28e |  | checkpoint | Pressure Relief Damper/ Fire Damper Installed
checkpoint-status | 296a7040-5dba-4172-85a8-7236d185fd80 |  | checkpoint | Sign off by AMF
text | 03196be3-7962-5986-8b7c-94f3ef8f5f29 |  | textbox | Witness Name (If Applicable)
checklist-flat | 1ad6806a-c049-40aa-acb9-35f38b2efbda |  | checklist | Fire Alarm First Fix |  |  |  |  | Yes | Fire Alarm First Fix | ea1a8572-021f-465f-a78b-43a9dd980e5e
checkpoint-status | 4b3fc78f-4819-4297-b161-6ce5252b4e15 |  | checkpoint | Ceiling cabling/ In place and secured
checkpoint-status | 8be6e0c2-8057-4c95-8b4f-1df8c8f1ea40 |  | checkpoint | Wall cabling/ In place and secure
checkpoint-status | 4d8332e2-dfa9-4c31-9501-b7360b004633 |  | checkpoint | Detector heads cable loops in approved locations
checkpoint-status | 26494eb8-33a0-41e4-8f6c-fec93668aff3 |  | checkpoint | MCP cable in approved locations
checkpoint-status | eefed2a6-5acf-4731-862d-59076a1dffa4 |  | checkpoint | Strobe light cable in correct location
checkpoint-status | 003ff43c-1e7d-451d-97df-993c3bd9f7d8 |  | checkpoint | Interface Module cable in approved locations
checkpoint-status | 280c0a9b-77a6-4925-bb57-7b96d6c2250e |  | checkpoint | VESDA Pipe installed correctly in approved locations
checkpoint-status | b8dcfa87-ef5e-4eb9-825a-b797a277dc79 |  | checkpoint | Linear Fire Wire installed correctly in approved locations
checkpoint-status | 6115cecd-39d9-492c-a01c-73605da72495 |  | checkpoint | Sign off by AMF
text | b63f213d-b6fd-53fb-a87b-5e318198381f |  | textbox | Witness Name (If Applicable)
checklist-flat | 970ba63f-05e9-4d0a-b7d8-91397d226577 |  | checklist | SYS - Fire Sprinkler First Fix |  |  |  |  | Yes | SYS - Fire Sprinkler First Fix | ece6f6a4-2295-4772-9cbe-711657c9d240
checkpoint-status | af1c7f6f-7054-4f9e-a128-45b28694c20c |  | checkpoint | Construction drawings approved for use.
checkpoint-status | bec2864f-8a34-4cf7-a307-573b120b819c |  | checkpoint | Black / Galv. / Primed Mild Steel to:
label | 1a219f5b-240f-56a4-93eb-1a848f87cdbe |  | note | NZS/BS 1387:1387
label | 2ccef73f-7ef9-586c-bfa6-fdb70b595e42 |  | note | AS1074 Medium
checkpoint-status | dece75b7-588e-4524-a93c-7099dcd8e604 |  | checkpoint | Sprinkler heads As Specified
checkpoint-status | 05032848-64fe-41b7-bb4a-76c69477ce4f |  | checkpoint | Sprinkler heads Type
checkpoint-status | 4392760e-fbb3-42a5-84dd-2742660e8dcf |  | checkpoint | In ceiling sprinklers installed
checkpoint-status | f9363a8f-8f27-4d48-8aa8-cae0ddc85f4c |  | checkpoint | Flexible Drops installed
checkpoint-status | 7fb1cac9-3bed-4eea-b8d3-8368af92fbc5 |  | checkpoint | Hanger Spacing
checkpoint-status | cb5a93a6-6c7e-4126-95c3-301ad8432adf |  | checkpoint | Seismic restraint’s Hangers
checkpoint-status | 520760fd-8d0d-49dd-9525-c5b8b7312e93 |  | checkpoint | Pipework Finish as specified
checkpoint-status | 313969ca-cbf2-4f4e-91eb-909cc918bbee |  | checkpoint | Pipework installed as per drawing.
checkpoint-status | bd6f0134-7a2e-4048-b1f5-00a85a2bfbee |  | checkpoint | Seismic Breaks
checkpoint-status | 54e9572d-d668-4b17-8dd6-2d65be539371 |  | checkpoint | Touch up paint
checkpoint-status | cefedcf1-01f9-4eee-855d-007e335647a6 |  | checkpoint | Pipework Tested Air & Water
checkpoint-status | 90e638d5-2ad9-4fa0-9f55-02d572be8ce7 |  | checkpoint | Paint protective cap on sprinkler
checkpoint-status | f22c5e5b-2ae3-4874-bcb9-abafada9ff8f |  | checkpoint | Sign off by AMF
text | 60fbc604-ef21-5b90-95fe-3f795459df28 |  | textbox | Witness Name (If Applicable)
checklist-flat | 87ed9dca-89d3-48fc-8d5f-267c54a9a156 |  | checklist | Fire Sprinkler Second Fix |  |  |  |  | Yes | Fire Sprinkler Second Fix | f427a7bb-42ed-4bd7-a267-e9711c311abf
checkpoint-status | e71a107c-1ced-459a-87de-f0cac236585a |  | checkpoint | Latest RCP drawings approved for use.
checkpoint-status | 399b7feb-6059-4064-9e40-00d122ec40bd |  | checkpoint | All sprinkler positions correct
checkpoint-status | 564b9872-5929-468f-827c-1f71d17872c9 |  | checkpoint | Approved type (ref. sample submission)
checkpoint-status | 48332df3-feb6-4aa1-8f0e-292271cb067b |  | checkpoint | Correct response time.
checkpoint-status | b28c2421-68ff-4fbe-b0f6-75e536a52af5 |  | checkpoint | Check sprinkler frames oriented.
checkpoint-status | 33a8418d-a1c7-486f-906d-759c95f76cb3 |  | checkpoint | Sprinkler finish colour to specification
checkpoint-status | 95c0ee78-e603-460d-b7c3-0d0120d1fbfe |  | checkpoint | Sprinkler Guards
boolean | 52ab59a0-e01f-54d1-a0c1-f4deac442b86 |  | tickbox | Fitted heads below 2m
checkpoint-status | 63253efc-5bae-4069-a940-3758d7f0bd9d |  | checkpoint | Cupboards
boolean | 31c836de-0ea5-573e-93af-2397e362c2a8 |  | tickbox | Gas
boolean | 17840cc3-1587-5ccb-890c-7f7f2091842f |  | tickbox | Electrical
boolean | 1929b65a-92da-5fc1-bf4f-937577b7fdae |  | tickbox | Wardrobes
boolean | d3750157-d732-5bd4-b778-2bb76058cf25 |  | tickbox | Top lift shaft
checkpoint-status | dcc93777-b36a-4d93-88e3-040ed2f665ba |  | checkpoint | Escutcheon Plates
boolean | 8f827094-569c-5f77-a795-77224dfdf6eb |  | tickbox | As specified
boolean | e35958a9-1f54-50f4-951e-7d118499c2d9 |  | tickbox | All escutcheon plates installed
checkpoint-status | e22e4799-232d-48f3-b421-6ece2353d97b |  | checkpoint | Orange caps removed off Sprinklers
checkpoint-status | d78d1309-0a3a-4b73-bed0-17120193dc4c |  | checkpoint | Pipework Tested Air & Water
text | 1a6d5872-453f-56af-8a28-f857467de33b |  | textbox | Start Time:
text | 6bccd6c5-98eb-5392-845e-272f62d32ce1 |  | textbox | Start Pressure:
text | 0b280271-244f-589b-9be7-21b0137f590b |  | textbox | Finish Time:
text | 2859a675-07f4-5231-ac54-02dba09ec58d |  | textbox | Finish Pressure:
text | 6a372372-1356-587c-b464-a465c0f8e260 |  | textbox | Duration:
text | 50ac4f52-9569-5b15-81de-6e25693373df |  | textbox | Pressure Drop:
checkpoint-status | 2fea1305-c757-464a-9ee5-bff78d91023c |  | checkpoint | Ceiling Tiles
checkpoint-status | 7887c8c5-0ef2-440e-b62c-24ab2ff7b3b2 |  | checkpoint | Sprinkler – Installed and Un-Damaged
checkpoint-status | 421d09b5-76af-44a3-ac61-e188f5bcdef9 |  | checkpoint | Sign off by AMF
text | a9827852-999c-5fc5-b658-55c6c2ae5b3e |  | textbox | Witness Name (If Applicable)
checklist-flat | d436e00d-b0ae-438e-9a9c-e4d0b75ea04b |  | checklist | Fire Alarm Second Fix - 203p |  |  |  |  | Yes | Fire Alarm Second Fix - 203p | fb527b52-a92b-4a4f-a7f9-4fbaf6b82ce8
checkpoint-status | e806fdd9-6c82-4bb3-b3fd-3155a37e1437 |  | checkpoint | Latest RCP drawings approved for use
checkpoint-status | abcd049f-2959-4a88-8331-f31c8b1a0d81 |  | checkpoint | Control & Index Panels Installed
checkpoint-status | 408324db-3ce1-4318-b8ce-9c355dbf46f3 |  | checkpoint | Detectors Installed
checkpoint-status | 281ec092-15ae-49ec-b675-21a72deaff2b |  | checkpoint | Manual Call Points Installed
checkpoint-status | f8a5defb-f2bd-429d-b007-2597b32e232b |  | checkpoint | Speaker Installed
checkpoint-status | 9d893bf0-7371-4d54-9b6d-f6ce9ce0f424 |  | checkpoint | Interface Modules Installed
checkpoint-status | 1141db8c-7eea-495d-921a-81b1b631a8fe |  | checkpoint | Sign off by AMF
text | 6beaa3e4-f9d7-5d1d-881b-65daa62d9374 |  | textbox | Witness Name (If Applicable)
checklist-flat | 361b42ff-4ddb-420e-88ec-a81231427fa3 |  | checklist | Fire Alarm Commissioning |  |  |  |  | Yes | Fire Alarm Commissioning | feb477b0-a721-42d8-8896-90fd9510d96b
checkpoint-status | 22ab4299-f084-40aa-9b79-a8f307475a1e |  | checkpoint | Correct Signal to PAVA
checkpoint-status | badccd61-3992-4c89-aa3f-7d43b33536db |  | checkpoint | Timer Started
checkpoint-status | faac8987-fa40-4b0a-81a0-cf329ec7d21d |  | checkpoint | Visual Alarm Strobes
checkpoint-status | 5acab9df-4d98-4d6b-8895-86ad860babf2 |  | checkpoint | FACP Notification
checkpoint-status | c17000ab-9355-4ad1-b5b9-29d05a5f3964 |  | checkpoint | Correct Mimic & LCD indication
checkpoint-status | d87436bf-344a-46d9-8a74-914a13b48d02 |  | checkpoint | Electrical System Control
checkpoint-status | 20bf7aa1-1ec4-4648-9b9f-914814ee5d5d |  | checkpoint | Access Control
checkpoint-status | 3ac0cbb0-d055-4508-b38c-a1af2e9c2e81 |  | checkpoint | Escalator Shutdown
checkpoint-status | 8c7b0d30-0c82-40c1-aeb9-cc7ebd5ca515 |  | checkpoint | HVAC System Shutdown
checkpoint-status | 354db48b-f741-4371-8f5e-220895189c4f |  | checkpoint | Lift Recall
checkpoint-status | a2d834a4-d48d-42fc-b8b0-1cdf6d459f6e |  | checkpoint | Correct BMS Signal
checkpoint-status | eee194e6-d91a-4b45-9161-3edcb629e3a8 |  | checkpoint | National Train Control Signal
checkpoint-status | 3444eca5-8e8e-488b-bf46-654f8838003e |  | checkpoint | Station Group Control Centre
checkpoint-status | 61500cb7-18a1-4082-89c4-cd6a006a7122 |  | checkpoint | Platform information Displays
checkpoint-status | 9f54690c-7a74-43b0-93e0-5ea222e00f1a |  | checkpoint | Stair Pressurization
checkpoint-status | 8d73d710-7948-4d65-879b-1001a05242db |  | checkpoint | Paging Notification
checkpoint-status | 79f600e1-0651-4416-85f2-024a09cc8841 |  | checkpoint | Staff Investigate Signal