## Resources
Rich Type | Id | Warnings | type | name | values | prefix | postfix | Usage Count | User Addable | Template Name | Template Id
checklist-flat |  |  | checklist | Inspection Test Plan_MSB 4-4 |  |  |  |  | Yes | Inspection Test Plan_MSB 4-4 | 002b0653-c2f3-4947-a154-d41b5ed2d1be
checkpoint-status |  |  | checkpoint | Measurements and location of array marked in accordance with drawings
checkpoint-status |  |  | checkpoint | Panel clamps are installed properly and straight
checkpoint-status |  |  | checkpoint | Num. of rails match prescribed structural mounting zones
checkpoint-status |  |  | checkpoint | Rail overhang from last roof fixing does not exceed 500mm
checkpoint-status |  |  | checkpoint | Every row is earthed
checkpoint-status |  |  | checkpoint | Solar modules are installed square
checkpoint-status |  |  | checkpoint | Modules are max. 350mm from last fixing
checkpoint-status |  |  | checkpoint | Solar modules are correctly connected according the string configuration
checkpoint-status |  |  | checkpoint | Cables are installed neatly and without slack
checkpoint-status |  |  | checkpoint | Channels or cable trays used on the roof are earthed
checkpoint-status |  |  | checkpoint | Check MC4 connectors: termination and brand of connectors
checkpoint-status |  |  | checkpoint | Suitable cable management is installed on the roof
checkpoint-status |  |  | checkpoint | Penetration(s) done are properly sealed with silicone or fire-resistant foam (if required)
checkpoint-status |  |  | checkpoint | Inverters are mounted and installed correctly
checkpoint-status |  |  | checkpoint | Test equipotential bonding of frames and exposed conductive parts
checkpoint-status |  |  | checkpoint | Test string voltage, insulation resistance, polarity
checkpoint-status |  |  | checkpoint | All DC Cable is Mechanically protected
checkpoint-status |  |  | checkpoint | Protection board is installed and terminated correctly
checkpoint-status |  |  | checkpoint | Data cables correctly connected and terminated
checkpoint-status |  |  | checkpoint | Test inverter insulation resistance, continuity
checkpoint-status |  |  | checkpoint | Inverters connected to the data switch via cat 6.
checkpoint-status |  |  | checkpoint | Inverters are configured via app and online
checkpoint-status |  |  | checkpoint | All the components are labelled clearly
checklist-flat |  |  | checklist | Foot Spacing Check Form |  |  |  |  | Yes | Foot Spacing Check Form | 1ff73bc3-76f2-40f1-bc42-d4e3e00876e9
checkpoint-status |  |  | checkpoint | Maximum Allowed Spacing (mm) 1200 (on purlin), Spacing less than max
checklist-flat |  |  | checklist | Inspection Test Plan_MSB 5-2 |  |  |  |  | Yes | Inspection Test Plan_MSB 5-2 | 524cebe9-08dd-4699-8a90-a6190c5a6cf2
checkpoint-status |  |  | checkpoint | Measurements and location of array marked in accordance with drawings
checkpoint-status |  |  | checkpoint | Panel clamps are installed properly and straight
checkpoint-status |  |  | checkpoint | Num. of rails match prescribed structural mounting zones
checkpoint-status |  |  | checkpoint | Rail overhang from last roof fixing does not exceed 500mm
checkpoint-status |  |  | checkpoint | Every row is earthed
checkpoint-status |  |  | checkpoint | Solar modules are installed square
checkpoint-status |  |  | checkpoint | Modules are max. 350mm from last fixing
checkpoint-status |  |  | checkpoint | Solar modules are correctly connected according the string configuration
checkpoint-status |  |  | checkpoint | Cables are installed neatly and without slack
checkpoint-status |  |  | checkpoint | Channels or cable trays used on the roof are earthed
checkpoint-status |  |  | checkpoint | Check MC4 connectors: termination and brand of connectors
checkpoint-status |  |  | checkpoint | Suitable cable management is installed on the roof
checkpoint-status |  |  | checkpoint | Penetration(s) done are properly sealed with silicone or fire-resistant foam (if required)
checkpoint-status |  |  | checkpoint | Inverters are mounted and installed correctly
checkpoint-status |  |  | checkpoint | Test equipotential bonding of frames and exposed conductive parts
checkpoint-status |  |  | checkpoint | Test string voltage, insulation resistance, polarity
checkpoint-status |  |  | checkpoint | All DC Cable is Mechanically protected
checkpoint-status |  |  | checkpoint | Protection board is installed and terminated correctly
checkpoint-status |  |  | checkpoint | Data cables correctly connected and terminated
checkpoint-status |  |  | checkpoint | Test inverter insulation resistance, continuity
checkpoint-status |  |  | checkpoint | Inverters connected to the data switch via cat 6.
checkpoint-status |  |  | checkpoint | Inverters are configured via app and online
checkpoint-status |  |  | checkpoint | All the components are labelled clearly
checklist-flat |  |  | checklist | Rail Earthing Check Form |  |  |  |  | Yes | Rail Earthing Check Form | 6e1cfdc2-6766-4be8-b051-aaef14376f80
checkpoint-status |  |  | checkpoint | (Every 2nd rail) Correct each lug used
checkpoint-status |  |  | checkpoint | Earth lug correctly installed
checklist-flat |  |  | checklist | Mounting Zone Checkform |  |  |  |  | Yes | Mounting Zone Checkform | 7d919383-c202-452d-bb87-93efb81bfa30
checkpoint-status |  |  | checkpoint | Minimum number of rails installed
select | f2801ffd-ed4a-5961-9533-a7fed9a0b43b |  | dropdown | Rails | 2,4
checklist-flat |  |  | checklist | Foot Torque Form |  |  |  |  | Yes | Foot Torque Form | c0e6a1d8-5aba-4c41-b265-bde2be936f76
checkpoint-status |  |  | checkpoint | Recommended torque 12-14 Nm, recommended torque used
checklist-flat |  |  | checklist | Rail Overhang Check Form |  |  |  |  | Yes | Rail Overhang Check Form | ce25cf92-8825-4695-b4be-0b9288f512e6
checkpoint-status |  |  | checkpoint | Expected rail overhang from last foot <300m, expected value met
checklist-flat |  |  | checklist | Rail Spacing Check Form |  |  |  |  | Yes | Rail Spacing Check Form | f2ec2d88-a13c-4658-8842-c9050fb934a0
checkpoint-status |  |  | checkpoint | Expected value between front & back rail 1008 – 1428mm, expected value met
checklist-flat |  |  | checklist | Inspection Test Plan_MSB 4-3 |  |  |  |  | Yes | Inspection Test Plan_MSB 4-3 | f39f7248-5dfb-4dba-a417-525679dd8d5e
checkpoint-status |  |  | checkpoint | Measurements and location of array marked in accordance with drawings
checkpoint-status |  |  | checkpoint | Panel clamps are installed properly and straight
checkpoint-status |  |  | checkpoint | Num. of rails match prescribed structural mounting zones
checkpoint-status |  |  | checkpoint | Rail overhang from last roof fixing does not exceed 500mm
checkpoint-status |  |  | checkpoint | Every row is earthed
checkpoint-status |  |  | checkpoint | Solar modules are installed square
checkpoint-status |  |  | checkpoint | Modules are max. 350mm from last fixing
checkpoint-status |  |  | checkpoint | Solar modules are correctly connected according the string configuration
checkpoint-status |  |  | checkpoint | Cables are installed neatly and without slack
checkpoint-status |  |  | checkpoint | Channels or cable trays used on the roof are earthed
checkpoint-status |  |  | checkpoint | Check MC4 connectors: termination and brand of connectors
checkpoint-status |  |  | checkpoint | Suitable cable management is installed on the roof
checkpoint-status |  |  | checkpoint | Penetration(s) done are properly sealed with silicone or fire-resistant foam (if required)
checkpoint-status |  |  | checkpoint | Inverters are mounted and installed correctly
checkpoint-status |  |  | checkpoint | Test equipotential bonding of frames and exposed conductive parts
checkpoint-status |  |  | checkpoint | Test string voltage, insulation resistance, polarity
checkpoint-status |  |  | checkpoint | All DC Cable is Mechanically protected
checkpoint-status |  |  | checkpoint | Protection board is installed and terminated correctly
checkpoint-status |  |  | checkpoint | Data cables correctly connected and terminated
checkpoint-status |  |  | checkpoint | Test inverter insulation resistance, continuity
checkpoint-status |  |  | checkpoint | Inverters connected to the data switch via cat 6.
checkpoint-status |  |  | checkpoint | Inverters are configured via app and online
checkpoint-status |  |  | checkpoint | All the components are labelled clearly