## Sheet1
type | name | values
checklist | Solar system
section | System Check | Complete
checkpoint | Air test solar collector loop to within 0.5bar of pressure relief valve for 2 hours
checkpoint | Flush piping with clean water before filling
checkpoint | Ensure system holds fluid pressure with no leaks
checkpoint | Operate pump manually and check flow
checkpoint | Check that all collector banks have balance flow
checkpoint | Exposed piping is insulated, jacketed and labeled
checkpoint | Interior piping is insulated and labeled
checkpoint | Temperature sensors are installed in proper location and providing accurate readings
checkpoint | Temperature gauges are installed on the solar thermal flow and return lines
checkpoint | Visual flow gauge is installed on the solar thermal loop
checkpoint | Pressure gauge is installed on solar thermal loop (for closed loop systems)
checkpoint | Motorised ball valve/s correctly orientated for default flow path
section | Evacuated Tube Installation | Complete
checkpoint | All heat pipe bulbs coated in heat transfer paste
checkpoint | No tubes have vacuum loss
checkpoint | All evacuated tubes are installed
checkpoint | All tubes have rubber caps and clips are neatly aligned
section | Operation & Performance Check | Complete
checkpoint | Collectors generate heat when pump is not running
checkpoint | Controller operates properly switching pumps and relays on/off as expected
section | Cleaning | Complete
checkpoint | Solar collector manifold and evacuated tubes have been cleaned
checkpoint | All rubbish has been removed from the roof and equipment rooms
section | Handover to Owner | Complete
checkpoint | Provided operation and maintenance documentation set
checkpoint | Completed explanation of the basic system operation
checkpoint | Completed training on how to safely turn off the system
checkpoint | Complete training on which valves must not be tampered with
checkpoint | Completed training on the basic operation of the controller to read system settings
checkpoint | Completed training on the maintenance tasks, and frequency at which to be conducted