## Resources
type | name | values | Template Name | Dwaynes comments
checklist | Distribution Board Post-livening Check Sheet - Single Phase DB |  | Distribution Board Post-livening Check Sheet - Single Phase DB | Remove "Single phase DB"
textbox | Switchboard name |  |  | Add
textbox | Location |  |  | Add
checkpoint | Confirm Distribution Board Pre-livening Check sheet is complete |  |  | Change
checkpoint | Isolate all subcircuits and switches |  |  | Add
checkpoint | Turn on supply and confirm the correct voltage is present |  |  | Change
textbox | R-N |  |  | Change
textbox | W-N |  |  | Change
textbox | B-N |  |  | Change
textbox | R-E |  |  | Change
textbox | W-E |  |  | Change
textbox | B-E |  |  | Change
textbox | N-E |  |  | Change
textbox | R-W |  |  | Change
textbox | R-B |  |  | Change
textbox | W-B |  |  | Change
checkpoint | Confirm the correct polarity |  |  | Good
checkpoint | R, W, B, N |  |  | Good
checkpoint | N-E |  |  | Good
checkpoint | Record impedance |  |  | Add
textbox | R-E |  |  | Add
textbox | W-E |  |  | Add
textbox | B-E |  |  | Add
checkpoint | Phase rotation |  |  | Add
checkpoint | Confirm the correct control voltage is present |  |  | Delete
checkpoint | Confirm all meters/monitoring devices are setup correctly and operational |  |  | Delete
checkpoint | Confirm control contractors and devices are operation correctly |  |  | Delete
checkpoint | Confirm all switching devices (ACB's, MCCB's, MCB's etc) are switching correctly |  |  | Delete
checkpoint | Confirm all auxilaries are swithcing correctly |  |  | Delete
checkpoint | Confirm all adjustable circuit breaker settings are recorded and correct |  |  | Good - can we have an option to note settings?
textbox | Settings |  |  | Add
checkpoint | Confirm switchboard is ready to be put into service |  |  | Good
checkpoint | Special Conditions |  |  | Good
textbox | Conditions |  |  | Good
checkpoint | Tested |  |  | Good
textbox | Tested By |  |  | Good
checkpoint | Confirm Ready To Be Livened |  |  | Good
signoff | Request Confirmation |  |  | Good
checklist | Cable Installation Check Sheet |  | Cable Installation Check Sheet
checkpoint | Test Conditions
button | Ambient air condition | Dry ,Humid
note | List any other special conditions or circumstances that should be noted as at the time of test.
checkpoint | Cable Details
textbox | Cable Number
textbox | Cable runs from
textbox | Cable runs to
textbox | Conductor Size
textbox | Cores (eg 4c, 4x1c)
textbox | Conductor Material
textbox | Cable type (eg PVC, XLPE)
textbox | Protection Rating (In)
textbox | IR Setting x In
checklist-flat | Test Results
checklist-flat | Tested
checklist | Emergency Lighting Check Sheet |  | Emergency Lighting Check Sheet
checkpoint | Pre Checks
note | All testing initiated by Famco central processor
note | Check that all fittings are labelled and communicating with central system
note | Every 12 months clean all surfaces and note that fittings cleaned in comments area.
checkpoint | Lighting Information
textbox | Fitting No.
textbox | Circuit No.
textbox | Fitting Type
textbox | Location
checklist-flat | Checks
checkpoint | Tested and Witnessed
textbox | Tested By
textbox | Witnessed by
checklist | Lightning Protection earth Check Sheet |  | Lightning Protection earth Check Sheet
checkpoint | Earth Location |  |  | Add
textbox | Give a description of the main earth (peg or pegs, buried conductor, building reinforcing etc) and the point at which the tests will be carried out |  |  | Good
checkpoint | Main Earth Lead |  |  | Good
textbox | Record the size and type of conductor installed as the main earth lead from the main earth electrode to the MSB earth bar and describe its route |  |  | Good
checkpoint | Test Results |  |  | Good
note | Using an Earth Test Measuring Device record the resistance of the main earth |  |  | Good
textbox | Type of tester |  |  | Good
textbox | Serial No. |  |  | Good
textbox | Earth resistance |  |  | Good
checkpoint | Confirm that main earth has 'Do Not Disconnect' labels fitted |  |  | Good
checkpoint | Dynasphere |  |  | Add
textbox | Give a discription of the location, mounting and cable route of the dynasphere and conductor |  |  | Add
checkpoint | All terminatons are made and secure |  |  | Add
checkpoint | Dynasphere pole is seismically restrained and secure |  |  | Add
checkpoint | Special Conditions |  |  | Add
textbox | Conditions |  |  | Add
checkpoint | Tested By |  |  | Add
textbox | Tested by |  |  | Add
checklist | Post Livening Cable Check Sheet - Single Phase |  | Post Livening Cable Check Sheet - Single Phase
checkpoint | Cable Details
textbox | Cores (eg4c, 4x1 C)
textbox | Earth conductor size
textbox | Breaker size (A)
textbox | Conductor size
textbox | Conductor material
textbox | Cable runs from
textbox | Conductor insulation
textbox | Cable runs to
checkpoint | Confirm Pre-Livening cable test sheet is completed
checkpoint | Live Test
textbox | Phase to Earth
textbox | Phase to Neutral
textbox | Neutral to Earth
checkpoint | Confirm installed circuit breaker is correct size and rating
checkpoint | Special Conditions
textbox | Conditions
checkpoint | Tested By
checkpoint | Recorded
checkpoint | Tested & Livened
checkpoint | Recorded
textbox | Tested by
textbox | Livened By
checklist | Pre - Livening Cable Installation Check Sheet - Single Phase |  | Pre - Livening Cable Installation Check Sheet - Single Phase
checkpoint | Cable Details |  |  | Use below
textbox | Cores (eg4c, 4x1 C)
textbox | Earth conductor size
textbox | Breaker size (A)
textbox | Conductor size
textbox | Conductor material
textbox | Cable runs from
textbox | Conductor insulation
textbox | Cable runs to
checkpoint | Prior to any testing ensure cable terminations are isolated and safe.
textbox | Phase to Earth
textbox | Phase to Neutral
note | Using a 1000 volt insulation tester test and record the resistance between
textbox | Neutral to Earth
checkpoint | Confirm Cable Continuity Phase ID & Polarity
textbox | Neutral
textbox | Earth
textbox | Phase
checkpoint | Special Conditions
textbox | Conditions
checkpoint | Tested By
textbox | Tested by
checkpoint | Confirm ready to be livened
checklist | Pre - Livening Cable Installation Check Sheet - Three Phase |  | Pre - Livening Cable Installation Check Sheet - Three Phase
textbox | Cable name |  |  | add
checkpoint | Cable Details |  |  | Good
textbox | Cable runs from |  |  | Good
textbox | Cable runs to |  |  | Good
textbox | Conductor material |  |  | Good
textbox | Cores (eg4c, 4x1 C) |  |  | Good
textbox | Conductor size |  |  | Good
textbox | Earth conductor size |  |  | Good
textbox | Conductor insulation |  |  | Good
textbox | Breaker size (A) |  |  | Good
checkpoint | Prior to any testing ensure cable terminations are isolated and safe. |  |  | Good
note | Using a 500VDC volt insulation tester test and record the resistance between |  |  | Good
textbox | Red to Earth |  |  | Good
textbox | White to Earth |  |  | Good
textbox | Blue to Earth |  |  | Good
textbox | Neutral to Earth |  |  | Good
checkpoint | If cable is disconnected test between conductors of cable |  |  | Good
textbox | Red to White |  |  | Good
textbox | Red to Blue |  |  | Good
textbox | White to Blue |  |  | Good
textbox | Red to Neutral |  |  | Good
textbox | White to Neutral |  |  | Good
textbox | Blue to Neutral |  |  | Good
checkpoint | Confirm Cable Continuity Phase ID & Polarity |  |  | Good
textbox | Red Phase |  |  | Good
textbox | White Phase |  |  | Good
textbox | Blue Phase |  |  | Good
textbox | Neutral |  |  | Good
textbox | Earth |  |  | Good
checkpoint | Special Conditions |  |  | Good
textbox | Conditions |  |  | Good
checkpoint | Tested By |  |  | Good
textbox | Tested by |  |  | Good
checkpoint | Confirm ready to be livened |  |  | Good
checklist | Main Switchboard Post-livening Check Sheet - Single Incomer |  | Main Switchboard Post-livening Check Sheet - Single Incomer
checkpoint | Confirm pre livening check is complete
checkpoint | Confirm the correct voltage is present at incomer
textbox | R-W
textbox | B-N
textbox | R-B
textbox | R-E
textbox | W-B
textbox | W-E
textbox | R-N
textbox | B-E
textbox | W-N
textbox | N-E
checkpoint | Confirm the correct polarity and phase rotation at Incomer
textbox | R
textbox | W
textbox | B
textbox | N
checkpoint | Record impedance
textbox | R-E
textbox | W-E
textbox | B-E
checkpoint | Confirm the correct control voltage is present
checkpoint | Confirm all meters/monitoring devices are setup correctly and operational
checkpoint | Confirm the phase failure relay is setup correctly and operational
checkpoint | Confirm all switching devices (ACB's, MCCB's, MCB's etc) are switching correctly
checkpoint | Confirm all auxilaries are swithcing correctly
checkpoint | Confirm all adjustable circuit breaker settings are recorded and correct
checkpoint | Confirm ATS units are operational and are switching correctly
checkpoint | Confirm switchboard is ready to be put into service
checkpoint | Special Conditions
textbox | Conditions
checkpoint | Tested
textbox | Tested By
checkpoint | Confirm Ready To Be Livened
checklist | Post Livening Cable Check Sheet - Three Phase |  | Post Livening Cable Check Sheet - Three Phase
checkpoint | Cable Details
note | Trip Unit Settings
textbox | Cores (eg4c, 4x1 C)
textbox | Earth conductor size
textbox | Trip Unit Setting (A)
textbox | Breaker size (A)
textbox | Conductor size
textbox | lr
textbox | Conductor material
textbox | Cable runs from
textbox | Conductor insulation
textbox | lsd
textbox | Cable runs to
textbox | lo
checkpoint | Confirm Pre-Livening cable test sheet is completed
checkpoint | Live Test
textbox | Blue to Neutral
textbox | White to Neutral
textbox | White to Earth
textbox | White to Blue
textbox | Red to Neutral
textbox | Red to White
textbox | Neutral to Earth
textbox | Red to Blue
textbox | Blue to Earth
textbox | Red to Earth
checkpoint | Confirm installed circuit breaker is correct size and rating
checkpoint | Confirm correct trip unit is fitted and adjusted to the correct settings
checkpoint | Confirm Phase Rotation is correct
checkpoint | Special Conditions
textbox | Conditions
checkpoint | Tested & Livened
textbox | Tested by
textbox | Livened By
checklist | Main Switchboard Post-livening Check Sheet - Dual Incomer |  | Main Switchboard Post-livening Check Sheet - Dual Incomer
checkpoint | Confirm pre livening check is complete
checkpoint | Confirm the correct voltage is present at incomer 1
textbox | R-W
textbox | B-N
textbox | R-B
textbox | R-E
textbox | W-B
textbox | W-E
textbox | R-N
textbox | B-E
textbox | W-N
textbox | N-E
checkpoint | Confirm the correct voltage is present at incomer 2
textbox | R-W
textbox | B-N
textbox | R-B
textbox | R-E
textbox | W-B
textbox | W-E
textbox | R-N
textbox | B-E
textbox | W-N
textbox | N-E
checkpoint | Confirm the correct polarity and phase rotation at Incomer 1
textbox | R
textbox | W
textbox | B
textbox | N
checkpoint | Confirm the correct polarity and phase rotation at Incomer 2
textbox | R
textbox | W
textbox | B
textbox | N
checkpoint | Confirm the correct control voltage is present
checkpoint | Confirm all meters/monitoring devices are setup correctly and operational
checkpoint | Confirm the phase failure relay is setup correctly and operational
checkpoint | Confirm all switching devices (ACB's, MCCB's, MCB's etc) are switching correctly
checkpoint | Confirm all auxilaries are swithcing correctly
checkpoint | Confirm all adjustable circuit breaker settings are recorded and correct
checkpoint | Confirm ATS units are operational and are switching correctly
checkpoint | Confirm switchboard is ready to be put into service
checkpoint | Special Conditions
textbox | Conditions
checkpoint | Tested
textbox | Tested By
checkpoint | Confirm Ready To Be Livened
checklist | Second Fix Check Sheet |  | Second Fix Check Sheet
section | Second Fix Checks
checkpoint | Light fittings, correct fitting installed as per luminaire schedule , fitting seismically restrained as per design.
checkpoint | All power points installed and cover plates installed.
checkpoint | Emergency fittings, correct fitting installed as per luminaire schedule and all fittings individually identified.
checkpoint | All PIR sensors in the core installed and operating correctly.
checkpoint | Confirm as-builts
checkpoint | Checked and completed
checklist | Declaration of Conformity (DoC) |  | Declaration of Conformity (DoC)
checkpoint | Information
textbox | DoC Identification Number
note | Issuer(Designer) details
textbox | Name
textbox | Address
textbox | Telephone
textbox | Email Address
textbox | Fax
checkpoint | Location of the premises where installation work is to be carried out:-
textbox
checkpoint | Description of the installation or part of installation, to which this DoC applies
textbox
checkpoint | The design listed above, fully complies with:
note | AS/NZS 3000:2007, including Amendment 1 “Electrical installations” (known as the Australian/New Zealand Wiring Rules) Part 2
radio | Supply System | 230 V 50 Hz single phase MEN,400 V 50 Hz 2 &amp; 3 phase MEN
checkpoint | Declaration
note | I hereby declare that the above Installation complies with the design detailed above.
textbox | Signiture/Passed By
checklist | Main Earth Check Sheet |  | Main Earth Check Sheet
checkpoint | Stake or Array # |  |  | Good
textbox | # |  |  | Good
checkpoint | Test Conditions |  |  | Good
button | Ambient air condition | Dry ,Humid |  | Good
button | Ground condition | Dry ,Wet |  | Good
checkpoint | List any other special conditions or circumstances that should be noted as at the time of test. |  |  | Good
textbox |  |  |  | Good
checkpoint | Earth Location |  |  | Good
textbox | Give a description of the main earth (peg or pegs, buried conductor, building reinforcing etc) and the point at which the tests will be carried out. |  |  | Good
checkpoint | Main Earth Lead |  |  | Good
textbox | Record the size and type of conductor installed as the main earth lead from the main earth electrode to the MSB earth bar and describe its route. |  |  | Good
checkpoint | Test Results |  |  | Good
note | Using an Earth Test Measuring Device record the resistance of the main earth. |  |  | Good
textbox | Type of tester |  |  | Good
textbox | Serial No. |  |  | Good
textbox | Earth resistance |  |  | Good
checkpoint | Confirm that main earth has 'Do Not Disconnect' labels fitted |  |  | Good
checklist | Main earth Check Sheet - Sofitel |  | Main earth Check Sheet - Sofitel
checkpoint | Test Conditions
button | Ambient Air Conditions | dry,humid
button | Ground Conditions | Dry,Wet
textbox | List any other special conditions or circumstances that should be noted as at the time of test.
checkpoint | Earth Location
textbox | Give a description of the main earth (peg or pegs, buried conductor, building reinforcing etc) and the point at which the tests will be carried out.
checkpoint | Main Earth Lead
textbox | Record the size and type of conductor installed as the main earth lead from the main earth electrode to the MSB earth bar and describe its route.
checklist-flat | Test Results
checkpoint | Tested and Witnessed
textbox | Tested By
textbox | Witnessed By
checklist | Mains cable Installation Check Sheet |  | Mains cable Installation Check Sheet
checkpoint | Test Conditions
button | Ambient air condition | Dry ,Humid
note | List any other special conditions or circumstances that should be noted as at the time of test.
checkpoint | Cable Details
textbox
textbox | Cable runs from
textbox | Cable runs to
textbox | Conductor Material
textbox | Cores (eg 4c, 4x1c)
textbox | Conductor Size
textbox | Breaker Size (A)
textbox | Long Delay Current(Ir)
textbox | Long Delay Time(tr)
textbox | Current Short delay(lsd)
textbox | Time Short Delay(tsd)
textbox | Inst. Current (In)
textbox | Protection Rating
checklist-flat | Test Results
checklist-flat | Tested
checklist | Subcircuit test results |  |  | Able to create multiple test sheets under DB name
textbox | Circuit Name
textbox | Current rating
checkbox | Single phase/Three phase
RCD | checkbox
textbox | RCD mA rating
checkpoint | Pre-live tests
checkpoint | Check all field wiring and devices are safe and installed
textbox | Continity between Earth and Phase
textbox | Insulation resistance between P/E
textbox | Insulation resistance between N/E
checkpoint | Terminate phase cables and neutral into switchgear/neutral bar
checkpoint | Tested & Passed
textbox | Tested By
checkpoint | Post-live tests
checkpoint | Earth Loop Impedance - See selection below for Impedance Values for type C MCB's AS/NZS3000:2007 Table 8.1
textbox | Max Allowed
textbox | P/E
dropdown | Impedance Values for type C MCB's AS/NZS3000:2007 Table 8.1 (MCB rating (amps) - Max Impedance (ohms)) | 0 - 5.11,10 - 3.07,16 - 1.92,20 - 1.53,25 - 1.23,32 - 0.96,40 - 0.77,50 - 0.61,63 - 0.49
checkpoint | If RCD protected complete below
checkpoint | RCD Tripping Time Test (record trip times and verify operation) (max times are shown in brackets for 30mA devices).
checkpoint | RCD test button functioning correctly
textbox | 1/2 x Test 0° (no trip)
textbox | 1 x Test @ 0° (<300ms)
textbox | 1 x Test @ 180° (<300ms)
textbox | 5 x Test @ 0° (<300ms)
textbox | 5 x Test @ 180° (<40ms)
checkpoint | Check phase rotation if three phase cicuit
checkpoint | 1,2,3
checkpoint | Tested & Passed
textbox | Tested By
checklist | Cct No. |  | ELI
checkpoint | MCB Rating
textbox
checkpoint | Insulation Resistance
textbox | P/P
textbox | P/E
textbox | P/N
checkpoint | Earth Loop Impedance - See selection below for Impedance Values for type C MCB's AS/NZS3000:2007 Table 8.1
textbox | Max Allowed
textbox | P/E
dropdown | Impedance Values for type C MCB's AS/NZS3000:2007 Table 8.1 (MCB rating (amps) - Max Impedance (ohms)) | 0 - 5.11,10 - 3.07,16 - 1.92,20 - 1.53,25 - 1.23,32 - 0.96,40 - 0.77,50 - 0.61,63 - 0.49
checkpoint | Tested & Passed
textbox | Tested By
checklist | Main Switchboard Pre-livening Check Sheet |  | Main Switchboard Pre-livening Check Sheet | T&C
textbox | Switchboard name |  |  | Add
checkpoint | Confirm MSB room / position meets regulations |  |  | Good
checkpoint | Confirm MSB is securely fastened |  |  | Good
checkpoint | Confirm Supplier has completed all site testing including shipping breaks |  |  | Good
checkpoint | Confirm there is a labelled removable link between the earth & neutral bars |  |  | Good
checkpoint | Check that the MSB has an identification label matching the single line diagram |  |  | Good
checkpoint | Confirm main earth is labelled |  |  | Good
checkpoint | Check that there is an earth bond to the case of the switchboard and doors |  |  | Good
checkpoint | Check that metal work is undamaged and free of corrosion |  |  | Good
checkpoint | Check that MCB/isolator ratings match the switchboard schedules / SLD particularly if the device has an adjustable setting. |  |  | Good
checkpoint | Check that all circuit terminations have phase identification |  |  | Good
checkpoint | Check all outgoing submain breakers have been tagged off prior to livening |  |  | Good
checkpoint | Confirm all connections are tight including circuit breakers to chassis |  |  | Good
button | Mains | Complete,N/A |  | Good
button | Sub Main CBs | Complete,N/A |  | Good
button | Main Earth | Complete,N/A |  | Good
button | Sub Main Earths | Complete,N/A |  | Good
button | Main Neutral | Complete,N/A |  | Good
button | Sub Main Neutrals | Complete,N/A |  | Good
checkpoint | Insulation resistance between bus and earth |  |  | Good
checkpoint | Once inspection is complete confirm MSB is ready is to be livened |  |  | Good
checkpoint | Confirm supply authority metering is installed | Complete,N/A |  | Good
checkpoint | Special Conditions |  |  | Good
textbox | Conditions |  |  | Good
checkpoint | Tested |  |  | Good
textbox | Tested By |  |  | Good
checkpoint | Confirm Ready To Be Livened |  |  | Good
checklist | PIR Test Sheet - Sofitel |  | PIR Test Sheet
checkpoint | PIR Information
textbox | PIR Model
textbox | Location
checklist-flat | Checks
checkpoint | To test Sensors
button | Ensure Time dealy is set for TEST MODE (Dip switchs 5.6&7 off) | Yes,no,n/a
button | Ensure Ultrasonic trim pot is set to 90% clock wise | yes,no,n/a
note | Remain still, The LEDs should not flash,Lights should turn off after 5 seconds.
note | Move around the coverage area, adjust ultra sonic sensitivity as necessary
checklist-flat | Once test complete-Set sensor Dip switches
checkpoint | Tested and Winessed
textbox | Tested By
textbox | Witnessed By
checklist | First Fix Check Sheet |  | First Fix Check Sheet | 1. QA by room name
checkpoint | Sub-circuit cables, supported. |  |  | Good
checkpoint | Catenary Wire, supported above ceiling |  |  | Good
checkpoint | Cable tray / trunking, earth bonded, no sharp edges |  |  | Good
checkpoint | Flush Boxes, fire pads fitted where required. |  |  | Good
checkpoint | Flush Boxes installed |  |  | Good
checkpoint | Acoustic sealing if required |  |  | Good
checkpoint | Flush Boxes Position, check electrical and Arch drawings for plan and elevation locations |  |  | Good
checkpoint | Circuit IDs, check cable marking vs drawings & DB schedule |  |  | Good
checkpoint | Penetrations bushed through metal studs |  |  | Good
checkpoint | Penetrations sealed through fire walls |  |  | Good
checkpoint | Earth bonding to sinks, benches, cable tray and trunking etc. |  |  | Good
checkpoint | PIR Control cabling installed |  |  | Good
checkpoint | Check that all in ceiling services are connected and there are no loose cables. |  |  | Good
checkpoint | Conduits saddled correctly, all box lids fitted |  |  | Good
checkpoint | All subcircuits at DB location |  |  | Good
checkpoint | Checked and completed |  |  | Good
checkpoint | Tested and Witnessed |  |  | Good
textbox | Tested By |  |  | Good
textbox | Winessed By |  |  | Good
checklist | Cable Tray and Trunking Check Sheet |  | Cable Tray and Trunking Check Sheet | 2. QA by room name
checkpoint | Are all trays and trunking level and straight. |  |  | Good
checkpoint | Are all rods straight. |  |  | Good
checkpoint | Are all unistrut supports level and straight. |  |  | Good
checkpoint | Are all unistrut supports square to tray and trunking. |  |  | Good
checkpoint | Are all tray and trunking nuts and bolts tight and locked down to supports. |  |  | Good
checkpoint | Have all exposed cut metal work been protected with the galvanised paint. |  |  | Good
checkpoint | Have all 'over drilled' areas or incorrect holes been filled and painted. |  |  | Good
checkpoint | Are all trays and trunking bonded. |  |  | Good
checkpoint | Has the seismic bracing been installed. |  |  | Good
checkpoint | Are all tray runs and rods aligned. |  |  | Good
checkpoint | Checked and completed |  |  | Good
checklist | Generator Operation Scenario Test |  | Generator Operation Scenario Test | T&C
checkpoint | Fail the mains with the generator circuit breaker closed and return to mains |  |  | Good
textbox | Confirm that outcome is acceptable and note any items to be reviewed below: |  |  | Good
checkpoint | Fail the mains with the generator controls isolated and return to mains |  |  | Good
textbox | Confirm that outcome is acceptable and note any items to be reviewed below: |  |  | Good
checkpoint | Reinstate mains with the mains controls isolated: |  |  | Good
textbox | Confirm that outcome is acceptable and note any items to be reviewed below: |  |  | Good
checkpoint | Reinstate mains with the generator controls isolated |  |  | Good
textbox | Confirm that outcome is acceptable and note any items to be reviewed below: |  |  | Good
checkpoint | On generator reinstate the mains for 5 seconds then fail |  |  | Good
textbox | Confirm that outcome is acceptable and note any items to be reviewed below: |  |  | Good
checkpoint | Fail the mains for 5 seconds then reinstate |  |  | Good
textbox | Confirm that outcome is acceptable and note any items to be reviewed below: |  |  | Good
checkpoint | Isolate the mains, the generator and all controls. Manually start the generator and put power to the MSB. |  |  | Good
textbox | Confirm that outcome is acceptable and note any items to be reviewed below: |  |  | Good
checkpoint | With the site failed and running manually return to auto and reinstate mains |  |  | Good
textbox | Confirm that outcome is acceptable and note any items to be reviewed below: |  |  | Good
checkpoint | Notes |  |  | Good
textbox | Notes: |  |  | Good
checkpoint | Tested |  |  | Good
textbox | Tested By: |  |  | Good
checklist | Distribution Board Post-livening Check Sheet - PFC |  | Distribution Board Post-livening Check Sheet - PFC
checkpoint | Confirm pre livening check is complete
checkpoint | Confirm the correct voltage is present
textbox | R-W
textbox | B-N
textbox | R-B
textbox | R-E
textbox | W-B
textbox | W-E
textbox | R-N
textbox | B-E
textbox | W-N
textbox | N-E
checkpoint | Confirm the correct polarity and phase rotation
textbox | R
textbox | W
textbox | B
textbox | N
checkpoint | Confirm the correct control voltage is present
checkpoint | Confirm all meters/monitoring devices are setup correctly and operational
checkpoint | Confirm the PFC controller is set up correctly and operational
checkpoint | Confirm all switching devices (ACB's, MCCB's, MCB's etc) are switching correctly
checkpoint | Confirm all auxilaries are swithcing correctly
checkpoint | Confirm all adjustable circuit breaker settings are recorded and correct
checkpoint | Confirm switchboard is ready to be put into service
checkpoint | Special Conditions
textbox | Conditions
checkpoint | Tested
textbox | Tested By
checkpoint | Confirm Ready To Be Livened
signoff | Request Confirmation
checklist | Distribution Board Pre-livening Check Sheet |  | Distribution Board Pre-livening Check Sheet
textbox | Switchboard Name |  |  | Add
textbox | Location |  |  | Add
checkpoint | Confirm Distribution Board room / position meets regulations |  |  | Good
checkpoint | Confirm board is securely fastened |  |  | Good
checkpoint | Confirm Supplier has completed all site testing including shipping breaks |  |  | Good
checkpoint | Confirm there is NO link between the earth & neutral bars |  |  | Good
checkpoint | Check that the board has an identification label matching the single line diagram |  |  | Good
checkpoint | Confirm main incoming earth is labelled |  |  | Good
checkpoint | Check that there is an earth bond to the case of the switchboard and doors |  |  | Good
checkpoint | Check that metal work is undamaged and free of corrosion |  |  | Good
checkpoint | Check that MCB/isolator ratings match the switchboard schedules / SLD |  |  | Good
checkpoint | Check that all circuit terminations have phase identification |  |  | Good
checkpoint | Check all sub-main & sub-circuit breakers have been 'tagged off' prior to livening |  |  | Good
checkpoint | Confirm there is a copy of the circuit schedule in the board |  |  | Good
checkpoint | Confirm all connections are tight including circuit breakers to chassis |  |  | Good
button | Sub Main Neutrals | Complete,N/A |  | Good
button | Main Neutral | Complete,N/A |  | Good
button | Sub Main Earths | Complete,N/A |  | Good
button | Mains | Complete,N/A |  | Good
button | Main Earth | Complete,N/A |  | Good
button | Sub Mains CBs | Complete,N/A |  | Good
textbox | Insulation resistance between bus and earth |  |  | Need to enter result - textbox
checkpoint | Special Conditions |  |  | Good
textbox | Conditions |  |  | Good
checkpoint | Tested |  |  | Good
textbox | Tested By |  |  | Good
checkpoint | Confirm Ready To Be Livened |  |  | Good
signoff | Request Confirmation |  |  | Good
checklist | Generator Operation Check Sheet |  | Generator Operation Check Sheet
checkpoint | Information |  |  | Good
textbox | Generator connects to: |  |  | Good
textbox | Location |  |  | Good
checkpoint | Please follow the below steps in order to confirm the correct operation of the geset: |  |  | Good
checklist-flat | Checks
checkpoint | Confirm generator connection cable Pre-Livening check sheet has been completed |  |  | Good
checkpoint | Manually start the generator with the output isolated and confirm operation |  |  | Good
checkpoint | Manually start the generator with the output isolated and confirm operation |  |  | Is this a double up?
checkpoint | Special Conditions |  |  | Need to enter, textbox?
checkpoint | Close generator output circuit breaker and complete Post-Livening check sheet |  |  | Good
checkpoint | Confirm Post-Livening check sheet has been completed |  |  | Good
checkpoint | Confirm the remote start/stop signal is connected to the generator and operational |  |  | Good
checkpoint | Test the remote start/start signal with the generator supply isolated |  |  | Good
checkpoint | Confirm generator is now ready to be put into remote service |  |  | Good
checkpoint | With the generator supply and controls isolated confirm the operation of the ATS |  |  | Good - have a N/A option
checkpoint | Check the ATS time delays are set correctly |  |  | Good - have a N/A option
checkpoint | Confirm the operation of the PFR to start and stop the generator |  |  | Good - have a N/A option
checkpoint | Confirm both ATS1 and ATS2 are ready to be put into service |  |  | Delete
checkpoint | Put the generator into remote start operation |  |  | Good - have a N/A option
checkpoint | Isolate the power to the MSB and confirm the generator starts |  |  | Good - have a N/A option
checkpoint | Confirm the ATS units change from Mains to Generator supply |  |  | Good - have a N/A option
checkpoint | Confirm the plant supplied from the generator is now live |  |  | Good - have a N/A option
checkpoint | Reinstate power to the MSB and confirm that the ATS units change back to Mains |  |  | Good - have a N/A option
checkpoint | Confirm that the generator stops |  |  | Good - have a N/A option
checkpoint | Confirm that the generator is now ready to be put into remote service |  |  | Good - have a N/A option
Have a notes and comments textbox here
checklist | Pre - Livening Cable Installation Check Sheet - Multi Set Three Phase |  | Pre - Livening Cable Installation Check Sheet - Multi Set Three Phase
checkpoint | Cable Details |  |  | Good
textbox | Cores (eg4c, 4x1 C)
textbox | Earth conductor size
textbox | Breaker size (A)
textbox | Conductor size
textbox | Conductor material
textbox | Cable runs from
textbox | Conductor insulation
textbox | Cable runs to
checkpoint | Prior to any testing ensure cable terminations are isolated and safe.
note | Using a 1000 volt insulation tester test and record the resistance between
checkpoint | Bundle 1
textbox | Red to Earth
textbox | White to Earth
textbox | Blue to Earth
textbox | Neutral to Earth
textbox | White to Neutral
textbox | Red to Blue
textbox | Red to White
textbox | Blue to Neutral
note | Confirm Cable Continuity Phase ID & Polarity
textbox | Red to Neutral
textbox | White to Blue
checkpoint | Bundle 2
textbox | Red to Earth
textbox | White to Earth
textbox | Blue to Earth
textbox | Neutral to Earth
textbox | White to Neutral
textbox | Red to Blue
textbox | Red to White
textbox | Blue to Neutral
note | Confirm Cable Continuity Phase ID & Polarity
textbox | Red to Neutral
textbox | White to Blue
checkpoint | Bundle 1
textbox | White Phase
textbox | Blue Phase
textbox | Red Phase
textbox | Earth
textbox | Neutral
checkpoint | Bundle 2
textbox | White Phase
textbox | Blue Phase
textbox | Red Phase
textbox | Earth
textbox | Neutral
checkpoint | Special Conditions
textbox | Conditions
checkpoint | Tested By
textbox | Tested by
checkpoint | Confirmation, ready to be livened