## Resources
Rich Type | Id | Warnings | type | name | values | prefix | postfix | Usage Count | User Addable | Template Name | Template Id
checklist-flat |  |  | checklist | ENT-009 - Pressure Test Report |  |  |  |  | Yes | ENT-009 - Pressure Test Report | 00f2a3c3-6814-42bf-a066-75a018ef2f8b
checkpoint-status |  |  | checkpoint | Test Details & Results
select | f15838a7-bbd1-5211-990e-0ca572c698b3 |  | dropdown | Select correct test criteria for Test | TEST CRITERIA HYDRANT HOSEREELS - HYDROSTATIC TEST – 1700kpa 2 HOURS,TEST CRITERIA FIRE SPRINKLERS - HYDROSTATIC TEST – 1700kpa 2 HOURS,TEST CRITERIA GAS SUPPRESSION - PNEUMATIC TEST – 300kpa 10 MINS - PRESSURE DROP SHALL NOT EXCEED 20% (60kpa),TEST CRITERIA WATER MIST - HYDROSTATIC TEST – 3300kpa 2 HOURS,Other (Specify below)
text | cf2ae07e-f213-52d0-86ae-53a4050fdda2 |  | textbox | Other (Specify here)
text | 601967a3-9f87-52ad-844b-be815ee9c46a |  | textbox | Test No.
text | 525b0ccf-9401-500d-9c9c-5ef4faa69a7d |  | textbox | Gauge Reference (or Attach photo below)
text | 307b054d-5737-5367-bb16-0e74168b3304 |  | textbox | Start Date
text | fee6c9bf-9981-5fcf-854f-8eb51140896f |  | textbox | Start Time
text | 77346f67-e749-5e1a-826b-a688e8881b5d |  | textbox | Start Pressure
text | 98a8f994-a48d-55d8-b0a7-e4e27e627ff0 |  | textbox | Final Pressure
text | 0cecbdaf-95a9-5213-9185-f0c9970a7adf |  | textbox | finish Time
checkpoint-status |  |  | checkpoint | Sign-Off Test completed to specification/drawings & Area left clean/tidy
label | d9cd216f-b8e9-55d1-9aee-3784ff992c12 |  | note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
button | 888eb9f7-09a2-5a07-8ed2-1c8c71720808 |  | button | Entire Fire Signature Sign-Off added below | Yes,No
checklist-flat |  |  | checklist | ENT-012 - Register of Non-Conformance Reports x10 |  |  |  |  | Yes | ENT-012 - Register of Non-Conformance Reports x10 | 184d0b72-fffb-4f1d-9dbd-4e0787bd2c90
checkpoint-status |  |  | checkpoint | Item 1. Pass once entered
text | f3651b7f-c222-5102-ad01-abeb5939bfad |  | textbox | Report Number
text | bd0857d5-caa6-5dd7-8522-b461173aa9aa |  | textbox | Description
button | c482cbdb-57b5-50ad-ab46-38b3968bb9a1 |  | button | Non-Conformance rectified (Input date below) | Yes,No
text | 563eb759-2e6b-5650-9f62-661bf94e49d4 |  | textbox | Date rectified
button | 37a39615-008b-5d2f-ad1a-d0835f7cba7e |  | button | Non-Conformance approved (Input date below) | Yes,No
checkpoint-status |  |  | checkpoint | Item 2. Pass once entered
text | bfce4f2a-055e-546b-a540-288263e1f584 |  | textbox | Report Number
text | 2fb894b5-baef-5bbe-bf06-a23691ad632b |  | textbox | Description
button | a1e0c043-4b2e-5db7-9049-09fbd57df5c0 |  | button | Non-Conformance rectified (Input date below) | Yes,No
text | 5e539f3b-56ed-502a-82d1-7cde194b41bb |  | textbox | Date rectified
button | 0e75e92c-1e06-5e78-b272-01e2e8cd00ad |  | button | Non-Conformance approved (Input date below) | Yes,No
checkpoint-status |  |  | checkpoint | Item 3. Pass once entered
text | d7ec281a-e64c-5959-b369-b527b1df4810 |  | textbox | Report Number
text | e53685ab-ab46-5a76-9fce-9b77e98f4ddb |  | textbox | Description
button | 73380838-254d-545d-9d70-27aa896b3693 |  | button | Non-Conformance rectified (Input date below) | Yes,No
text | bfe103c2-54ff-5419-9d96-75ac976a087a |  | textbox | Date rectified
button | 5580ceee-b3d2-5b4c-aef6-76bfea1d0ca4 |  | button | Non-Conformance approved (Input date below) | Yes,No
checkpoint-status |  |  | checkpoint | Item 4. Pass once entered
text | 0c36cc35-0470-53cd-9b98-663b4109a857 |  | textbox | Report Number
text | c6d3ca81-7f52-5f54-b010-c6b771298aa0 |  | textbox | Description
button | f2970c4c-c62a-5ecf-b9df-30a7c820a93a |  | button | Non-Conformance rectified (Input date below) | Yes,No
text | 9fa144dd-b52b-5219-85af-4211f2c97131 |  | textbox | Date rectified
button | 1b18d61e-44b6-5b74-b47b-9b583ed6c96d |  | button | Non-Conformance approved (Input date below) | Yes,No
checkpoint-status |  |  | checkpoint | Item 5. Pass once entered
text | 30d45803-8d4e-5d29-832f-4079b401f686 |  | textbox | Report Number
text | dfed5372-a70b-5700-ae94-cb00ac1d70ec |  | textbox | Description
button | 4c5da499-2402-5742-85b7-2be7e06f9ffe |  | button | Non-Conformance rectified (Input date below) | Yes,No
text | cf11ac2b-7e19-5b75-92ee-413a46e8f513 |  | textbox | Date rectified
button | 01fb0597-0433-5239-b678-1d9922f93c32 |  | button | Non-Conformance approved (Input date below) | Yes,No
checkpoint-status |  |  | checkpoint | Item 6. Pass once entered
text | e1b717d9-6278-51bf-9765-486280b27f87 |  | textbox | Report Number
text | 973b2ed7-5063-589a-bdf5-e9dad9323b61 |  | textbox | Description
button | 19fe5669-b05a-5730-ba81-a285e6ec672a |  | button | Non-Conformance rectified (Input date below) | Yes,No
text | 0d0ff253-6b67-5c89-9e25-1fa10a2f8f05 |  | textbox | Date rectified
button | 85ba4eab-36a0-5ee9-81ef-c26ccf68b9cf |  | button | Non-Conformance approved (Input date below) | Yes,No
checkpoint-status |  |  | checkpoint | Item 7. Pass once entered
text | fe9c9061-33f6-5fc4-a5ef-78bf7fb627c8 |  | textbox | Report Number
text | 372b5626-1bc3-51d8-ab08-da92dae5749e |  | textbox | Description
button | 889a626b-71ab-541b-b61b-bec4d20b6c85 |  | button | Non-Conformance rectified (Input date below) | Yes,No
text | 5aa74084-ca51-54b6-bdec-db04baecc1f5 |  | textbox | Date rectified
button | b51fbac9-6c3f-57e8-999b-2017e88da98a |  | button | Non-Conformance approved (Input date below) | Yes,No
checkpoint-status |  |  | checkpoint | Item 8. Pass once entered
text | dab14d09-2437-5758-b382-1adeaba2ff56 |  | textbox | Report Number
text | 6c40591a-bd1f-5ee6-b3a8-bbab21366983 |  | textbox | Description
button | bbbc1074-dcc9-541a-a1b8-18e601ab5cb5 |  | button | Non-Conformance rectified (Input date below) | Yes,No
text | 0beae4ef-1c22-5a24-a5cc-fa027bd5fc65 |  | textbox | Date rectified
button | d8d993f3-a383-521f-9bbf-60ef18345767 |  | button | Non-Conformance approved (Input date below) | Yes,No
checkpoint-status |  |  | checkpoint | Item 9. Pass once entered
text | fcf40739-81ca-5f46-81f5-a331393648a0 |  | textbox | Report Number
text | 4ba7fce9-62d1-59e5-9d46-36cab57940a4 |  | textbox | Description
button | db91b353-ddee-53da-a74a-eaa0c8d49abf |  | button | Non-Conformance rectified (Input date below) | Yes,No
text | 37e1ea92-2219-584e-be66-82e30f4710a6 |  | textbox | Date rectified
button | 280de89a-28f6-5215-9830-bc8c04a7825d |  | button | Non-Conformance approved (Input date below) | Yes,No
checkpoint-status |  |  | checkpoint | Item 10. Pass once entered
text | 717acd04-e358-5c06-b160-1e96e1e5f170 |  | textbox | Report Number
text | 8e63e558-1115-53c8-96f2-a4560e5da851 |  | textbox | Description
button | 44d6ece9-1a61-573f-bf43-f85f948483c7 |  | button | Non-Conformance rectified (Input date below) | Yes,No
text | 5c7c44d7-7b6b-5639-a5e8-a1c8822673a7 |  | textbox | Date rectified
button | 3f262752-00b5-5a3e-87d4-742544b7b654 |  | button | Non-Conformance approved (Input date below) | Yes,No
checkpoint-status |  |  | checkpoint | Sign-Off Records completed
label | 993b5a51-1e02-5eb2-81d4-43cb64c743a6 |  | note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
button | 5b34de31-7185-5b9f-bf18-83744a9c7830 |  | button | Entire Fire Signature Sign-Off added below | Yes,No
checklist-sectioned |  |  | checklist | ENT-019 - MASDS |  |  |  |  | Yes | ENT-019 - MASDS | 277daa90-9a3f-4b8d-96fe-cbd9e730e42e
checkpoint-group |  |  | section | Pre-Start
checkpoint-status |  |  | checkpoint | Specification reference checked
label | 1a899a0c-a4a4-56af-8d62-5e824b677648 |  | note | Specification Ref: AS:1670, AS:3000, BCA and drawing
checkpoint-status |  |  | checkpoint | Cable/Conduit/Tray
label | 9895608a-6e2b-5147-b318-847e4a6a3c48 |  | note | PASS if received in good condition - If not FAIL & Attach Photos/Comments below
checkpoint-status |  |  | checkpoint | MASDS Sampling Pipework
label | b1db071c-f7d4-5482-a296-6a1d6bb96ea0 |  | note | PASS if received in good condition - If not FAIL & Attach Photos/Comments below
checkpoint-status |  |  | checkpoint | MASDS Unit
label | 17b5fe49-d7a0-597e-9591-5c1838b08262 |  | note | PASS if received in good condition - If not FAIL & Attach Photos/Comments below
checkpoint-group |  |  | section | Installation Rough-In
checkpoint-status |  |  | checkpoint | Correct cable used (eg Fire rated as required)
checkpoint-status |  |  | checkpoint | Cable Support
checkpoint-status |  |  | checkpoint | Segregation from other electrical services
checkpoint-status |  |  | checkpoint | Type of cable fixing & spacing
checkpoint-status |  |  | checkpoint | No cable joins between equipment
checkpoint-status |  |  | checkpoint | Conduit type
checkpoint-status |  |  | checkpoint | Conduit fixings
checkpoint-status |  |  | checkpoint | MASDS
checkpoint-group |  |  | section | Installation Fit-Off
checkpoint-status |  |  | checkpoint | Sampling Points Installed
checkpoint-status |  |  | checkpoint | MASDS installed & connected to FIP
checkpoint-status |  |  | checkpoint | MASDS Panel Fit Off
checkpoint-status |  |  | checkpoint | Strobes/ Illuminated signs installed
checkpoint-status |  |  | checkpoint | Confirm obscuration and alarm thresholds
checkpoint-status |  |  | checkpoint | Measure transport times
checkpoint-group |  |  | section | Commissioning
checkpoint-status |  |  | checkpoint | Obscuration Levels Set
checkpoint-status |  |  | checkpoint | Confirm Travel Times
checkpoint-group |  |  | section | Sign-Off
checkpoint-status |  |  | checkpoint | Work(s) completed to specification/drawings & Area left clean/tidy - Builder final signature to be attached below if applicable
checklist-sectioned |  |  | checklist | ENT-020 - Occupant Warning System/EWIS |  |  |  |  | Yes | ENT-020 - Occupant Warning System/EWIS | 280d6ab1-0b91-4c38-8215-fe67c8eaa89f
checkpoint-group |  |  | section | Pre-Start
checkpoint-status |  |  | checkpoint | Specification reference checked
label | db86d874-2e4f-5b17-8d6e-de73969fb81a |  | note | Specification Ref: AS:1670, AS:3000 and drawing
text | 641c58fa-7d54-5878-90c2-96b29184997a |  | textbox | Drawing & Revision # (or Attach photo below)
checkpoint-status |  |  | checkpoint | Area clear, tidy and accessible
label | f998ff2e-ffdf-5c1d-8adc-7962ad23f6b7 |  | note | Attach Photos/Comments below if any issues & Send report to Builder
checkpoint-status |  |  | checkpoint | Cable/Conduit/Tray
label | 8a8979fd-710b-5e18-a85c-854bbed130f4 |  | note | PASS if received in good condition - If not FAIL & Attach Photos/Comments below
checkpoint-status |  |  | checkpoint | Speakers/Strobes
label | 3f4b3eda-f59a-5941-8c85-1e5e99810709 |  | note | PASS if received in good condition - If not FAIL & Attach Photos/Comments below
checkpoint-group |  |  | section | Installation Rough-In
checkpoint-status |  |  | checkpoint | Correct cable used (eg Fire rated as required)
checkpoint-status |  |  | checkpoint | Cable Support
checkpoint-status |  |  | checkpoint | Segregation from other electrical services
checkpoint-group |  |  | section | Installation Fit-Off
checkpoint-status |  |  | checkpoint | Speakers/Strobes
checkpoint-status |  |  | checkpoint | OWS Panel
checkpoint-group |  |  | section | Commissioning
checkpoint-status |  |  | checkpoint | Confirm operation of all speakers/strobes
checkpoint-status |  |  | checkpoint | Confirm decibel levels
checkpoint-status |  |  | checkpoint | Confirm OWS operation initiated from FDCIE
checkpoint-group |  |  | section | Sign-Off
checkpoint-status |  |  | checkpoint | Work(s) completed to specification/drawings & Area left clean/tidy - Builder final signature to be attached below if applicable
checklist-sectioned |  |  | checklist | ENT-006 - Hydrants & Hosereels rough in and fit off |  |  |  |  | Yes | ENT-006 - Hydrants & Hosereels rough in and fit off | 36b9292d-dc8c-4efc-908f-7addd0be9f06
checkpoint-group |  |  | section | Pre-Start
checkpoint-status |  |  | checkpoint | Specification reference checked
label | 52b6d2e4-fa60-5674-921e-7c0656f53d86 |  | note | Specification Ref: AS:2118, AS:2415, AS:2414, AS:1530, AS:2419 and drawing
text | 30ff5340-1dcd-5d33-9029-1716d81e4e9e |  | textbox | Drawing & Revision # (or Attach photo below)
checkpoint-status |  |  | checkpoint | Area clear, tidy and accessible
label | 246c17b7-7191-59a1-9557-ab73b713dd59 |  | note | Attach Photos/Comments below if any issues & Send report to Builder
checkpoint-status |  |  | checkpoint | Pipe + Fittings
label | 605a7395-90df-5e49-9bac-680afda772d3 |  | note | PASS if received in good condition - If not FAIL & Attach Photos/Comments below
checkpoint-status |  |  | checkpoint | Hose Reels / Millcocks
label | 40008aff-641b-53a1-8f1e-b4f8f24caaf0 |  | note | PASS if received in good condition - If not FAIL & Attach Photos/Comments below
checkpoint-group |  |  | section | Installation Rough-In
checkpoint-status |  |  | checkpoint | Mains & branches installed to drawing
checkpoint-status |  |  | checkpoint | Hangers Location
checkpoint-status |  |  | checkpoint | Pentrations sealed
checkpoint-group |  |  | section | Installation Fit-Off
checkpoint-status |  |  | checkpoint | Hose Reels (Minimum Clearances)
checkpoint-status |  |  | checkpoint | Millcocks (Minimum Clearances)
checkpoint-status |  |  | checkpoint | Pressure Test
label | 4ec0dec7-caff-5b12-8f67-ab055e5c8155 |  | note | Specification Ref: QCF-ENT-009
text | 605694f5-cb79-557a-8558-50717a648fa3 |  | textbox | Test No.
checkpoint-status |  |  | checkpoint | Pipe Identification Labelling
checkpoint-status |  |  | checkpoint | Statutory Signage
label | fd1b8280-e949-5f14-aa03-d48a2bdaace4 |  | note | Completed By Others
checkpoint-group |  |  | section | Commissioning
checkpoint-status |  |  | checkpoint | Flow Tests
label | 828c5f11-ffb7-523c-96d0-6b39d7ce7cbc |  | note | By Independent Certifier - Attached below as applicable
checkpoint-status |  |  | checkpoint | Certification
label | b018d5d2-aaaa-547e-b0b5-50d480cb7e0f |  | note | By Independent Certifier - Attached below as applicable
checkpoint-group |  |  | section | Sign-Off
checkpoint-status |  |  | checkpoint | Work(s) completed to specification/drawings & Area left clean/tidy - Builder final signature to be attached below if applicable
checklist-flat |  |  | checklist | ENT-007 Site works completion summary (hydrants and hosereels) |  |  |  |  | Yes | ENT-007 Site works completion summary (hydrants and hosereels) | 3972c3ac-71fe-408f-8024-533569f4f87e
checkpoint-status |  |  | checkpoint | Drawing number
text | 503b6cf1-1bcb-5c0b-b850-475781efd87c |  | textbox | Hydrants/hosereels rough in (ENT-006) date completed
text | 450e59f4-ae00-5530-89b5-2809349d25d7 |  | textbox | Hydrants/hosereels fit off (ENT-006) date completed
checkpoint-status |  |  | checkpoint | Drawing number
text | f4049e47-2ec7-5ec8-a801-7c6a0f38901d |  | textbox | Hydrants/hosereels rough in (ENT-006) date completed
text | 7869fbec-a11a-5055-ae40-ae2ab8eb4ff7 |  | textbox | Hydrants/hosereels fit off (ENT-006) date completed
checkpoint-status |  |  | checkpoint | Drawing number
text | a72cab5d-bb70-5872-9a03-fe411be5e854 |  | textbox | Hydrants/hosereels rough in (ENT-006) date completed
text | 71a5ef4e-8182-5cdf-b94c-fd5e207a95e4 |  | textbox | Hydrants/hosereels fit off (ENT-006) date completed
checkpoint-status |  |  | checkpoint | Drawing number
text | 3c629dbd-c313-516f-8165-ad9d19cf1b62 |  | textbox | Hydrants/hosereels rough in (ENT-006) date completed
text | 9ffe8089-47d3-5a54-9634-d5b43caa6f4e |  | textbox | Hydrants/hosereels fit off (ENT-006) date completed
checkpoint-status |  |  | checkpoint | Drawing number
text | 77348bd3-4f84-52e3-8fb9-578b67454b6f |  | textbox | Hydrants/hosereels rough in (ENT-006) date completed
text | ff88abfa-bfd4-579e-bb2b-412b2867cbc4 |  | textbox | Hydrants/hosereels fit off (ENT-006) date completed
checkpoint-status |  |  | checkpoint | Drawing number
text | 76fdffc7-23ec-5b63-977c-d9e5b1a4aa66 |  | textbox | Hydrants/hosereels rough in (ENT-006) date completed
text | 919b3cdf-c91c-56a2-b7a1-507a83f9edea |  | textbox | Hydrants/hosereels fit off (ENT-006) date completed
checkpoint-status |  |  | checkpoint | Drawing number
text | a0413f84-f04d-5526-81fe-207d94d91a81 |  | textbox | Hydrants/hosereels rough in (ENT-006) date completed
text | 6934e86c-e1ff-5b4e-99e8-a384661bd02a |  | textbox | Hydrants/hosereels fit off (ENT-006) date completed
checkpoint-status |  |  | checkpoint | Drawing number
text | 0247eb0e-f37f-5864-9b4c-0364cc6b34ba |  | textbox | Hydrants/hosereels rough in (ENT-006) date completed
text | 17372482-5375-53ca-b355-79f50d0430e7 |  | textbox | Hydrants/hosereels fit off (ENT-006) date completed
text | 34c4a054-dc7c-5a8f-9598-d16a6599e6de |  | textbox | Sprinklers control valves (ENT-003) date completed
checkpoint-status |  |  | checkpoint | Sign-Off Records completed
label | 8811dc31-0742-549d-a49d-f68358549433 |  | note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
button | 2c3c14cf-be57-53d5-86ea-d2e0e3270fbe |  | button | Entire Fire Signature Sign-Off added below | Yes,No
checklist-sectioned |  |  | checklist | ENT-003 - Sprinkler control valves |  |  |  |  | Yes | ENT-003 - Sprinkler control valves | 417cefb9-db23-4461-81dc-c319918fa9f4
checkpoint-group |  |  | section | Installation
checkpoint-status |  |  | checkpoint | Specification reference checked
label | 678a29fe-d6d7-52e3-8f01-32a30d367dbe |  | note | Specification Ref: AS:2118 and drawing
checkpoint-status |  |  | checkpoint | Valves and valve monitors installed
checkpoint-status |  |  | checkpoint | Pressure switches supplied and operable
checkpoint-status |  |  | checkpoint | Pressure gauges fitted
checkpoint-status |  |  | checkpoint | Drains connected
checkpoint-status |  |  | checkpoint | Statutory Labelling
checkpoint-status |  |  | checkpoint | Certification
checkpoint-group |  |  | section | Sign-Off
checkpoint-status |  |  | checkpoint | Work(s) completed to specification/drawings & Area left clean/tidy - Builder final signature to be attached below if applicable
checklist-sectioned |  |  | checklist | ENT-013 - Fire Electrical rough in and fit off |  |  |  |  | Yes | ENT-013 - Fire Electrical rough in and fit off | 554c2398-6ed9-405e-beeb-5ea7ca43f79c
checkpoint-group |  |  | section | Pre-Start
checkpoint-status |  |  | checkpoint | Specification reference checked
label | c977b655-efee-5b77-8d7b-8675b79ff945 |  | note | Specification Ref: AS:1670, AS:3000, AS:1760, BCA and drawing
text | c7beb064-bff4-51ae-95e0-9b42c3bd1341 |  | textbox | Drawing & Revision # (or Attach photo below)
checkpoint-status |  |  | checkpoint | Area clear, tidy and accessible
label | 2320fa91-1200-59cb-8c81-6fcf0ef42a43 |  | note | Attach Photos/Comments below if any issues & Send report to Builder
checkpoint-status |  |  | checkpoint | Cable/Conduit/Tray
label | 5d90bb31-b273-5de0-a08c-33f724490a10 |  | note | PASS if received in good condition - If not FAIL & Attach Photos/Comments below
checkpoint-status |  |  | checkpoint | Fire Devices
label | 27940fbb-4d0c-5d1a-ac69-40dae7d1b425 |  | note | PASS if received in good condition - If not FAIL & Attach Photos/Comments below
checkpoint-group |  |  | section | Installation Rough-In
checkpoint-status |  |  | checkpoint | Correct cable used (eg Fire rated as required)
checkpoint-status |  |  | checkpoint | Cable Support
checkpoint-status |  |  | checkpoint | Segregation from other electrical services
checkpoint-status |  |  | checkpoint | Type of cable fixing and spacing
checkpoint-status |  |  | checkpoint | No cable joins between equipment
checkpoint-status |  |  | checkpoint | Conduit type
checkpoint-status |  |  | checkpoint | Conduit fixings
checkpoint-status |  |  | checkpoint | MASDS
checkpoint-group |  |  | section | Installation Fit-Off
checkpoint-status |  |  | checkpoint | Sensor locations as shown on drawings
checkpoint-status |  |  | checkpoint | Warden intercom phone locations
checkpoint-status |  |  | checkpoint | Break glass alarm located per drawings
checkpoint-status |  |  | checkpoint | Hold open devices located per drawings
checkpoint-status |  |  | checkpoint | Interface with Mechanical services
checkpoint-status |  |  | checkpoint | Interface with DDC
checkpoint-status |  |  | checkpoint | Sensors fixed correctly
checkpoint-status |  |  | checkpoint | FIP installed & connected
checkpoint-status |  |  | checkpoint | Connection of system to Tyco for Monitoring
checkpoint-status |  |  | checkpoint | MASDS Panel Fit Off
checkpoint-status |  |  | checkpoint | Strobes
checkpoint-group |  |  | section | Commissioning
checkpoint-status |  |  | checkpoint | Confirm all devices indicate at FDCIE
checkpoint-status |  |  | checkpoint | Confirm operation of all ancillary functions from FDCIE
checkpoint-status |  |  | checkpoint | FDCIE. Operate each alarm test, isolate and reset for each alarm zone
checkpoint-status |  |  | checkpoint | ASE. Confirm the master alarm facility receives all alarms
checkpoint-status |  |  | checkpoint | ASE. Confirm the master alarm facility receives all alarms
checkpoint-group |  |  | section | Sign-Off
checkpoint-status |  |  | checkpoint | Work(s) completed to specification/drawings & Area left clean/tidy - Builder final signature to be attached below if applicable
checklist-sectioned |  |  | checklist | ENT-FIRE-ITC07B Automatic Fire Sprinkler Flow Test Report Sheet |  |  |  |  | Yes | ENT-FIRE-ITC07B Automatic Fire Sprinkler Flow Test Report Sheet | 5d269828-224a-4454-95ef-83d9abf300b9
checkpoint-group |  |  | section | Pre-test details
checkpoint-status |  |  | checkpoint | Latest IFC drawings checked & referenced
text | 3aa6c657-9b43-58b2-8186-e0ba70f228d3 |  | textbox | Drawing & Revision # (or Attach photo below)
text | fc7290d5-35ed-5262-bc6e-d0775118cd7a |  | textbox | Grid Ref
button | 883ae892-4144-5289-9926-47e36c86fa2d |  | button | Area clear, tidy and accessible | Yes,No
label | 591769bb-53f7-5416-baa5-3fdab22c8522 |  | note | Attach Photos/Comments below if any issues & Send report to Builder
checkpoint-status |  |  | checkpoint | Year & Height - pass once entered
text | 54d41479-a030-5860-9f02-86ac277f3753 |  | textbox | Year of installation
text | f90f7ffa-2557-525f-b48a-b6759b8361c2 |  | textbox | Head height (m)
select | 477fc623-ee5c-5f25-958d-1ea48e71c707 |  | dropdown | Classification | xlh,oh,xhh,other (Specify below)
text | efafd6c5-b178-5ac5-a599-e30609ecd651 |  | textbox | Other (Specify here)
checkpoint-status |  |  | checkpoint | Block Plan Flow 1 - pass once entered (n/a if not applicable)
text | e3ebc613-bdd3-5163-8055-eefa369a02b1 |  | textbox | l/min
text | 69393741-308c-54f4-aa77-520831705f78 |  | textbox | kPa
checkpoint-status |  |  | checkpoint | Block Plan Flow 2 - pass once entered (n/a if not applicable)
text | 3ee6acdf-4b36-566f-a7ef-2f15a821d7b2 |  | textbox | l/min
text | 0b744bfd-bd67-5d80-986f-f052244df6aa |  | textbox | kPa
checkpoint-status |  |  | checkpoint | Block Plan Flow 3 - pass once entered (n/a if not applicable)
text | e996a70b-b55b-50bc-bec3-5426c0eb4a0a |  | textbox | l/min
text | a118f296-5557-58ac-9ad8-6e043cdbea00 |  | textbox | kPa
checkpoint-status |  |  | checkpoint | Block Plan Flow 4 - pass once entered (n/a if not applicable)
text | c9873e2d-0459-557d-8caa-1f71a715bb9b |  | textbox | l/min
text | 2efb8bbd-3a98-5866-a289-ba6a11c78dd5 |  | textbox | kPa
checkpoint-status |  |  | checkpoint | Block Plan Flow5 - pass once entered (n/a if not applicable)
text | bd2bfa99-3423-5d4b-8ac8-5be1052570a4 |  | textbox | l/min
text | 5c5304c8-fc23-56cf-afdc-a9f9fc71a118 |  | textbox | kPa
checkpoint-status |  |  | checkpoint | Water supply and mains - pass once entered
button | 96cabf54-4390-5c3a-94fb-26a7717b626c |  | button | Water supply - grade | 1,2,3
text | 6446e4e8-a64b-5cac-ae55-e435e6cf68db |  | textbox | Towns main #1
text | 4ee0bdaa-76ff-5ba3-b91f-fd4d5c6cb9e4 |  | textbox | Towns main #2
checkpoint-status |  |  | checkpoint | Tank details - pass once entered
button | 15559ed3-2639-5aa8-8247-a39aac260c0a |  | button | Tank supply (Y/N) | Yes,No
text | a83e48dc-d3b0-5214-a5a0-b712ed8a9648 |  | textbox | Capacity
text | 2e674453-fd34-5b25-915b-2ed1775cd711 |  | textbox | Status
checkpoint-status |  |  | checkpoint | Pump details - pass once entered
select | 8cba8ab1-493f-5dda-971b-09cfd406c3ad |  | dropdown | Pump type | Electric,Diesel
text | 3a60441a-ccc3-58a0-9bf4-c3eb47b7d36d |  | textbox | Make
text | 4adb598d-bbb9-5ada-8ca6-5c4a72489e66 |  | textbox | Serial no
text | c45e30a4-8a1d-5ab0-af7a-19b872a22e5c |  | textbox | Rated flow & pressure
text | fa76c5b3-88b1-5de0-951a-b65ba67ff3e5 |  | textbox | Cut-in pressure
text | fd920331-17a8-5ce5-b9ff-07b98ac0ae94 |  | textbox | Pump orifice size (if electric)
text | 94dc37ef-4fe8-5742-88d6-84ff7b8d8727 |  | textbox | K-factor (if electric)
text | e606007e-8b42-5c25-83e9-aa245f0cd127 |  | textbox | Annubar size (if diesel)
button | 052ae756-7110-5c95-8003-54ee75bc4b14 |  | button | Annubar type (if diesel) | Round,Diamond
text | afb83bb0-458b-516b-83e3-df2ca898ad7c |  | textbox | Measuring device
checkpoint-group |  |  | section | Pressure Tests (kPa)
checkpoint-status |  |  | checkpoint | Pressure test 1 (n/a if not required)
text | 18b93077-cc3a-5f0d-9016-e9222b4d7dbe |  | textbox | %
text | e3a6841b-38b3-5902-8c84-d42e551929d2 |  | textbox | L/min
text | 39f4d5b4-81de-5290-8f07-804649045235 |  | textbox | T/main no.1
text | c34da92a-2e8c-520f-b491-b0f9fa7a4417 |  | textbox | Inst. gauge
text | 7462bd37-9f6f-59c7-8372-a2c42e7932e2 |  | textbox | T/main no.2
text | 73073147-e9e3-5348-abdd-de4428a654d3 |  | textbox | Inst. gauge
text | 93f44bdb-f35d-55e3-a046-a24578c18d9a |  | textbox | Comb. main
text | 652a1d29-55c9-523f-9b61-a701763ed6e0 |  | textbox | Inst. gauge
checkpoint-status |  |  | checkpoint | Pressure test 2 (n/a if not required)
text | 39b848d9-5bdf-58f1-8e41-95cff4bfdfeb |  | textbox | %
text | f19936c0-a1f1-5b06-901d-2fc7b622fdb4 |  | textbox | L/min
text | 21173c2b-b1a2-53ee-a49b-95abd8e8b0e0 |  | textbox | T/main no.1
text | 1ba931bb-8d18-58f7-95f7-18e11217eba8 |  | textbox | Inst. gauge
text | 29395288-6e3f-5756-bf40-cd0925b0f715 |  | textbox | T/main no.2
text | 62028ba6-ddfe-5602-9c7e-63c889e443e3 |  | textbox | Inst. gauge
text | 8bc1b4d7-0346-58fb-bc84-c6ae8e2f9e01 |  | textbox | Comb. main
text | 27db0644-f915-542b-acd9-8da4c78c33e2 |  | textbox | Inst. gauge
checkpoint-status |  |  | checkpoint | Pressure test 3 (n/a if not required)
text | 1e3900da-493b-5b28-9c65-194eecb6e807 |  | textbox | %
text | cf8d30cc-bd03-5d16-93ed-a41c2b4a415a |  | textbox | L/min
text | 42b9c7f4-326c-54c1-8774-197787a55bf6 |  | textbox | T/main no.1
text | 6dd48744-980c-5333-9b09-e1d50dcc9de3 |  | textbox | Inst. gauge
text | d95012b1-960d-531c-8781-0675e86edfd9 |  | textbox | T/main no.2
text | da3118fd-666c-5d3e-aff6-4f5a12514e0b |  | textbox | Inst. gauge
text | 66ec3658-0c1a-56e6-81ba-63175a0591bd |  | textbox | Comb. main
text | 47335aca-6005-5207-aa5b-d31251e51757 |  | textbox | Inst. gauge
checkpoint-status |  |  | checkpoint | Pressure test 4 (n/a if not required)
text | 09541f5a-8d24-5b3e-8f30-21017fae8267 |  | textbox | %
text | 14ec6b67-e9fc-5436-9b33-002ad12dd5eb |  | textbox | L/min
text | 53e661e5-56e6-55e7-8c9e-05945599471c |  | textbox | T/main no.1
text | 5495fe44-3085-58cd-9147-7f6c390bee59 |  | textbox | Inst. gauge
text | 7098c045-4afa-5f5d-925e-3259a0a618b6 |  | textbox | T/main no.2
text | 1b0e2bdd-2589-5983-8ed4-afeb1a65ac5b |  | textbox | Inst. gauge
text | d7dad531-da7b-5500-b026-02a8a378a1b3 |  | textbox | Comb. main
text | a7cab992-2f63-5005-802c-6be2238be256 |  | textbox | Inst. gauge
checkpoint-status |  |  | checkpoint | Pressure test 5 (n/a if not required)
text | a806f6e7-db71-5b19-8963-ccba9c8bfce1 |  | textbox | %
text | 99dc4f8c-4e4d-5d71-a986-4b287b99aa08 |  | textbox | L/min
text | 45cd6012-2909-5b2f-9c85-d9c247e0ba65 |  | textbox | T/main no.1
text | 933e5ef3-8c5d-529c-a2f2-6f6c78c09292 |  | textbox | Inst. gauge
text | 30d149b1-ac60-54ff-b018-0218450cd50e |  | textbox | T/main no.2
text | 9c4f2507-77b3-5948-a301-c095bd3fc911 |  | textbox | Inst. gauge
text | 9c1426f6-7d68-56e4-b635-a574597a5c61 |  | textbox | Comb. main
text | 7abec98a-5abb-527c-b9e4-50ad8fd250a0 |  | textbox | Inst. gauge
checkpoint-status |  |  | checkpoint | Pressure test 6 (n/a if not required)
text | 14aa481b-4250-5d40-b6f1-2272a2845071 |  | textbox | %
text | 5c17eef1-ef22-50d3-868b-3b7f6559bbf5 |  | textbox | L/min
text | cb7b2c6f-c1c0-55b0-b19e-373a46ed6b27 |  | textbox | T/main no.1
text | 0d183154-6a02-5d6e-90b7-3cf167f4a296 |  | textbox | Inst. gauge
text | 5efd7b4f-6274-5734-a7ae-5b50ac73d1ff |  | textbox | T/main no.2
text | 1fa7717f-6126-5993-98a2-2bdefd70fb2d |  | textbox | Inst. gauge
text | 14f17629-a61f-5f0b-bfdf-77c143385ab0 |  | textbox | Comb. main
text | 2a0f1e84-42e0-5a3e-83cb-52e54f149016 |  | textbox | Inst. gauge
checkpoint-status |  |  | checkpoint | Pressure test 7 (n/a if not required)
text | 14fd344d-6021-53d9-8d8b-b2d12ddcd17c |  | textbox | %
text | 60ff8d4c-4fc4-5465-84b1-a203b3254425 |  | textbox | L/min
text | e01233f4-6ca5-5b63-8ae1-c73c6f8ff402 |  | textbox | T/main no.1
text | 8386c596-fc62-5ef0-890b-7b308de4af25 |  | textbox | Inst. gauge
text | e8110bb0-e13c-51b9-8c56-aa066697fda0 |  | textbox | T/main no.2
text | 9881d38e-fcd1-56f0-8ef0-b0031e13b529 |  | textbox | Inst. gauge
text | 73bc6f32-3275-5ca9-981f-529640d16412 |  | textbox | Comb. main
text | 6b870744-76b0-5243-bac2-76ebf6079780 |  | textbox | Inst. gauge
checkpoint-status |  |  | checkpoint | Pressure test 8 (n/a if not required)
text | a200fc3b-8aee-5d4a-a981-39355e7f19ae |  | textbox | %
text | d64ac9c6-f67a-5a76-951e-228e89347fab |  | textbox | L/min
text | f8ab9743-8ed5-5152-9854-7b9d440710ca |  | textbox | T/main no.1
text | 17e7f5a0-ec72-5628-a9f0-690e1f48074e |  | textbox | Inst. gauge
text | 630beac4-9282-5abf-b198-c84ecdee8edc |  | textbox | T/main no.2
text | 3c454452-c775-5d04-9457-aefd4cc7ff42 |  | textbox | Inst. gauge
text | 8dd78d5f-79f0-5872-9ff2-03566dcf6726 |  | textbox | Comb. main
text | da0c35a6-fcb8-506e-9d2f-35c9fea80bc0 |  | textbox | Inst. gauge
checkpoint-status |  |  | checkpoint | Pressure test 9 (n/a if not required)
text | 4707b3ff-e309-5ace-bc3f-bbc3419d6baa |  | textbox | %
text | 068263df-8a17-5bbd-a130-daf53e550af3 |  | textbox | L/min
text | b8165960-7584-502d-a9eb-e3db141ea88d |  | textbox | T/main no.1
text | 951c6924-4475-5de0-8243-a31acf4547c9 |  | textbox | Inst. gauge
text | 85de7cf2-7eac-52d8-8873-7a1b605725f5 |  | textbox | T/main no.2
text | 671e8f3c-b998-5ae9-b1ce-6cbc240ef48c |  | textbox | Inst. gauge
text | a9047107-eb59-5ae1-b1ee-031d8fd53927 |  | textbox | Comb. main
text | f723e2fa-4282-5106-9439-97429fe48b74 |  | textbox | Inst. gauge
checkpoint-status |  |  | checkpoint | Pressure test 10 (n/a if not required)
text | b1a01f8a-4cbb-5119-b7cf-cb9a1d6a8b36 |  | textbox | %
text | ddfc147d-8a5f-5048-acf4-7cdfd9430aac |  | textbox | L/min
text | 0cbcd0fb-e33e-5afe-b76c-387a8fa9b32c |  | textbox | T/main no.1
text | 98645bc2-077e-565e-8288-555203b261ca |  | textbox | Inst. gauge
text | aa535122-1679-5b8c-aab0-f7d0717b7beb |  | textbox | T/main no.2
text | 0daa0fa0-0d6a-5c07-a454-71fe49ffb11e |  | textbox | Inst. gauge
text | 9ee2d591-adff-5451-acf6-c5f58d27c228 |  | textbox | Comb. main
text | 8e953fb7-0ea7-56c6-9765-dfc83857e863 |  | textbox | Inst. gauge
checkpoint-group |  |  | section | Pressure Tests (psi)
checkpoint-status |  |  | checkpoint | Pressure test 1 (n/a if not required)
text | f75fbf69-f587-5ca0-9afb-0ca8805e6f0c |  | textbox | %
text | cbfcb7c6-abd6-5a16-b7c0-781afb5d4e66 |  | textbox | L/min
text | ed5a8fd8-209e-5588-8e3b-58ede890502d |  | textbox | Diesel disch.
text | b13dd836-e5bb-50f0-988f-3f38ea32aa0e |  | textbox | Diesel suction
text | 408530ff-4f7f-5454-88e4-a8dc261c00ec |  | textbox | Inst. gauge
text | 0d840b40-74cf-5018-bddb-fd82b226f532 |  | textbox | Elect. disch
text | 716bdf7d-ae67-5cb3-bab9-ce49eab29caf |  | textbox | Elect. suction
text | e5f9cff0-c455-581a-84d7-0ecdb5068412 |  | textbox | Inst. gauge
checkpoint-status |  |  | checkpoint | Pressure test 2(n/a if not required)
text | 78b6f3a3-2407-54aa-ad82-f2525cb067f1 |  | textbox | %
text | c8db2188-c544-5150-af27-47802d2496e6 |  | textbox | L/min
text | 631b5d44-9436-54bb-985a-686887e29b42 |  | textbox | Diesel disch.
text | f12c7995-1219-5506-a649-180aab2be8f3 |  | textbox | Diesel suction
text | 32aead7e-5e8b-507d-b5a5-7234fd5b197d |  | textbox | Inst. gauge
text | 1a085204-d01c-5b27-9b30-379dec6483bf |  | textbox | Elect. disch
text | fc3223d2-df9d-5e72-972e-42965a14bf83 |  | textbox | Elect. suction
text | c58cf55a-c74a-556b-9a68-3d2d333f49b2 |  | textbox | Inst. gauge
checkpoint-status |  |  | checkpoint | Pressure test 3 (n/a if not required)
text | 79f3c8f0-411a-572f-b912-b4e0c6c5fc6f |  | textbox | %
text | d1ec9990-a6ce-588b-8ca0-19dfb1c9bd0b |  | textbox | L/min
text | 4bcdbdff-7126-502a-bfb4-b8e55949bd48 |  | textbox | Diesel disch.
text | 77046264-15d9-5fc0-b5ea-f2b0f7173463 |  | textbox | Diesel suction
text | f1c6be28-e123-5865-bf2a-57d48a8747f6 |  | textbox | Inst. gauge
text | 3f419ab5-5c04-5051-ae54-508005b192a0 |  | textbox | Elect. disch
text | f3cc80a2-fbe2-5314-8d99-4a63b4159f55 |  | textbox | Elect. suction
text | 476d5663-7995-52e3-83b7-2f751bb09e11 |  | textbox | Inst. gauge
checkpoint-status |  |  | checkpoint | Pressure test 4 (n/a if not required)
text | a44a4d32-b1f0-5e9d-b696-0e6b7f1db417 |  | textbox | %
text | d9bb2b69-0f88-5abd-895f-9ec74ba8d698 |  | textbox | L/min
text | e771ca7a-f088-52d9-a9cd-1ce9a7524ecd |  | textbox | Diesel disch.
text | b3e8d850-615d-5202-bd84-ceedfd7626ef |  | textbox | Diesel suction
text | 98ac3888-2e0f-5b4d-afe6-5822f48d4133 |  | textbox | Inst. gauge
text | 3a4dbf25-77a3-5fb7-a2cf-d520f9bf940d |  | textbox | Elect. disch
text | b9dfd8b1-5e47-54d5-88c1-0970ca9a70e9 |  | textbox | Elect. suction
text | 6fa51eb3-0130-5ff8-a6e2-3f11ba0ccb29 |  | textbox | Inst. gauge
checkpoint-status |  |  | checkpoint | Pressure test 5 (n/a if not required)
text | b5b86807-695d-5eb2-bb65-8718a3a24f9a |  | textbox | %
text | 03cbf665-fdb4-5eb4-9092-d2bd8c6a6b1e |  | textbox | L/min
text | c5761de0-4143-5f0b-b6f0-272366cc15df |  | textbox | Diesel disch.
text | b961acb8-9ca4-5033-980e-6a1f29da85d9 |  | textbox | Diesel suction
text | 1e16c397-54b3-5ed7-9aff-29f2c2df76d7 |  | textbox | Inst. gauge
text | e3feb89e-5709-5b7c-84d2-9d6acf5523a6 |  | textbox | Elect. disch
text | b4e55491-18bf-5ac8-b2e3-5480e98697ae |  | textbox | Elect. suction
text | 289889f3-ded1-51c1-bf5f-0fe74c743f74 |  | textbox | Inst. gauge
checkpoint-status |  |  | checkpoint | Pressure test 6 (n/a if not required)
text | de528aa6-9171-586c-a3d2-803cb289ff25 |  | textbox | %
text | 00697b1c-4b11-5a27-8c13-89f52fce3f64 |  | textbox | L/min
text | 711a29d8-3340-5dc6-b5a6-352e14e3541d |  | textbox | Diesel disch.
text | f0534485-6ef9-522e-95a0-39fe34912ba9 |  | textbox | Diesel suction
text | bcf14a6e-7422-5063-ac28-bac04daa9b4d |  | textbox | Inst. gauge
text | 8a861030-dbe2-5122-be18-cde7dfec8aa4 |  | textbox | Elect. disch
text | d46c2a7e-49ef-5a99-ad91-9420baedde3a |  | textbox | Elect. suction
text | b6afd21f-3239-5d9a-af4e-21c82d614990 |  | textbox | Inst. gauge
checkpoint-status |  |  | checkpoint | Pressure test 7 (n/a if not required)
text | e737326a-f709-5f33-a735-d9ad5c7e93fa |  | textbox | %
text | e40d8a24-8613-585d-aacb-8b766d2be417 |  | textbox | L/min
text | d81fda27-00c4-5074-95f1-28f94e05b9e1 |  | textbox | Diesel disch.
text | c18c5ea0-176d-5f65-bbaa-3933e1a012b1 |  | textbox | Diesel suction
text | 04f6a693-d939-5d2d-8cdd-425b78df9742 |  | textbox | Inst. gauge
text | 7a4c3798-0df0-567b-8e50-847d7d83167c |  | textbox | Elect. disch
text | 9bf76150-1042-5cfc-9073-60add1979038 |  | textbox | Elect. suction
text | c7b3c72b-a8b1-5e2a-beae-81baf178d1f5 |  | textbox | Inst. gauge
checkpoint-status |  |  | checkpoint | Pressure test 8 (n/a if not required)
text | d3cfe3ec-9510-5b08-9749-95c01d46931d |  | textbox | %
text | 31b1bac6-179b-54cc-abbb-69281e799600 |  | textbox | L/min
text | b7938a24-3e6f-5e75-a177-0e207416f1fe |  | textbox | Diesel disch.
text | 87644ac9-8481-5aca-8fc0-9f46888a0a9e |  | textbox | Diesel suction
text | a93d873c-25ff-5d65-82a3-686bd6e1be78 |  | textbox | Inst. gauge
text | ac16a991-5440-551f-b91c-5d6c0ea1debf |  | textbox | Elect. disch
text | 9ee7ab6e-33ab-545f-8b26-69cef546917b |  | textbox | Elect. suction
text | 8fa952fa-7f31-543d-b5bd-803ebffd4be3 |  | textbox | Inst. gauge
checkpoint-status |  |  | checkpoint | Pressure test 9 (n/a if not required)
text | 1dc2369f-023d-5d7a-9826-6d4c3a7b05a4 |  | textbox | %
text | d3e4ecc2-6d14-51f3-bb70-30f8b27d3b8d |  | textbox | L/min
text | 4ea5adcc-f65b-58f3-9b28-ebca5883bd9d |  | textbox | Diesel disch.
text | d3b912f5-02ad-5846-9b46-92fe265e5ef1 |  | textbox | Diesel suction
text | 955b192e-9df9-5716-beaf-cb803b97471d |  | textbox | Inst. gauge
text | aa323947-5f3f-5e26-8fb3-b8564c3730af |  | textbox | Elect. disch
text | ef337d15-a52f-50c0-824b-dadfcd76bdf0 |  | textbox | Elect. suction
text | 227c0493-8de3-5025-b87f-f024aa916b81 |  | textbox | Inst. gauge
checkpoint-status |  |  | checkpoint | Pressure test 10 (n/a if not required)
text | ce884662-eaad-5d08-8efe-91b94407886b |  | textbox | %
text | 08fcdc06-2a1c-59e8-bcd3-783744f08f3d |  | textbox | L/min
text | 60c6b201-9d3c-5d59-b013-4cf5993fc249 |  | textbox | Diesel disch.
text | cfd0e2ec-157b-5906-9004-3e0a37b93948 |  | textbox | Diesel suction
text | 465354a5-307b-5f30-bdc0-858649b8ecab |  | textbox | Inst. gauge
text | c7606c1f-86a6-55e5-bc9a-f95374b4008c |  | textbox | Elect. disch
text | 79277978-0c78-5109-84b3-de39642f9b81 |  | textbox | Elect. suction
text | c70e9c68-227d-5442-8dfc-779f4cf1ca44 |  | textbox | Inst. gauge
checkpoint-group |  |  | section | Sign-Off
checkpoint-status |  |  | checkpoint | Work(s) completed to specification/drawings & Area left clean/tidy - Builder final signature to be attached below if applicable
checklist-sectioned |  |  | checklist | ENT-016 - Fire Extinguishers |  |  |  |  | Yes | ENT-016 - Fire Extinguishers | 5d8ae071-9eea-48fc-888e-b7b7606ccf4c
checkpoint-group |  |  | section | Pre-Start
checkpoint-status |  |  | checkpoint | Specification reference checked
label | b967dcc4-a9b9-5543-be79-d543cc0486a4 |  | note | Specification Ref: AS:2444, AS:2941 and drawing
text | 417e315f-ae78-5142-977f-0eed5a824a12 |  | textbox | drawing reference
checkpoint-group |  |  | section | Installation
checkpoint-status |  |  | checkpoint | Secure cabinet
checkpoint-status |  |  | checkpoint | Extinguishers installed
checkpoint-status |  |  | checkpoint | Signage to meet code compliance
checkpoint-status |  |  | checkpoint | Hangers location and spacing
checkpoint-status |  |  | checkpoint | Fire blankets
checkpoint-group |  |  | section | Sign-Off
checkpoint-status |  |  | checkpoint | Work(s) completed to specification/drawings & Area left clean/tidy - Builder final signature to be attached below if applicable
checklist-sectioned |  |  | checklist | ENT-014 - Site Works Completion Summary (Fire Electrical) |  |  |  |  | Yes | ENT-014 - Site Works Completion Summary (Fire Electrical) | 8e38424e-79d6-4ebd-8750-87e363493a13
checkpoint-group |  |  | section | Completion Summary
checkpoint-status |  |  | checkpoint | Electrical Rough in (ENT-013)
checkpoint-status |  |  | checkpoint | Electrical Fit off (ENT-013)
text | 79bdcfea-48d9-5be4-b23f-959c3c8b9949 |  | textbox | Date completed
text | eb990a08-4de3-57d3-a32e-81def1bb554e |  | textbox | Level and/or area
checkpoint-status |  |  | checkpoint | Electrical Rough in (ENT-013)
checkpoint-status |  |  | checkpoint | Electrical Fit off (ENT-013)
text | be814ddf-e946-5a7e-9ec7-ccea5eef2acc |  | textbox | Date completed
text | e491b5ce-57f5-5363-8574-6015affb839b |  | textbox | Level and/or area
checkpoint-status |  |  | checkpoint | Electrical Rough in (ENT-013)
checkpoint-status |  |  | checkpoint | Electrical Fit off (ENT-013)
text | 3e51d38f-e7d4-59f3-8be0-c67ee523ac3e |  | textbox | Date completed
text | ff4744fd-6d0e-5f64-bfcd-d1538be5d42d |  | textbox | Level and/or area
checkpoint-status |  |  | checkpoint | Electrical Rough in (ENT-013)
checkpoint-status |  |  | checkpoint | Electrical Fit off (ENT-013)
text | a3d08e87-cf2c-54e4-bb94-ca344962d04a |  | textbox | Date completed
text | 3ddcdf36-41bf-5bf9-b2fd-1e75fb61a569 |  | textbox | Level and/or area
checkpoint-status |  |  | checkpoint | Electrical Rough in (ENT-013)
checkpoint-status |  |  | checkpoint | Electrical Fit off (ENT-013)
text | ad918195-4ab9-5eae-b7d1-4839dfd701f3 |  | textbox | Date completed
text | f3ec961c-7e82-5300-a51d-6886f7489ec4 |  | textbox | Level and/or area
checkpoint-status |  |  | checkpoint | Electrical Rough in (ENT-013)
checkpoint-status |  |  | checkpoint | Electrical Fit off (ENT-013)
text | 8c558c41-7d1f-5519-8bd4-08d313c8a4ce |  | textbox | Date completed
text | 74bef28c-7578-5fa8-aa61-c00817c0b871 |  | textbox | Level and/or area
checkpoint-status |  |  | checkpoint | Electrical Rough in (ENT-013)
checkpoint-status |  |  | checkpoint | Electrical Fit off (ENT-013)
text | be8cbef6-eda2-5101-80d4-f6555b6fc6a2 |  | textbox | Date completed
text | 0be3bdc2-e67a-5f00-9c77-a0938206fe37 |  | textbox | Level and/or area
checkpoint-status |  |  | checkpoint | Electrical Rough in (ENT-013)
checkpoint-status |  |  | checkpoint | Electrical Fit off (ENT-013)
text | c8f7477a-9785-5b68-849a-a6e216396b0e |  | textbox | Date completed
text | f2043e18-b1e6-5abd-ac57-33cda1441386 |  | textbox | Level and/or area
checkpoint-status |  |  | checkpoint | Electrical Rough in (ENT-013)
checkpoint-status |  |  | checkpoint | Electrical Fit off (ENT-013)
text | 07748513-39c7-5cc0-a82f-0a1a747ad437 |  | textbox | Date completed
text | e35c7b69-23b3-50db-8cad-eb477ff06156 |  | textbox | Level and/or area
checkpoint-status |  |  | checkpoint | Electrical Rough in (ENT-013)
checkpoint-status |  |  | checkpoint | Electrical Fit off (ENT-013)
text | a04bc985-53ae-5820-809a-71dcb10bb172 |  | textbox | Date completed
text | 9e4f1a12-094d-5fdb-ac21-d3da7ed8299d |  | textbox | Level and/or area
checkpoint-status |  |  | checkpoint | Electrical Rough in (ENT-013)
checkpoint-status |  |  | checkpoint | Electrical Fit off (ENT-013)
text | 3890aea3-0047-5d00-ba47-1fa0d62ac070 |  | textbox | Date completed
text | aa74b2da-4d2d-5bf4-ad06-943cc5b9de3e |  | textbox | Level and/or area
checkpoint-status |  |  | checkpoint | Electrical Rough in (ENT-013)
checkpoint-status |  |  | checkpoint | Electrical Fit off (ENT-013)
text | 91a68e0d-8546-5703-a50f-0e96f9db4fa1 |  | textbox | Date completed
text | 489e3111-e1b2-597f-8ace-9eefbf18961c |  | textbox | Level and/or area
checkpoint-status |  |  | checkpoint | Electrical Rough in (ENT-013)
checkpoint-status |  |  | checkpoint | Electrical Fit off (ENT-013)
text | e2b96be1-a4ea-50e9-aaf6-886d5c2fdab1 |  | textbox | Date completed
text | 6898f5ed-7b57-58f6-bb75-3402a53082d8 |  | textbox | Level and/or area
checkpoint-status |  |  | checkpoint | Electrical Rough in (ENT-013)
checkpoint-status |  |  | checkpoint | Electrical Fit off (ENT-013)
checkpoint-group |  |  | section | Sign-Off
checkpoint-status |  |  | checkpoint | Inspected / Certified
text | 391b7dac-8707-5d83-b567-cfad46c04f01 |  | textbox | Date completed
checkpoint-status |  |  | checkpoint | Sign-Off Records completed
label | 97986ce0-2216-5c61-82da-42eb698a253d |  | note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
button | f5a4b217-016b-5784-b06e-d9fb4254fd2d |  | button | Entire Fire Signature Sign-Off added below | Yes,No
checklist-sectioned |  |  | checklist | ENT-001 - Inspection and Test Plan Schedule |  |  |  |  | Yes | ENT-001 - Inspection and Test Plan Schedule | 9bb3ebf7-b237-493e-90c3-23e2c587b913
checkpoint-group |  |  | section | Design
checkpoint-status |  |  | checkpoint | Hydraulic Calculations
label | 034c351a-92e6-57ec-9f83-177f3ba1407d |  | note | Works By: Entire
label | b1d6020d-b0d1-52c7-a2bb-a748942a2e45 |  | note | Entire: Review/Approve & Submitted
label | 15d09fcf-2e75-5749-aaa1-0d5a7b36f637 |  | note | Consulting Engineer: Review/Approve
label | 859f8e6d-b1f9-5e74-9f70-965eacd4255c |  | note | Builder: Review/Approve
label | 5b0ba054-0d3b-5e5e-8742-008670e39ebe |  | note | Acceptance Criteria: AS:2118
checkpoint-status |  |  | checkpoint | Gaseous System Design
label | c0ead5fc-d7ea-5176-ba72-50d8576b58ea |  | note | Works By: Entire
label | 2d8966f6-b75f-5541-b6b4-66dcd9c26e69 |  | note | Entire: Review/Approve & Submitted
label | b0ccabd2-ff64-5d0d-8e42-8c4a01e47cfa |  | note | Consulting Engineer: Review/Approve
label | 24df5775-606e-52c5-ab64-8fdd4da8d32a |  | note | Builder: Review/Approve
label | 6f878093-e6bf-5dae-9521-2cf8071ba55c |  | note | Acceptance Criteria: AS:14520
checkpoint-status |  |  | checkpoint | Fire Electrical
label | 0a9f1261-9d21-56b1-96cc-98e5820ba5f7 |  | note | Entire: Review/Approve & Submitted
label | 42615961-85f7-5c09-b1a1-11df617155e6 |  | note | Consulting Engineer: Review/Approve
label | 500188b8-22e3-5eb3-a765-98ff26a06141 |  | note | Builder: Review/Approve
label | cec17a53-6b41-5bed-9234-fb2cc8ca16e5 |  | note | Acceptance Criteria: AS:1670, AS:1668, AS:3000
checkpoint-group |  |  | section | Drafting
checkpoint-status |  |  | checkpoint | Drafting sprinkler
label | 0e0f444e-4b8a-5d8c-82a3-423eec605b56 |  | note | Works By: Entire
label | fcbcfcf1-0ff3-514e-b0e8-19b282f33a3d |  | note | Entire: Review/Approve & Submitted
label | cf417959-9855-50d8-825d-f9673488dc51 |  | note | Consulting Engineer: Review/Approve
label | 5fb8e404-d371-519e-a3f7-bf4327206f37 |  | note | Builder: Review/Approve
label | bd93f704-afe6-56c7-9053-c0b14c65dc52 |  | note | Statutory Authority: Inspect & Review/Approve
label | bb077968-b047-5491-a166-78bfecfbeff5 |  | note | Acceptance Criteria: AS:2419, AS:2441
label | a12d2fc1-6405-5d53-85d5-9523374bff23 |  | note | QC Form: Drawing Register
checkpoint-status |  |  | checkpoint | Drafting Gaseous Suppression
label | 3482474d-3e26-5946-a1cf-fae5b18e51e5 |  | note | Works By: Entire
label | b90735fa-ab75-5686-b6dd-84cfa7dda1f7 |  | note | Entire: Review/Approve & Submitted
label | 40263072-4bde-5834-97fe-4e9f4e0b7665 |  | note | Consulting Engineer: Review/Approve
label | 22991bb7-6845-52e0-ac86-853ba4ec3db5 |  | note | Builder: Review/Approve
label | 9be0dd06-fd10-5fe5-9c31-e97b1dadd279 |  | note | Statutory Authority: Inspect & Review/Approve
label | bc48b9b4-3204-5618-b310-f5d53dac299b |  | note | Acceptance Criteria: AS:4214
label | c431928e-b3f0-52d0-a3eb-8e87af43534f |  | note | QC Form: Drawing Register
checkpoint-status |  |  | checkpoint | Drafting Fire Electrical
label | 4d898a59-3d18-5b09-bc6d-beb0956be21b |  | note | Works By: Entire
label | f7696c15-4ab3-5bc2-a4c7-621e8be45750 |  | note | Entire: Review/Approve & Submitted
label | e6eb4788-8c32-5fce-a554-00b4dc9e0b91 |  | note | Consulting Engineer: Review/Approve
label | df0aa9be-1f9c-5423-bf93-661114b92a6e |  | note | Builder: Review/Approve
label | 0a60bd98-446c-57c0-bd9b-7537ccdecaab |  | note | Statutory Authority: Inspect & Review/Approve
label | 47d1f437-7d58-50e7-af96-80cf352cc9c1 |  | note | Acceptance Criteria: AS:1670, AS:1668, AS:3000
label | 8453aa5a-3ea8-582e-8464-ec28bf874c0c |  | note | QC Form: Drawing Register
checkpoint-group |  |  | section | Samples
checkpoint-status |  |  | checkpoint | Sample Tech Data
label | caa0ddc0-7304-5cce-ad58-ac9b4612ad37 |  | note | Works By: Entire
label | f33142da-b028-5e4d-a2cc-c9438115be89 |  | note | Entire: Review/Approve & Submitted
label | 663bd5a8-2607-5045-b77c-2b65c5d9757a |  | note | Consulting Engineer: Review/Approve
label | dfc5ae44-b798-540d-a209-c680ce42d553 |  | note | Builder: Review/Approve
label | 9072f04c-d4d3-5946-9dd5-692ec3b3249e |  | note | Acceptance Criteria: Specification
label | 4ceb5e73-7e90-5d15-a3ea-2d03a0c27474 |  | note | QC Form: Sample Register
checkpoint-group |  |  | section | Off-Site Manufacture
checkpoint-status |  |  | checkpoint | Fire pumps and tanks
label | a7eccca7-7a3d-525c-ba32-141239b1411b |  | note | Works By: Supplier
label | 7d9a287c-599a-5837-a16a-6f6786cff58a |  | note | Entire: Review/Approve & Submitted
label | c9b3879d-f1c2-5c2f-ad19-b905f92e010b |  | note | Consulting Engineer: Review/Approve
label | 6f02a0ea-eb35-5c5c-ad4e-a70a21ca98c8 |  | note | Builder: Review/Approve
label | e75a2508-6edf-52dc-a9cb-8080d6acba56 |  | note | Acceptance Criteria: AS:2941
checkpoint-status |  |  | checkpoint | Fire Indicator Panel
label | 9c07fb88-42fe-5458-be19-b70b469d72cd |  | note | Works By: Supplier
label | 7394ec80-92d3-5415-98cb-81fc6c69b7a4 |  | note | Entire: Review/Approve & Submitted
label | bfff1a6a-99a4-5bb2-8fdb-592788514a57 |  | note | Consulting Engineer: Review/Approve
label | 558254d4-e2e0-5403-90fc-305fc251fedf |  | note | Builder: Review/Approve
label | 96cc18e0-83cf-5ce2-aa8e-ef379c1b6bfe |  | note | Acceptance Criteria: AS:1670, AS3000
checkpoint-group |  |  | section | Incoming Inspection
checkpoint-status |  |  | checkpoint | Sprinkler pipe
label | 73bb95e4-2a5f-556a-9cf9-cad8d99f2717 |  | note | Works By: Entire
label | 7a4f32ad-4a6b-5629-99a0-bac9d4b5ff9d |  | note | Entire: Review/Approve & Submitted
label | 759b13ef-6bd0-5b26-a232-118f53880bac |  | note | Consulting Engineer: Review/Approve
label | 61f86528-ae54-58dc-bd53-d73d5bf79b1f |  | note | Builder: Review/Approve
label | 1a58a60c-4e31-5ab7-836b-1f8ec8ac76f4 |  | note | Acceptance Criteria: AS:2118
label | cd6608e6-8386-5852-967e-9a3b0f5705be |  | note | QC Form: ENT-006 Hydrants and hosereels
checkpoint-status |  |  | checkpoint | Fire pumps and tanks
label | 79156df3-d19b-5401-8522-d7835f9f2e96 |  | note | Works By: Entire
label | b501e25f-f42b-5026-bae5-78845fb4f6a4 |  | note | Entire: Review/Approve & Submitted
label | 513e7a38-5df9-53d7-8770-f0d93d2873e6 |  | note | Consulting Engineer: Review/Approve
label | a7748351-7ac6-591b-a558-0c1968751cfb |  | note | Builder: Review/Approve
label | 6f140b37-8350-5c5c-bedc-b39d7258abe5 |  | note | Acceptance Criteria: AS:2941
label | 53381fc0-7b2c-5847-a9d4-c3aa4090ad93 |  | note
checkpoint-status |  |  | checkpoint | Gaseous Fire Suppression
label | e0818e9f-8065-542a-b848-b9e334463869 |  | note | Works By: Entire
label | 56de8aaf-b733-5f70-a53a-040e00eb3a69 |  | note | Entire: Review/Approve & Submitted
label | 595a441f-25c0-5ba3-968f-3bf1a6b65a4c |  | note | Consulting Engineer: Review/Approve
label | 3f1ceeaf-60b1-53b0-8bc6-975843f8a1cb |  | note | Builder: Review/Approve
label | a1c9b060-96c2-50b5-8add-369512fe9d62 |  | note | Acceptance Criteria: AS:4214
label | 3ef35d4f-03c0-573c-a1d3-9f61b056584c |  | note | QC Form: ENT-002 - Gaseous Suppression
checkpoint-status |  |  | checkpoint | Fire Electrical
label | 914545ff-a1dd-5a3b-ac1d-f7165cf34787 |  | note | Works By: Subcontractor
label | edb891d9-61a7-595a-9108-c16e72913365 |  | note | Entire: Review/Approve & Submitted
label | d9226516-e938-5a7a-96f2-2209c943d7dd |  | note | Consulting Engineer: Review/Approve
label | 0e8c68d0-9674-5983-a9a9-f61050c746fd |  | note | Builder: Review/Approve
label | 47192c1e-a7ec-5f14-b8d1-9c1be4614486 |  | note | Acceptance Criteria: AS:1670, AS:1668, AS:3000
label | 158c29ab-e92c-5741-8de3-0529e4e02200 |  | note | QC Form: ENT-013 - Fire Detection
checkpoint-group |  |  | section | Installation
checkpoint-status |  |  | checkpoint | Fire Hydrant / Hosereels - Rough-In & Fit-Off
label | c5e5c04e-c0d7-546f-aa3d-588076aefbb4 |  | note | Works By: Entire
label | 1c716f07-c216-594b-b28d-d18c86421c6b |  | note | Entire: Review/Approve & Submitted
label | d9e3200c-5c57-5f49-a8da-33394e43d22b |  | note | Consulting Engineer: Review/Approve
label | a73d238f-ec63-5081-bdfa-7d79f4b75297 |  | note | Builder: Review/Approve
label | 9cc2d9e3-8cc3-51f3-9b06-85e346339cd8 |  | note | Statutory Authority: Inspect & Review/Approve
label | 741aaa4f-b9ba-524c-b0d5-b56c3ebd372a |  | note | Acceptance Criteria: AS:2419, AS:2441
label | 084709f6-fbea-56c0-8b3c-92a2bbd9d749 |  | note | QC Form: ENT-004 - Sprinkler rough in and fit off
checkpoint-status |  |  | checkpoint | Gaseous Fire Suppression - Rough-In & Fit-Off
label | 3f41dc68-f04d-5bf9-baac-d5101bfb8e06 |  | note | Works By: Entire
label | ea72aef3-a106-5a55-92aa-c84b067d224e |  | note | Entire: Review/Approve & Submitted
label | b1ce5700-f605-5f52-893d-67f4094ba658 |  | note | Consulting Engineer: Review/Approve
label | 0adc4caf-7ac2-5544-8dd1-5b7e775af2d7 |  | note | Builder: Review/Approve
label | 610f123a-d268-52cd-bba9-7e9fa02ae7c3 |  | note | Statutory Authority: Inspect & Review/Approve
label | 410d4ed1-f1cc-5c8c-9540-602fbdc32b5a |  | note | Acceptance Criteria: AS:4214
label | 4965ab40-844c-527a-bb54-f1792989e237 |  | note | QC Form: ENT-002 - Gaseous Suppression
checkpoint-status |  |  | checkpoint | Fire Electrical - Rough-In & Fit-Off
label | 72812943-7804-5581-8241-96c837aef056 |  | note | Works By: Subcontractor
label | 2d6f7862-126a-5ed5-b688-ee5f1af1c57d |  | note | Entire: Review/Approve & Submitted
label | 05ab7a26-52ce-58d4-abfd-c0196d04a33d |  | note | Consulting Engineer: Review/Approve
label | 1cdc231e-f0a3-581f-8875-e0590c7ad042 |  | note | Builder: Review/Approve
label | 0f509c9d-1d02-551e-86e8-ec6ec47e87d1 |  | note | Statutory Authority: Inspect & Review/Approve
label | 45dc9bae-d861-5109-912c-3d180d9f3bbb |  | note | Acceptance Criteria: AS:1670, AS:1668, AS:3000
label | 5dace8cd-3d79-5264-9d74-6afe6dbed991 |  | note | QC Form: ENT-013 - Fire Detection
checkpoint-group |  |  | section | Commissioning
checkpoint-status |  |  | checkpoint | Fire Hydrant / Hosereels
label | 99a20f76-9116-5660-b312-ff1120a4d692 |  | note | Works By: Entire
label | 7e70dd1a-5832-5ffd-ba63-e83307a8cbc9 |  | note | Entire: Review/Approve & Submitted
label | ca6e8878-5067-5d59-97b8-cfd9944d6f6c |  | note | Consulting Engineer: Review/Approve
label | a169498d-a8c3-5313-b775-8b233a4ce7d5 |  | note | Builder: Review/Approve
label | 5413443a-908f-5c1b-98e4-1ad982b63847 |  | note | Statutory Authority: Inspect & Review/Approve
label | a913ab60-582c-5b7f-8996-b0274718f705 |  | note | Acceptance Criteria: AS:2419, AS:2441
label | 7803b8b0-7c47-5ffe-9f29-48211c3b41e5 |  | note | QC Form: ENT-006 - Hydrants & Hosereels
checkpoint-status |  |  | checkpoint | Gaseous Fire Suppression
label | b559a6ff-a761-5e0c-afaf-2c192d4b1e64 |  | note | Works By: Entire
label | 932be757-fbf0-5372-b057-be0bda42aa24 |  | note | Entire: Review/Approve & Submitted
label | fccd75e5-28c6-5ef9-8902-141e905709f1 |  | note | Consulting Engineer: Review/Approve
label | ab927211-b7e0-55be-804c-6f1c03bdc897 |  | note | Builder: Review/Approve
label | 004bf572-8dd0-505d-8f6d-6e9d73d8d6b1 |  | note | Statutory Authority: Inspect & Review/Approve
label | b4bc8d54-b2eb-591d-9786-cb4891ae958e |  | note | Acceptance Criteria: AS:4214
label | a96251b8-ed3e-5246-8040-95ac7489357b |  | note | QC Form: ENT-002 - Gaseous Suppression
checkpoint-status |  |  | checkpoint | Fire Electrical
label | 04591ca8-0bbf-50de-a0ff-df2a386c005c |  | note | Works By: Subcontractor
label | cb6bc9d0-749a-5b1b-93f5-4605e2bed88a |  | note | Entire: Review/Approve & Submitted
label | 1d7539b1-17c3-507b-9723-b3fcf430fc48 |  | note | Consulting Engineer: Review/Approve
label | 1ff2b1da-c655-5223-bd66-6c35f297156e |  | note | Builder: Review/Approve
label | a7088d12-0975-5640-8def-1f78888a34d4 |  | note | Statutory Authority: Inspect & Review/Approve
label | 54515e61-9262-5677-8d4a-a2a202b31a7f |  | note | Acceptance Criteria: AS:1670
label | 8aa4d57c-00cf-599c-8703-2c8d2d5aead9 |  | note | QC Form: ENT-015
checkpoint-status |  |  | checkpoint | Interface Checks - Mechanical / Fire
label | d04b39af-f604-5d15-b4f8-604c31f23c9a |  | note | Works By: Entire
label | 1c903a34-93e9-5f1c-99a4-5d6a3d10755e |  | note | Entire: Review/Approve & Submitted
label | 00d5cf6e-d9a0-58f6-8ddd-97349994b113 |  | note | Consulting Engineer: Review/Approve
label | bbe28b38-08b5-526b-b8dc-d186f9bec601 |  | note | Builder: Review/Approve
label | 12560e7f-9484-5647-b038-1b31d46029b3 |  | note | Statutory Authority: Inspect & Review/Approve
label | 658c36e5-a0a4-5705-b888-991074701243 |  | note | Acceptance Criteria: AS:1670, AS:1668
label | bb6e9ce0-f15e-52be-9a4d-34dfc93ec452 |  | note | QC Form: ENT-015
checkpoint-status |  |  | checkpoint | As-Installed Drawings and - Manuals (inc. Test Data)
label | 5bbe42e7-9118-5737-9d5f-79ac773715dd |  | note | Works By: Entire
label | 166a01c5-5df5-5cfd-a268-cdded66b71fa |  | note | Entire: Submitted
label | a4a2740c-d6ac-5c63-b7af-fc85c82cc3b8 |  | note | Consulting Engineer: Inspected & Review/Approve
label | 6813140a-5b75-5987-8385-be8532a014bd |  | note | Builder: Inspected & Review/Approve
checkpoint-status |  |  | checkpoint | Final Defects List
label | b90c5b42-78bc-5c90-842b-6431e4b089fe |  | note | Works By: Entire
label | 20f289d0-3706-5466-b014-4ba18d9db534 |  | note | Entire: Inspected
label | 4b9dcc52-6876-5a49-9b9e-1d70e9ddc952 |  | note | Consulting Engineer: Inspected & Review/Approve
label | 401642ac-8286-591a-97c6-168829055b05 |  | note | Builder: Inspected & Review/Approve
checkpoint-group |  |  | section | Defects Liability & Warranty
checkpoint-status |  |  | checkpoint | Entire to Provide Servicing information for Defects Liability Period
label | e1b33b21-2e07-5e98-9822-180c7b7456fe |  | note | Works By: Entire Service Department
label | c8f6c6f2-968b-5e27-8cd8-b8fd321cf267 |  | note | Entire: Provide
label | c3b36d08-f391-5a6b-8d82-8162eeb9e663 |  | note | Builder: Review/Approve
label | add2f777-e8ac-565e-baa2-fd9a904ae7cd |  | note | Acceptance Criteria: AS:1851.3
checkpoint-status |  |  | checkpoint | Entire to Provide Warranty Information
label | 224e72a3-54e8-59d8-9f44-810c2eb6c2fd |  | note | Works By: Entire Service Department
label | 4c5094f4-818e-555c-b594-59cfe3aadd30 |  | note | Entire: Provide
label | 17d3e7fd-8c93-563e-9fb3-7f031931df10 |  | note | Builder: Review/Approve
label | f0e83b40-6a11-5ac0-831a-fa9ddf6a2c94 |  | note | Acceptance Criteria: AS:1851.4
checklist-sectioned |  |  | checklist | ENT-004 - Sprinkler rough in and fit off |  |  |  |  | Yes | ENT-004 - Sprinkler rough in and fit off | a576f23b-e122-4ed1-ae97-d0ba5f1f7119
checkpoint-group |  |  | section | Pre-Start
checkpoint-status |  |  | checkpoint | Specification reference checked
label | f3e67771-693f-585e-be11-6ac573c5d03d |  | note | Specification Ref: AS:2118 and drawing
checkpoint-status |  |  | checkpoint | Pipe + Fittings
label | 75aceae5-0508-5d16-9bfe-ca441f28782f |  | note | PASS if received in good condition - If not FAIL & Attach Photos/Comments below
checkpoint-status |  |  | checkpoint | Sprinklers
label | 8f39e20f-c75c-50dd-bda3-76ef5f193add |  | note | PASS if received in good condition - If not FAIL & Attach Photos/Comments below
checkpoint-group |  |  | section | Installation Rough-In
checkpoint-status |  |  | checkpoint | Mains & branches installed to drawing
checkpoint-status |  |  | checkpoint | Hangers Location
checkpoint-status |  |  | checkpoint | Concealed spaces sprinker heads installed
checkpoint-status |  |  | checkpoint | Outlets capped
label | 4b7131e0-19a1-52b5-9f02-bec495ba49de |  | note | Specification Ref: drawing
checkpoint-status |  |  | checkpoint | Pressure test carried out
label | 0071d9a9-ac25-557b-b917-ec5a828679cf |  | note | Specification Ref: ENT-009
checkpoint-status |  |  | checkpoint | Pentrations sealed
checkpoint-group |  |  | section | Installation Fit-Off
checkpoint-status |  |  | checkpoint | Sprinkler heads fitted to final locations as per coordinated RCP
checkpoint-status |  |  | checkpoint | Pressure test fit off
label | e33cde4f-02ea-5304-8fdf-75eb46fb04f1 |  | note | Specification Ref: ENT-009
checkpoint-group |  |  | section | Sign-Off
checkpoint-status |  |  | checkpoint | Inspected by Independent Certifier - Signature attached below as applicable
label | bdac02be-bec1-55f2-9b3a-efed37b2ce1f |  | note | Specification Ref: AS:2419, AS:2414
checklist-flat |  |  | checklist | ENT-011 - Action Request Form |  |  |  |  | Yes | ENT-011 - Action Request Form | ad47c735-db5d-44dc-96e5-323003e01eb5
checkpoint-status |  |  | checkpoint | Action Request Details - Pass once entered
text | 90bf404b-0f33-5f2a-a63b-1bdbfc331c54 |  | textbox | Action Request Number
label | 779fc7e9-e496-5bc3-a5b2-2658e3a4e7c4 |  | note | This action request is a result of (Tick below)
boolean | a9f73e6f-6fb6-5654-86f1-ded2c9a826b3 |  | tickbox | Audit
boolean | e29da38a-8313-5742-a5b5-e79c573d5e45 |  | tickbox | Failure
boolean | da3e0c40-aecc-5adf-88a4-3ac15719ff9f |  | tickbox | Non-Conformance
boolean | a5623efb-fdf8-5fd6-9b5c-91c416531a22 |  | tickbox | Process Improvement Idea
boolean | a3efff37-13e9-5131-9f0e-4ff69fb91291 |  | tickbox | Customer Complaint
boolean | 4a3bdb1d-0561-58f0-ad4e-dc698022b50c |  | tickbox | Corrective/Preventative Action
checkpoint-status |  |  | checkpoint | Description of failure/Non Conformance/Improvement Idea/Customer Complaint
label | 041b7c66-df5a-5891-8c6f-32d113be8531 |  | note | Send to Quality Manager for allocation of number and passing to appropriate person for action
text | 80eb5321-f6b2-5c33-8b38-0c66bb9bc519 |  | textbox | Details
text | 7450d40f-e226-5fad-8b5c-5a6c04359729 |  | textbox | Reported By
text | 3314426d-8666-5520-b9db-87ff87d1c097 |  | textbox | Date
checkpoint-status |  |  | checkpoint | Investigate cause and list details
label | 54ebb01e-08d6-57a3-9919-a423caee02bb |  | note | State action when and if there is a deeper underlying issue or problem
text | f174dce9-6872-5fae-8d99-da2038c74fe2 |  | textbox | Details
text | 33fcfb3c-7c29-581c-bf8f-10df31f35069 |  | textbox | Assigned To
text | 7f8186d3-d934-5e66-97c6-dc847e2257d4 |  | textbox | Date of Completion
label | ad3498da-2a2c-573f-ae28-1d0d90c0e77d |  | note | Signature Sign-Off attached below
checkpoint-status |  |  | checkpoint | List details of deeper underlying issue and corrective action
label | 750fe04b-4c8a-554d-ac69-991d2a733683 |  | note | This section only applicable if above indicates the need
text | 381dc14a-661b-5ef2-89c5-46cf3eadcef3 |  | textbox | Details
text | 08ca72c6-c261-537f-b53f-3133e57d1855 |  | textbox | Assigned To
text | f12ee814-01c3-5ce6-b211-7d4d5083b732 |  | textbox | Date of Completion
label | a130f858-5c71-5118-a23d-3f05e88fc46e |  | note | Signature Sign-Off attached below
checkpoint-status |  |  | checkpoint | Verification/Follow-up
text | bbe4ea26-f38c-543f-bdb2-ffeaf2041c22 |  | textbox | Details
text | 03981bd2-b9e5-5056-889a-99cfd60e32f0 |  | textbox | Assigned To
text | e8e5c1c9-5c90-54ba-8517-5bf6fb8ba45d |  | textbox | Date of Completion
label | e2c20b64-5a8e-57a2-93b3-92c4c7783279 |  | note | Signature Sign-Off attached below
checkpoint-status |  |  | checkpoint | Sign-Off Records completed
label | 4fc5a325-e3a7-5831-9ab1-79fb20599bcb |  | note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
button | 7265228c-3498-57a8-a41d-3ca97cfd4ba0 |  | button | Entire Fire Quality Manager Signature Sign-Off added below | Yes,No
checklist-flat |  |  | checklist | ENT-005 Site works completion summary (sprinklers) |  |  |  |  | Yes | ENT-005 Site works completion summary (sprinklers) | bc06feb8-4801-4751-969c-3c6401d4b425
checkpoint-status |  |  | checkpoint | Drawing number
text | f9ac2b06-0164-51f2-b68d-5c794fa860fb |  | textbox | Sprinklers rough in (ENT-004) date completed
text | 80865116-616e-50e7-b518-6d8514c65ed4 |  | textbox | Sprinklers fit off (ENT-004) date completed
text | fd78485a-d5f5-51b9-a626-abfe53234dd5 |  | textbox | Sprinklers control valves (ENT-003) date completed
checkpoint-status |  |  | checkpoint | Drawing number
text | c9646406-6615-568d-a2f3-3ebaab118257 |  | textbox | Sprinklers rough in (ENT-004) date completed
text | a3d31c0c-d494-5686-9f5f-b1535352d88f |  | textbox | Sprinklers fit off (ENT-004) date completed
text | f36b005d-7622-5656-9a4c-ea705b329beb |  | textbox | Sprinklers control valves (ENT-003) date completed
checkpoint-status |  |  | checkpoint | Drawing number
text | 238100ad-1459-5d28-b84c-d37436b75ef1 |  | textbox | Sprinklers rough in (ENT-004) date completed
text | 1256a60a-9b3e-5043-a626-2d1fc0fd9444 |  | textbox | Sprinklers fit off (ENT-004) date completed
text | 6de2d954-5a6e-5de4-b14b-71ad5f12c9de |  | textbox | Sprinklers control valves (ENT-003) date completed
checkpoint-status |  |  | checkpoint | Drawing number
text | f3fce0a8-8f51-5155-a8c8-e8e224ec34e4 |  | textbox | Sprinklers rough in (ENT-004) date completed
text | 84d42f8b-02b0-5e6e-a5f0-1e4610dbd2b4 |  | textbox | Sprinklers fit off (ENT-004) date completed
text | b3997b0b-fad2-55f6-8334-5a66123598b2 |  | textbox | Sprinklers control valves (ENT-003) date completed
checkpoint-status |  |  | checkpoint | Drawing number
text | 8833a81d-9343-5faf-aa90-761d285970b5 |  | textbox | Sprinklers rough in (ENT-004) date completed
text | 7c501e33-a901-544e-90a5-7de24bf07786 |  | textbox | Sprinklers fit off (ENT-004) date completed
text | 02be7e30-a07e-54b7-b2a7-c3baf07ccc26 |  | textbox | Sprinklers control valves (ENT-003) date completed
checkpoint-status |  |  | checkpoint | Drawing number
text | 3def5ff1-a18b-5df0-9b11-d0614ef7168b |  | textbox | Sprinklers rough in (ENT-004) date completed
text | ca58778d-51ca-5832-b92a-df1bc77e5317 |  | textbox | Sprinklers fit off (ENT-004) date completed
text | f50e1bb0-7d55-5527-8577-67955eefedba |  | textbox | Sprinklers control valves (ENT-003) date completed
checkpoint-status |  |  | checkpoint | Drawing number
text | f9942671-399d-5380-989e-53510acdeafd |  | textbox | Sprinklers rough in (ENT-004) date completed
text | 411ef639-0380-5360-b212-065631221e9f |  | textbox | Sprinklers fit off (ENT-004) date completed
text | ac5788f1-21c2-54ab-8fd6-7e63006cc8ff |  | textbox | Sprinklers control valves (ENT-003) date completed
checkpoint-status |  |  | checkpoint | Work(s) completed to specification/drawings & Area left clean/tidy - Builder final signature to be attached below if applicable
checklist-sectioned |  |  | checklist | ENT-018 - Water mist installation |  |  |  |  | Yes | ENT-018 - Water mist installation | c2fa2a3e-1759-490c-b200-a44e18450f06
checkpoint-group |  |  | section | Pre-Start
checkpoint-status |  |  | checkpoint | Specification reference checked
label | 0b6a337d-bb24-5d1f-a5b0-5d3c8134e3ac |  | note | Specification Ref: AS:4587, AS:1530, AS:2419, AS:2414 and drawing
checkpoint-status |  |  | checkpoint | Pipe, Fittings
label | c88f9457-a3f1-5c5e-82f5-7c23b3ca702d |  | note | PASS if received in good condition - If not FAIL & Attach Photos/Comments below
checkpoint-status |  |  | checkpoint | Nozzles
label | 77f13f55-acd3-52c1-9f1b-84bce75a3072 |  | note | PASS if received in good condition - If not FAIL & Attach Photos/Comments below
checkpoint-group |  |  | section | Installation Rough-In
checkpoint-status |  |  | checkpoint | Mains, ranges & riser pipes
checkpoint-status |  |  | checkpoint | Hangers location & spacing
checkpoint-status |  |  | checkpoint | Manual and automatic isolation valves
checkpoint-status |  |  | checkpoint | Pressure test carried out
label | 2877c68d-ef20-5559-b695-91b165cc5faa |  | note | Specification Ref: ENT-009
text | 57b7dc7b-a258-55c3-956c-d0592cea5e5d |  | textbox | Test number
checkpoint-status |  |  | checkpoint | Penetrations sealed
checkpoint-group |  |  | section | Sign-Off
checkpoint-status |  |  | checkpoint | Inspected by Independent Certifier - Signature attached below as applicable
label | 4770fd58-e55f-552a-8182-5fef4d539bed |  | note | Specification Ref: AS:2419, AS:2414
checklist-sectioned |  |  | checklist | ENT-002 - Gaseous Suppression |  |  |  |  | Yes | ENT-002 - Gaseous Suppression | d05b6f43-7d4c-4eb6-8dd3-215b15974e29
checkpoint-group |  |  | section | Pre-Start
checkpoint-status |  |  | checkpoint | Specification reference checked
label | 2ec07d8a-03a5-5ccf-a4c4-1d03b034cf87 |  | note | Specification Ref: AS:2414
checkpoint-status |  |  | checkpoint | Pipe, Fittings, Manifolds, Hoses, Nozzles
label | 28635a0e-8c6d-5926-99ca-919b5d02c7ff |  | note | PASS if received in good condition - If not FAIL & Attach Photos/Comments below
checkpoint-status |  |  | checkpoint | Cylinders
label | 666c4b87-b6d6-54f2-a07e-4e90d67cafe7 |  | note | PASS if received in good condition - If not FAIL & Attach Photos/Comments below
checkpoint-group |  |  | section | Installation Rough-In
checkpoint-status |  |  | checkpoint | Mains, ranges & riser pipes
checkpoint-status |  |  | checkpoint | Hangers location & spacing
checkpoint-status |  |  | checkpoint | Cylinders mounted as per manufacturer's recommendations
checkpoint-status |  |  | checkpoint | Cylinder hoses fitted correctly to discharge manifold
checkpoint-status |  |  | checkpoint | Cylinder pressure gauges fitted and indicating correctly
checkpoint-status |  |  | checkpoint | Discharge solenoid fitted
checkpoint-status |  |  | checkpoint | Manual release device fitted
checkpoint-status |  |  | checkpoint | Barometric dampers fitted
checkpoint-status |  |  | checkpoint | Penetrations Sealed
checkpoint-group |  |  | section | Installation Fit-Off
checkpoint-status |  |  | checkpoint | Discharge nozzles fitted
label | 3a3eac23-28a3-515c-a697-df7ddedf497c |  | note | Certification AS:14520
checkpoint-group |  |  | section | Sign-Off
checkpoint-status |  |  | checkpoint | Work(s) completed to specification/drawings & Area left clean/tidy - Builder final signature to be attached below if applicable
checklist-sectioned |  |  | checklist | ENT-008 - Fire Service Pumps |  |  |  |  | Yes | ENT-008 - Fire Service Pumps | e3b78771-44bf-4771-a809-d5d3d78562a3
checkpoint-group |  |  | section | Pre-Start
checkpoint-status |  |  | checkpoint | Specification reference checked
label | d3c9dae4-c3c7-5091-a919-177a80da6f53 |  | note | Specification Ref: AS:2118, AS:2941 and drawing
checkpoint-status |  |  | checkpoint | Pumps
label | 15574289-a685-5502-868f-8b557a377ac8 |  | note | PASS if received in good condition - If not FAIL & Attach Photos/Comments below
checkpoint-status |  |  | checkpoint | Pipe
label | 3c649821-3d15-5507-b9cd-4093becd8f6e |  | note | PASS if received in good condition - If not FAIL & Attach Photos/Comments below
checkpoint-status |  |  | checkpoint | Valves, Pressure Switch, Gauge
label | 161dc0f8-492b-5270-ad78-b18bb156d9f3 |  | note | PASS if received in good condition - If not FAIL & Attach Photos/Comments below
checkpoint-group |  |  | section | Installation
checkpoint-status |  |  | checkpoint | Plinths positioned
checkpoint-status |  |  | checkpoint | Pipes installed to drawing
checkpoint-status |  |  | checkpoint | Valves located as drawing
checkpoint-status |  |  | checkpoint | Hangers location and spacing
checkpoint-status |  |  | checkpoint | Pipework, pressure switches and gauges and ancillary valves
checkpoint-status |  |  | checkpoint | Water Supply Available
checkpoint-status |  |  | checkpoint | Power available
checkpoint-status |  |  | checkpoint | Pressure Switches Set
checkpoint-status |  |  | checkpoint | Flow Test
checkpoint-status |  |  | checkpoint | Statutory Labelling
checkpoint-group |  |  | section | Sign-Off
checkpoint-status |  |  | checkpoint | Work(s) completed to specification/drawings & Area left clean/tidy - Builder final signature to be attached below if applicable
checklist-flat |  |  | checklist | ENT-010 - Calibration Record x5 |  |  |  |  | Yes | ENT-010 - Calibration Record x5 | fa1fe2b5-718e-4d2e-801c-4f1e90bf7247
checkpoint-status |  |  | checkpoint | 1.Calibration Details - Pass once entered
text | 4f83c31b-a9f5-5cbc-be1a-479b6cddd21e |  | textbox | Equipment
text | f7a33659-73b7-51f2-9952-98815b94355d |  | textbox | ID Number
text | 7209a597-623a-5fe4-990e-68431d90befa |  | textbox | Expiry (If applicable)
text | 6dfd0734-13cb-59e9-aeaf-75c2e4a27d8b |  | textbox | Record Number
text | 33275335-f552-509f-807a-d86ffbc99fb9 |  | textbox | Date Calibrated
checkpoint-status |  |  | checkpoint | 1.Calibration Details - Pass once entered
text | d1676dbf-4c15-56ae-8bfb-f9d26f5507fc |  | textbox | Equipment
text | f4dcd92c-0ea2-50e6-ad30-e43760692ec1 |  | textbox | ID Number
text | fc374e26-d50c-5a19-8b2c-6e93eedfd13c |  | textbox | Expiry (If applicable)
text | c12b8f87-44db-59d3-ae9d-a60ea246b5cc |  | textbox | Record Number
text | 179c6279-0f85-57f3-b93c-bbcb439f55d7 |  | textbox | Date Calibrated
checkpoint-status |  |  | checkpoint | 1.Calibration Details - Pass once entered
text | b7ca952f-ab56-5bd6-ac03-e6e3e154f9cd |  | textbox | Equipment
text | ef89e392-d0c3-51a0-9a92-f81b4058a108 |  | textbox | ID Number
text | eeff9d93-56ed-5ec1-9f4d-a13f663670ba |  | textbox | Expiry (If applicable)
text | a30d6e09-f230-5ec8-9785-60666521ad39 |  | textbox | Record Number
text | 7bb9a0d7-38cd-5ae5-b4c4-15f33f03804e |  | textbox | Date Calibrated
checkpoint-status |  |  | checkpoint | 1.Calibration Details - Pass once entered
text | 17110eb8-88bf-5139-925c-f1ed97bdb517 |  | textbox | Equipment
text | f9e069fc-3d28-5a17-88b5-9783b54182d2 |  | textbox | ID Number
text | fbb05512-a011-50cf-a76f-3d801255611f |  | textbox | Expiry (If applicable)
text | 6fdd0dae-6dbd-5fdf-8fad-779d7ed5c2f3 |  | textbox | Record Number
text | bc53b8e3-0007-5b90-9304-8533254424b3 |  | textbox | Date Calibrated
checkpoint-status |  |  | checkpoint | 1.Calibration Details - Pass once entered
text | a5404cc0-6914-5157-8f05-de9528b41ced |  | textbox | Equipment
text | 9504be57-2293-52d3-b664-e98edd0f1ab1 |  | textbox | ID Number
text | 12b1184e-cd15-5c11-98f5-71f850e790f5 |  | textbox | Expiry (If applicable)
text | 313b8719-1b45-5970-972f-ffabe98fd71e |  | textbox | Record Number
text | 15e42173-1565-5808-a25e-1d9fc1dd3d17 |  | textbox | Date Calibrated
checkpoint-status |  |  | checkpoint | Sign-Off Records completed
label | e8b737f3-f759-5852-b1b2-3f04e40d227d |  | note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
button | 17c329cb-1ef0-50d0-a081-7505ef4dac1c |  | button | Entire Fire Signature Sign-Off added below | Yes,No