## QA Folder Structure
QA Folder Structure |  |  | Checklists
Site QA
P1
|  | Sprinkler Control Valves | ENT-003 - Sprinkler control valves
|  | Sprinkler Rough In & Fit Off | ENT-004 - Sprinkler rough in and fit off
|  | Pressure Test | ENT-009 - Pressure Test Report
|  | Calibration | ENT-010 - Calibration Record x5

## Fire QA Checklists
type | name | values | prefix | postfix
checklist | ENT-003 - Sprinkler control valves
section | Installation
checkpoint | Confirm correct construction issue drawings approved for use
checkpoint | Confirm isolation valve installed
checkpoint | Confirm alarm valve installed
checkpoint | Confirm drain valve installed and pipework connected to hydraulic drain
checkpoint | Confirm test valves installed
checkpoint | Confirm alarm pressure switch installed
checkpoint | Confirm local alarm installed
checkpoint | Confirm pressure gauges installed
checkpoint | Confirm jacking pump installed
checkpoint | Confirm alarms wiring complete
section | Commissioning
checkpoint | Confirm monitored valves indicate at the FIP
checkpoint | Confirm system alarm pressure switch indicates at the FIP via manual test valve
checkpoint | Confirm operation of the local alarm via the manual test valve
checkpoint | Confirm correct operation of the jacking pump
label | Record cut in and cut out pressures
checkpoint | Perform sprinkler flow test
label | Attach results
checkpoint | Confirm statutory labelling installed
section | Sign-Off
checkpoint | Certifier report
checklist | ENT-004 - Sprinkler rough in and fit off
section | Pre-Start
checkpoint | Confirm correct construction issue drawings approved for use
label | PASS if confirming "for construction" drawing issued - Attach drawing
checkpoint | Pipe + Fittings + Hangers
label | PASS if received in good condition - If not FAIL & Attach Photos/Comments below
checkpoint | Sprinklers
label | PASS if received in good condition - If not FAIL & Attach Photos/Comments below
section | Installation Rough-In
checkpoint | Confirm fixing methods approved for use
checkpoint | Confirm maximum spacing of hangers at 4m for 25mm pipe
checkpoint | Confirm maximum spacing of hangers at 5m for 32mm to 100mm pipe
checkpoint | Confirm maximum spacing of hangers at 6m for 150mm or greater pipe
checkpoint | Confirm hanger location at change of direction at 1m maximum
checkpoint | Confirm first range pipe hangers from mains at 2m maximum
checkpoint | Confirm range pipe hangers 1m maximum from end
checkpoint | Confirm armpeice longer than 500mm supported
checkpoint | Confirm installation of isolation valves or ancilliary devices
checkpoint | Confirm pipework installed as per drawing
checkpoint | Confirm sprinklers installed as per the drawing
checkpoint | Confirm open ends plugged or capped
checkpoint | Pressure test installation
label | Specification Ref: ENT-009
checkpoint | Confirm pipe identification or painting
checkpoint | Pentrations sealed
section | Installation Fit-Off
checkpoint | Sprinkler heads fitted to final locations as per coordinated RCP
checkpoint | Confirm fit off sprinkler bracketing installed
checkpoint | Pressure test installation
label | Specification Ref: ENT-009
section | Commissioning
checkpoint | Charge installation
section | Sign-Off
checkpoint | Certifier report
section | Pre-Start
checkpoint | Specification reference checked
label | Specification Ref: AS:2118, AS:2415, AS:2414, AS:1530, AS:2419 and drawing
text | Drawing & Revision # (or Attach photo below)
checkpoint | Area clear, tidy and accessible
label | Attach Photos/Comments below if any issues & Send report to Builder
checkpoint | Pipe + Fittings
label | PASS if received in good condition - If not FAIL & Attach Photos/Comments below
checkpoint | Hose Reels / Millcocks
label | PASS if received in good condition - If not FAIL & Attach Photos/Comments below
section | Installation Rough-In
checkpoint | Mains & branches installed to drawing
checkpoint | Hangers Location
checkpoint | Pentrations sealed
section | Installation Fit-Off
checkpoint | Hose Reels (Minimum Clearances)
checkpoint | Millcocks (Minimum Clearances)
checkpoint | Pressure Test
label | Specification Ref: QCF-ENT-009
text | Test No.
checkpoint | Pipe Identification Labelling
checkpoint | Statutory Signage
label | Completed By Others
section | Commissioning
checkpoint | Flow Tests
label | By Independent Certifier - Attached below as applicable
checkpoint | Certification
label | By Independent Certifier - Attached below as applicable
section | Sign-Off
checkpoint | Work(s) completed to specification/drawings & Area left clean/tidy - Builder final signature to be attached below if applicable
section | Pre-test details
checkpoint | Latest IFC drawings checked & referenced
text | Drawing & Revision # (or Attach photo below)
text | Grid Ref
button | Area clear, tidy and accessible | Yes,No
label | Attach Photos/Comments below if any issues & Send report to Builder
checkpoint | Year & Height - pass once entered
text | Year of installation
text | Head height (m)
select | Classification | xlh,oh,xhh,other (Specify below)
text | Other (Specify here)
checkpoint | Block Plan Flow 1 - pass once entered (n/a if not applicable)
text | l/min
text | kPa
checkpoint | Block Plan Flow 2 - pass once entered (n/a if not applicable)
text | l/min
text | kPa
checkpoint | Block Plan Flow 3 - pass once entered (n/a if not applicable)
text | l/min
text | kPa
checkpoint | Block Plan Flow 4 - pass once entered (n/a if not applicable)
text | l/min
text | kPa
checkpoint | Block Plan Flow5 - pass once entered (n/a if not applicable)
text | l/min
text | kPa
checkpoint | Water supply and mains - pass once entered
button | Water supply - grade | 1,2,3
text | Towns main #1
text | Towns main #2
checkpoint | Tank details - pass once entered
button | Tank supply (Y/N) | Yes,No
text | Capacity
text | Status
checkpoint | Pump details - pass once entered
select | Pump type | Electric,Diesel
text | Make
text | Serial no
text | Rated flow & pressure
text | Cut-in pressure
text | Pump orifice size (if electric)
text | K-factor (if electric)
text | Annubar size (if diesel)
button | Annubar type (if diesel) | Round,Diamond
text | Measuring device
section | Pressure Tests (kPa)
checkpoint | Pressure test 1 (n/a if not required)
text | %
text | L/min
text | T/main no.1
text | Inst. gauge
text | T/main no.2
text | Inst. gauge
text | Comb. main
text | Inst. gauge
checkpoint | Pressure test 2 (n/a if not required)
text | %
text | L/min
text | T/main no.1
text | Inst. gauge
text | T/main no.2
text | Inst. gauge
text | Comb. main
text | Inst. gauge
checkpoint | Pressure test 3 (n/a if not required)
text | %
text | L/min
text | T/main no.1
text | Inst. gauge
text | T/main no.2
text | Inst. gauge
text | Comb. main
text | Inst. gauge
checkpoint | Pressure test 4 (n/a if not required)
text | %
text | L/min
text | T/main no.1
text | Inst. gauge
text | T/main no.2
text | Inst. gauge
text | Comb. main
text | Inst. gauge
checkpoint | Pressure test 5 (n/a if not required)
text | %
text | L/min
text | T/main no.1
text | Inst. gauge
text | T/main no.2
text | Inst. gauge
text | Comb. main
text | Inst. gauge
checkpoint | Pressure test 6 (n/a if not required)
text | %
text | L/min
text | T/main no.1
text | Inst. gauge
text | T/main no.2
text | Inst. gauge
text | Comb. main
text | Inst. gauge
checkpoint | Pressure test 7 (n/a if not required)
text | %
text | L/min
text | T/main no.1
text | Inst. gauge
text | T/main no.2
text | Inst. gauge
text | Comb. main
text | Inst. gauge
checkpoint | Pressure test 8 (n/a if not required)
text | %
text | L/min
text | T/main no.1
text | Inst. gauge
text | T/main no.2
text | Inst. gauge
text | Comb. main
text | Inst. gauge
checkpoint | Pressure test 9 (n/a if not required)
text | %
text | L/min
text | T/main no.1
text | Inst. gauge
text | T/main no.2
text | Inst. gauge
text | Comb. main
text | Inst. gauge
checkpoint | Pressure test 10 (n/a if not required)
text | %
text | L/min
text | T/main no.1
text | Inst. gauge
text | T/main no.2
text | Inst. gauge
text | Comb. main
text | Inst. gauge
section | Pressure Tests (psi)
checkpoint | Pressure test 1 (n/a if not required)
text | %
text | L/min
text | Diesel disch.
text | Diesel suction
text | Inst. gauge
text | Elect. disch
text | Elect. suction
text | Inst. gauge
checkpoint | Pressure test 2(n/a if not required)
text | %
text | L/min
text | Diesel disch.
text | Diesel suction
text | Inst. gauge
text | Elect. disch
text | Elect. suction
text | Inst. gauge
checkpoint | Pressure test 3 (n/a if not required)
text | %
text | L/min
text | Diesel disch.
text | Diesel suction
text | Inst. gauge
text | Elect. disch
text | Elect. suction
text | Inst. gauge
checkpoint | Pressure test 4 (n/a if not required)
text | %
text | L/min
text | Diesel disch.
text | Diesel suction
text | Inst. gauge
text | Elect. disch
text | Elect. suction
text | Inst. gauge
checkpoint | Pressure test 5 (n/a if not required)
text | %
text | L/min
text | Diesel disch.
text | Diesel suction
text | Inst. gauge
text | Elect. disch
text | Elect. suction
text | Inst. gauge
checkpoint | Pressure test 6 (n/a if not required)
text | %
text | L/min
text | Diesel disch.
text | Diesel suction
text | Inst. gauge
text | Elect. disch
text | Elect. suction
text | Inst. gauge
checkpoint | Pressure test 7 (n/a if not required)
text | %
text | L/min
text | Diesel disch.
text | Diesel suction
text | Inst. gauge
text | Elect. disch
text | Elect. suction
text | Inst. gauge
checkpoint | Pressure test 8 (n/a if not required)
text | %
text | L/min
text | Diesel disch.
text | Diesel suction
text | Inst. gauge
text | Elect. disch
text | Elect. suction
text | Inst. gauge
checkpoint | Pressure test 9 (n/a if not required)
text | %
text | L/min
text | Diesel disch.
text | Diesel suction
text | Inst. gauge
text | Elect. disch
text | Elect. suction
text | Inst. gauge
checkpoint | Pressure test 10 (n/a if not required)
text | %
text | L/min
text | Diesel disch.
text | Diesel suction
text | Inst. gauge
text | Elect. disch
text | Elect. suction
text | Inst. gauge
section | Sign-Off
checkpoint | Work(s) completed to specification/drawings & Area left clean/tidy - Builder final signature to be attached below if applicable
checklist-flat | ENT-009 - Pressure Test Report
checkpoint | Test Details & Results
select | Select correct test criteria for Test | TEST CRITERIA HYDRANT HOSEREELS - HYDROSTATIC TEST – 1700kpa 2 HOURS,TEST CRITERIA FIRE SPRINKLERS - HYDROSTATIC TEST – 1700kpa 2 HOURS,TEST CRITERIA GAS SUPPRESSION - PNEUMATIC TEST – 300kpa 10 MINS - PRESSURE DROP SHALL NOT EXCEED 20% (60kpa),TEST CRITERIA WATER MIST - HYDROSTATIC TEST – 3300kpa 2 HOURS,Other (Specify below)
text | Other (Specify here)
text | Test No.
text | Gauge Reference (or Attach photo below)
text | Start Date
text | Start Time
text | Start Pressure
text | Final Pressure
text | Finish Time
checklist-flat | ENT-010 - Calibration Record x5
checkpoint | 1.Calibration Details - Pass once entered
text | Equipment
text | ID Number
text | Expiry (If applicable)
text | Record Number
text | Date Calibrated
checkpoint | 1.Calibration Details - Pass once entered
text | Equipment
text | ID Number
text | Expiry (If applicable)
text | Record Number
text | Date Calibrated
checkpoint | 1.Calibration Details - Pass once entered
text | Equipment
text | ID Number
text | Expiry (If applicable)
text | Record Number
text | Date Calibrated
checkpoint | 1.Calibration Details - Pass once entered
text | Equipment
text | ID Number
text | Expiry (If applicable)
text | Record Number
text | Date Calibrated
checkpoint | 1.Calibration Details - Pass once entered
text | Equipment
text | ID Number
text | Expiry (If applicable)
text | Record Number
text | Date Calibrated
section | Pre-Start
checkpoint | Specification reference checked
label | Specification Ref: AS:2444, AS:2941 and drawing
text | drawing reference
section | Installation
checkpoint | Secure cabinet
checkpoint | Extinguishers installed
checkpoint | Signage to meet code compliance
checkpoint | Hangers location and spacing
checkpoint | Fire blankets
section | Sign-Off
checkpoint | Work(s) completed to specification/drawings & Area left clean/tidy - Builder final signature to be attached below if applicable
section | Pre-Start
checkpoint | Specification reference checked
label | Specification Ref: AS:1670, AS:3000 and drawing
text | Drawing & Revision # (or Attach photo below)
checkpoint | Area clear, tidy and accessible
label | Attach Photos/Comments below if any issues & Send report to Builder
checkpoint | Cable/Conduit/Tray
label | PASS if received in good condition - If not FAIL & Attach Photos/Comments below
checkpoint | Speakers/Strobes
label | PASS if received in good condition - If not FAIL & Attach Photos/Comments below
section | Installation Rough-In
checkpoint | Correct cable used (eg Fire rated as required)
checkpoint | Cable Support
checkpoint | Segregation from other electrical services
section | Installation Fit-Off
checkpoint | Speakers/Strobes
checkpoint | OWS Panel
section | Commissioning
checkpoint | Confirm operation of all speakers/strobes
checkpoint | Confirm decibel levels
checkpoint | Confirm OWS operation initiated from FDCIE
section | Sign-Off
checkpoint | Work(s) completed to specification/drawings & Area left clean/tidy - Builder final signature to be attached below if applicable