## QA Folder Structure
QA Folder Structure |  | Date: 17/06/22 |  | checklists
Site QA
Level 1
Woolworths
|  |  | Ductwork Installation | ITC-001 Floor Rough In
|  |  | Ductwork insulation | ITC-006 Subcontractor Fit Off
|  |  | Ductwork Piece Factory | ITC-001 Floor Rough In
|  |  | Grille Installation | ITC-002 Floor Fit Off
|  |  | CHW Pipe work installation | ITC-007 Chilled water pipe
|  |  | HHW Pipe work installation | ITC-008 Heating water pipe
|  |  | Fan installaion | ITC-003 Equipment Installation
|  |  | Mech elec installation | ITC-006 Subcontractor Fit Off
|  |  | Fire Dampers & Fire Penetrations Register | ITC-012 Fire/smoke damper checklist
|  |  | Plant room | ITC-004 Plant Room
|  |  | AHU Installation | ITC-003 Equipment Installation
|  |  | Pump installation | ITC-003 Equipment Installation
|  |  | FCU Installation | ITC-003 Equipment Installation
|  |  | Fan coil splits installation | ITC-003 Equipment Installation
Zone 3
|  |  | Ductwork Installation | ITC-001 Floor Rough In
|  |  | Ductwork insulation | ITC-006 Subcontractor Fit Off
|  |  | Ductwork Piece Factory | ITC-001 Floor Rough In
|  |  | Grille Installation | ITC-002 Floor Fit Off
|  |  | CHW Pipe work installation | ITC-007 Chilled water pipe
|  |  | HHW Pipe work installation | ITC-008 Heating water pipe
|  |  | Fan installaion | ITC-003 Equipment Installation
|  |  | Mech elec installation | ITC-006 Subcontractor Fit Off
|  |  | Fire Dampers & Fire Penetrations Register | ITC-012 Fire/smoke damper checklist
Zone 4
|  |  | Ductwork Installation | ITC-001 Floor Rough In
|  |  | Ductwork insulation | ITC-006 Subcontractor Fit Off
|  |  | Ductwork Piece Factory | ITC-001 Floor Rough In
|  |  | Grille Installation | ITC-002 Floor Fit Off
|  |  | FCU Installation | ITC-003 Equipment Installation
|  |  | Mech elec installation | ITC-006 Subcontractor Fit Off
|  |  | CHW Pipe work installation | ITC-007 Chilled water pipe
|  |  | HHW Pipe work installation | ITC-008 Heating water pipe
|  |  | Fan installaion | ITC-003 Equipment Installation
|  |  | Fire Dampers & Fire Penetrations Register | ITC-012 Fire/smoke damper checklist
Zone 6 (Ambience)
|  |  | Ductwork Installation | ITC-001 Floor Rough In
|  |  | Grille Installation | ITC-002 Floor Fit Off
Zone 7 (Ambience)
|  |  | Ductwork Installation | ITC-001 Floor Rough In
|  |  | Grille Installation | ITC-002 Floor Fit Off
Level 2
Zone 3
|  |  | Ductwork Installation | ITC-001 Floor Rough In
|  |  | Ductwork insulation | ITC-006 Subcontractor Fit Off
|  |  | CHW Pipe work installation | ITC-007 Chilled water pipe
|  |  | HHW Pipe work installation | ITC-008 Heating water pipe
|  |  | Grille Installation | ITC-002 Floor Fit Off
|  |  | AHU Installation | ITC-003 Equipment Installation
|  |  | Mech elec installation | ITC-006 Subcontractor Fit Off
|  |  | Fire Dampers & Fire Penetrations Register | ITC-012 Fire/smoke damper checklist
Zone 4
|  |  | Ductwork Installation | ITC-001 Floor Rough In
|  |  | Ductwork insulation | ITC-006 Subcontractor Fit Off
|  |  | CHW Pipe work installation | ITC-007 Chilled water pipe
|  |  | HHW Pipe work installation | ITC-008 Heating water pipe
|  |  | Grille Installation | ITC-002 Floor Fit Off
|  |  | AHU Installation | ITC-003 Equipment Installation
|  |  | Mech elec installation | ITC-006 Subcontractor Fit Off
|  |  | Fan installation | ITC-003 Equipment Installation
|  |  | Fire Dampers & Fire Penetrations Register | ITC-012 Fire/smoke damper checklist
Zone 6 (Ambience)
|  |  | Ductwork Installation | ITC-001 Floor Rough In
|  |  | Ductwork insulation | ITC-006 Subcontractor Fit Off
|  |  | Grille Installation | ITC-002 Floor Fit Off
Zone 7 (Ambience)
|  |  | Ductwork Installation | ITC-001 Floor Rough In
|  |  | Ductwork insulation | ITC-006 Subcontractor Fit Off
|  |  | Grille Installation | ITC-002 Floor Fit Off
Level 3
Zone 3
|  |  | Ductwork Installation | ITC-001 Floor Rough In
|  |  | Ductwork insulation | ITC-006 Subcontractor Fit Off
|  |  | Grille Installation | ITC-002 Floor Fit Off
|  |  | CHW Pipe work installation | ITC-007 Chilled water pipe
|  |  | HHW Pipe work installation | ITC-008 Heating water pipe
|  |  | Fan installation | ITC-003 Equipment Installation
|  |  | AHU Installation | ITC-003 Equipment Installation
|  |  | Mech elec installation | ITC-006 Subcontractor Fit Off
|  |  | VAV installation | ITC-003 Equipment Installation
|  |  | Fire Dampers & Fire Penetrations Register | ITC-012 Fire/smoke damper checklist
Zone 4
|  |  | Ductwork Installation | ITC-001 Floor Rough In
|  |  | Ductwork insulation | ITC-006 Subcontractor Fit Off
|  |  | Grille Installation | ITC-002 Floor Fit Off
|  |  | CHW Pipe work installation | ITC-007 Chilled water pipe
|  |  | HHW Pipe work installation | ITC-008 Heating water pipe
|  |  | AHU Installation | ITC-003 Equipment Installation
|  |  | Mech elec installation | ITC-006 Subcontractor Fit Off
|  |  | VAV installation | ITC-003 Equipment Installation
|  |  | Fire Dampers & Fire Penetrations Register | ITC-012 Fire/smoke damper checklist
Level 4
Zone 3
|  |  | Ductwork Installation | ITC-001 Floor Rough In
|  |  | Ductwork insulation | ITC-006 Subcontractor Fit Off
|  |  | Grille Installation | ITC-002 Floor Fit Off
|  |  | CHW Pipe work installation | ITC-007 Chilled water pipe
|  |  | HHW Pipe work installation | ITC-008 Heating water pipe
|  |  | AHU Installation | ITC-003 Equipment Installation
|  |  | Mech elec installation | ITC-006 Subcontractor Fit Off
|  |  | VAV installation | ITC-003 Equipment Installation
|  |  | Fire Dampers & Fire Penetrations Register | ITC-012 Fire/smoke damper checklist
Zone 4
|  |  | Ductwork Installation | ITC-001 Floor Rough In
|  |  | Ductwork insulation | ITC-006 Subcontractor Fit Off
|  |  | Grille Installation | ITC-002 Floor Fit Off
|  |  | CHW Pipe work installation | ITC-007 Chilled water pipe
|  |  | HHW Pipe work installation | ITC-008 Heating water pipe
|  |  | AHU Installation | ITC-003 Equipment Installation
|  |  | Mech elec installation | ITC-006 Subcontractor Fit Off
|  |  | VAV installation | ITC-003 Equipment Installation
|  |  | Fire Dampers & Fire Penetrations Register | ITC-012 Fire/smoke damper checklist
Roof
Zone 3
|  |  | Ductwork Installation | ITC-001 Floor Rough In
|  |  | CHW Pipe work installation | ITC-007 Chilled water pipe
|  |  | HHW Pipe work installation | ITC-008 Heating water pipe
|  |  | Mech elec installation | ITC-006 Subcontractor Fit Off
|  |  | AHU Installation | ITC-003 Equipment Installation
|  |  | Fan installation | ITC-003 Equipment Installation
Zone 4
|  |  | Ductwork Installation | ITC-001 Floor Rough In
|  |  | CHW Pipe work installation | ITC-007 Chilled water pipe
|  |  | HHW Pipe work installation | ITC-008 Heating water pipe
|  |  | Mech elec installation | ITC-006 Subcontractor Fit Off
|  |  | AHU Installation | ITC-003 Equipment Installation
|  |  | Fan installation | ITC-003 Equipment Installation
Zone 6 (Ambience)
|  |  | Fan installation | ITC-003 Equipment Installation
|  |  | Ductwork Installation | ITC-001 Floor Rough In
|  |  | Mech elec installation | ITC-006 Subcontractor Fit Off
Zone 7 (Ambience)
|  |  | Ductwork Installation | ITC-001 Floor Rough In
|  |  | Fan installation | ITC-003 Equipment Installation
|  |  | Mech elec installation | ITC-006 Subcontractor Fit Off
Plant Rooms
Level 2
|  |  | Zone 3 | ITC-004 Plant Room | ITC-004 Plant Room
|  |  | Zone 4 | ITC-004 Plant Room | ITC-004 Plant Room
Level 3
|  |  | Zone 3 | ITC-004 Plant Room | ITC-004 Plant Room
|  |  | Zone 4 | ITC-004 Plant Room | ITC-004 Plant Room
Level 4
|  |  | Zone 3 | ITC-004 Plant Room | ITC-004 Plant Room
Roof
|  |  | Zone 3 | ITC-004 Plant Room | ITC-004 Plant Room

## Copy of MECH ITCs
type | name | values
checklist | ITC-001 Floor Rough In
section | Pre-Start
checkpoint | Specification reference checked
text | Drawing number and revision
section | Ductwork
checkpoint | Supported to Entire standard (ENT-STD-3.1)
checkpoint | Duct flanges firmly bolted
checkpoint | Cleats installed
checkpoint | Installed to latest drawing
checkpoint | Correct rod lengths
checkpoint | Insulated as required
checkpoint | Damage free
checkpoint | Flex Supported to Entire standard (ENT-STD-1.1)
checkpoint | Seismic restraints installed as per Seismic design
checkpoint | Cushion Boxes Installed correctly
checkpoint | Fire dampers installed correctly
checkpoint | Volume control dampers installed correctly
checkpoint | Kitchen Exhaust duct sealed correctly
checkpoint | Hangers installed as per the design
checkpoint | Attenuators installed to the latest drawing
section | Pipework
checkpoint | Pipes correctly supported
checkpoint | Hydrostatically tested as per (ITC-010 & ITC-011)
checkpoint | Pipes insulated as required
checkpoint | Hangers installed as per the design
checkpoint | No other services suspended from pipe work
checkpoint | Installed to latest drawing
checkpoint | Welds checked
checkpoint | Seismic restraints installed as per Seismic design
checkpoint | Drains installed to standard & on correct grade
checkpoint | Refrigeration pressure test as per (ITC-013)
checkpoint | Springs correctly selected
checkpoint | Correct valves installed
checkpoint | Control valves installed correctly
checklist | ITC-003 Equipment Installation
section | Pre-Start
checkpoint | Specification reference checked
text | Drawing number and revision
section | Fans
checkpoint | Installed to latest drawing
checkpoint | Fan direction checked
checkpoint | Flexible connections installed
checkpoint | Viberation control correctly selected & installed
checkpoint | Seismic restraints Installed as per Seismic design
checkpoint | Acoustic treatment (if required)
checkpoint | Labelled
checkpoint | VSD installed (if required)
section | AHU / FCU / Cassettes
checkpoint | Installed to latest drawing
checkpoint | Seismic restraints Installed as per Seismic design
checkpoint | Pipe valve sets Installed correctly (ENT-STD-2.1) Pipe connections checked
checkpoint | Hydrostatic test as per (ITC-010 & ITC-011)
checkpoint | Drains installed to standard & correct fall
checkpoint | Unit clearly labelled
checkpoint | Viberation control correctly selected & installed
section | DX Split Systems
checkpoint | Indoor Unit installed as per the latest drawing
checkpoint | Outdoor unit installed as per the latest drawing
checkpoint | Installed in the correct positions and clearances
checkpoint | Pipe works installed to standards
checkpoint | Vibration control installed as required
checkpoint | Units clearly labelled
checkpoint | Refrigeration correctly lagged
checkpoint | Refrigeration pressure test as per (ITC-012)
checkpoint | Nitrogen used for purging during welding
section | Other Equipment
checkpoint | Dust extraction system installed as per drawing
checkpoint | Humidifier installed as per the latest drawing
checkpoint | Air compressors installed as per drawing
checkpoint | Equipment clearly labelled
checklist | ITC-004 Plant Room
section | Pre-Start
checkpoint | Specification reference checked
text | Drawing number and revision
section | Ductwork
checkpoint | Supported to Entire standard (ENT-STD-3.1)
checkpoint | Duct flanges firmly bolted
checkpoint | Cleats installed
checkpoint | Installed to latest drawing
checkpoint | Correct rod lengths
checkpoint | Insulated as required
checkpoint | Damage free
checkpoint | Seismic restraints installed as per seismic design
checkpoint | Attenuators installed to the latest drawing
checkpoint | VSD's installed correctly
checkpoint | Fire Dampers installed correctly
section | Pipework
checkpoint | Pipe fitings complete and pipes properly supported
checkpoint | Hydrostatic test as per (ITC-010 & ITC-011)
checkpoint | Pipes insulated as required
checkpoint | No other services suspended from pipe work
checkpoint | Installed to latest drawing
checkpoint | Welds checked
checkpoint | Seismic Restraints Installed as per Seismic design
checkpoint | Refrigeration pressure test as per (ITC-013)
checkpoint | Correct valves installed
checkpoint | Control valves installed correctly
checkpoint | Pipe work clearly labelled
section | Plant Room Equipment
checkpoint | Fans installed as per latest drawing
checkpoint | Quckfill installed as per latest drawing
checkpoint | Buffer tanks installed as per latest drawing
checkpoint | Chillers installed as per latest drawing
checkpoint | Pumps installed as per latest drawing
checkpoint | Expansion Tanks installed as per latest drawing
checkpoint | Cooling tower/s installed as per latest drawing
checkpoint | Water Treatment installed as per latest drawing
checkpoint | Air and dirt separtor installed as per latest drawing
checkpoint | Equipment Clealy Labelled
checklist | ITC-007 Chilled water pipe
section | Pre-Start
checkpoint | Test specifications met
text | Test period to be a minimum of 4 hours
label | Test pressure to be 900kPa (Exceeds AS4041-2006 Appendix U)
label | AS4041-2006 Table 6.7.3 Requires Test Time of 15min for pipe ≤DN300 (For all other buildings)
label | AS4041-2006 Table 6.7.3 Requires Test Time of 25min for pipe >DN300 (For CU building)
section | Test details
checkpoint | Test details
bool | Applies on this floor or level | yes,no
text | Pipe system
text | area/section under
text | from
text | to
text | System working pressure
text | System test pressure
text | Initial reading - kPA, time, ambient temperature
text | 15/25 min reading - kPA, time, ambient temperature
section | Sign off
checkpoint | Sign off - attach signature below and pass once complete
checklist | ITC-008 Heating water pipe
section | Pre-Start
checkpoint | Test specifications met
text | Test period to be a minimum of 4 hours
label | Test pressure to be 700kPa (Exceeds AS4041-2006 Appendix U)
label | AS4041-2006 Table 6.7.3 Requires Test Time of 15min for pipe ≤DN300 (For all other buildings)
label | AS4041-2006 Table 6.7.3 Requires Test Time of 25min for pipe >DN300 (For CU building)
section | Test details
checkpoint | Test Details
bool | Applies on this floor or level | yes,no
text | Pipe system
text | area/section under
text | from
text | to
text | System working pressure
text | System test pressure
text | Initial reading - kPA, time, ambient temperature
text | 15/25 min reading - kPA, time, ambient temperature
section | Sign off
checkpoint | Sign off - attach signature below and pass once complete
checklist | ITC-009 Condenser water pipe
section | Pre-Start
checkpoint | Test specifications met
text | Test period to be a minimum of 4 hours
label | Test pressure to be 700kPa (Exceeds AS4041-2006 Appendix U)
label | AS4041-2006 Table 6.7.3 Requires Test Time of 15min for pipe ≤DN300 (For all other buildings)
label | AS4041-2006 Table 6.7.3 Requires Test Time of 25min for pipe >DN300 (For CU building)
section | Test details
checkpoint | Test Details
bool | Applies on this floor or level | yes,no
text | Pipe system
text | area/section under
text | from
text | to
text | System working pressure
text | System test pressure
text | Initial reading - kPA, time, ambient temperature
text | 15/25 min reading - kPA, time, ambient temperature
section | Sign off
checkpoint | Sign off - attach signature below and pass once complete