## Project Structure
Site QA |  |  |  | Checklists
Site Wide
|  | Ground level | In ground conduits | Underground Conduits ITP001
|  |  | Sub mains | Mains, Sub Mains Cable in Conduits or on Trays ITP004
Block A
Ground level
|  |  | Lights | Installation of lighting cabling and fit off
|  |  | Containment | Installation of steel tray/basket
|  |  | Power | Installation of power cabling
|  |  | Data | Installation of data cabling and outlets
|  |  | Fire Contractor | Contractor
|  |  | Security Contractor | Contractor
|  |  | AV Contractor | Contractor
|  |  | Solar Contractor | Contractor
Level 1
|  |  | Lights | Installation of lighting cabling and fit off
|  |  | Containment | Installation of steel tray/basket
|  |  | Containment | Installation of in-deck/slab conduits
|  |  | Power | Installation of power cabling
|  |  | Data | Installation of data cabling and outlets
|  |  | Fire Contractor | Contractor
|  |  | Security Contractor | Contractor
|  |  | AV Contractor | Contractor
DB's
|  |  | EDB-A-GR | Install Distribution Boards -Terminate Cables TP006
|  |  | EDB-A-L1 | Install Distribution Boards -Terminate Cables TP006
Main Swithcboard
|  |  | MSB | Main Switchboard & Termination of Cables ITP002
Block B2
Ground level
|  |  | Lights | Installation of lighting cabling and fit off
|  |  | Containment | Installation of steel tray/basket
|  |  | Power | Installation of power cabling
|  |  | Data | Installation of data cabling and outlets
|  |  | Fire Contractor | Contractor
|  |  | Security Contractor | Contractor
|  |  | AV Contractor | Contractor
Level 1
|  |  | Lights | Installation of lighting cabling and fit off
|  |  | Containment | Installation of steel tray/basket
|  |  | Containment | Installation of in-deck/slab conduits
|  |  | Power | Installation of power cabling
|  |  | Data | Installation of data cabling and outlets
|  |  | Fire Contractor | Contractor
|  |  | Security Contractor | Contractor
|  |  | AV Contractor | Contractor
DB's
|  |  | EDB-B2-GR | Install Distribution Boards -Terminate Cables TP006
|  |  | EDB-B2-L1 | Install Distribution Boards -Terminate Cables TP006
Block B3
Ground level
|  |  | Lights | Installation of lighting cabling and fit off
|  |  | Containment | Installation of steel tray/basket
|  |  | Power | Installation of power cabling
|  |  | Data | Installation of data cabling and outlets
|  |  | Fire Contractor | Contractor
|  |  | Security Contractor | Contractor
|  |  | AV Contractor | Contractor
Level 1
|  |  | Lights | Installation of lighting cabling and fit off
|  |  | Containment | Installation of steel tray/basket
|  |  | Containment | Installation of in-deck/slab conduits
|  |  | Power | Installation of power cabling
|  |  | Data | Installation of data cabling and outlets
|  |  | Fire Contractor | Contractor
|  |  | Security Contractor | Contractor
|  |  | AV Contractor | Contractor
DB's
|  |  | EDB-B3-GR | Install Distribution Boards -Terminate Cables TP006
|  |  | EDB-B3-L1 | Install Distribution Boards -Terminate Cables TP006
Block C
Ground level
|  |  | Lights | Installation of lighting cabling and fit off
|  |  | Containment | Installation of steel tray/basket
|  |  | Power | Installation of power cabling
|  |  | Data | Installation of data cabling and outlets
|  |  | Fire Contractor | Contractor
|  |  | Security Contractor | Contractor
|  |  | AV Contractor | Contractor
DB's
|  |  | EDB-C-GR | Install Distribution Boards -Terminate Cables TP006
|  |  | EDB Canteen | Install Distribution Boards -Terminate Cables TP006

## ITPs
type | name | values
Checklist | Underground Conduits ITP001
section | Preparation
checkpoint | Check clear of other services (The Clearance for gas pipes is 300mm & other services 100mm)
checkpoint | Check cable size to verify conduit size & determine size of trench
checkpoint | Organise barricades, webbing, plates, warning lights (if applicable prior to excavation) - please take a photo
checkpoint | Determine spoil removal, backfill material, compaction, cable marking protection & installment requirements
section | Installation
checkpoint | Confirm area of work is accessible & acceptable to commence (If not comment below)
checkpoint | Setout & alignment as per drawing (include revision below)
text | Drawing & revision number(s)
checkpoint | Mark out trench route - Arrange saw cutting if required
checkpoint | Excavate trench & install barricades as required - please take a photo
checkpoint | Determine which way cable will be installed & lay coupling in no friction direction, install conduit glue.
button | Install draw wire if required | Yes, No, N/A
checkpoint | Inspect trench by supply authority if applicable
button | Inspect & backfill trench | Yes, No, N/A
button | Reinstate & clean area | Yes, No, N/A
checkpoint | Install direction marker if applicable
checkpoint | Mark up DGR for future as builts
checkpoint | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
Checklist | Main Switchboard & Termination of Cables ITP002
section | Preparation
checkpoint | Locate & fix switchboard into position - check for clearances fix correctly
checkpoint | Determine cable sizes for cable glands & mark out gland plate (check cable O.D's for cable size glands)
button | Install cable glands & cables | Yes, No, N/A
button | Install lugs & terminate | Yes, No, N/A
checkpoint | Clean & vacuum out board - please take a photo
checkpoint | Check all circuits are terminated & safe at the other end or disconnect
checkpoint | Final visual inspection of board - please take a photo
section | Installation
checkpoint | Test earth continuity & resistance
button | Test insulation resistance | Yes, No, N/A
button | Test polarity | Yes, No, N/A
button | Test phase rotation | Yes, No, N/A
checkpoint | Attach prescribed certificate of electrical safety. Organise inspection by inspector (Add photo or attached certification
checkpoint | Isolate / lock off/ dange tag all outgoing circuits - please take a photo
button | Ensure labelling is complete & accurate | Yes, No, N/A
checkpoint | Energise system
button | Check phase rotation | Yes, No, N/A
button | Check switchboard as installed as per drawings | Yes, No, N/A
text | Drawing & revision number(s)
checkpoint | Ensure any modifications to shop drawings are matched to existing & returned to office / attach drawings
checkpoint | Ensure switch room is left clean - please take a photo
checkpoint | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
Checklist | Mains, Sub Mains Cable in Conduits or on Trays ITP004
checkpoint | Measure cable runs with appropriate accurate measuring instrument (eg tape measure, wheel)
checkpoint | Check cable sizes resistance of protective earth conductor - shall be low enough to permit passage of current necessary to operate protective device
checkpoint | Confirm length of cable if sub contract item & order
text | Record length of cable
checkpoint | Install cable in appliance method (EG. Cable stands, electric winch, pulleys etc.) - ANY CABLE NOT TERMINATED IMMEDIATELY MUST HAVE THE ENDS TAPED COVERING THE BARE COPPER - please take a photo
checkpoint | Trefoil cables & tie cables to support system (ensure spacing)
button | Check requirements for cable identification & install | Yes, No, N/A
checkpoint | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
Checklist | Install Distribution Boards -Terminate Cables ITP006
checkpoint | Check delivery of distribution board - Check for damage (paint finish, dimensions & door against drawing) - Please take a photo
checkpoint | Locate & fix into position
checkpoint | Install sub mains cabling as appropriate (glands, tray & duct)
checkpoint | Install lugs & terminate
checkpoint | Install sub circuit & terminate (if circuit not complete at the other end, it must not be terminated)
checkpoint | Clean & vacuum area - please take a photo
text | Record results
checkpoint | Clearly identify services
checkpoint | Energise system
button | Check phase rotation | Yes, No, N/A
button | Check switchboard as installed as per drawings | Yes, No, N/A
text | Drawing & revision number(s)
checkpoint | Check typed schedule for accuracy & install
checkpoint | Ensure switchboard cupboard & area is left clean - Please take a photo
checkpoint | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
Checklist | ITP003 Conduit & Cable Tray form
checkpoint | Check delivery for damage & correct quantity
checkpoint | Ensure locations of lights is coordinated with other trades
checkpoint | Refer to reflected ceiling plan for set out
checkpoint | Plug in or fit off light
checkpoint | Fit off data capable (if applicable)
checkpoint | Install light fighting
button | Install lamp & diffuser & clean fitting | Yes, No, N/A
checkpoint | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
Checklist | Switchboard Delivery ITP013
checkpoint | Prior to delivery, visual inspection to coordinate delivery on site - please take a photo if delivery is unable to be completed
checkpoint | Review & determine method of unloading (eg. Crane, forklift, man power, specialist subcontractor. Arrange & upload all necessary documentation
checkpoint | Coordinate time of delivery - take photo of delivery docket
checkpoint | Check delivery for damage & correct quantity
checkpoint | Safely position delivery into place (eg. crane, forklift, rollers, manual, specialist subcontractor
label | If Ergo Group are positioning main switchboard maneuvering kit is to be delivered with main switchboard.
label | Distributions boards require a lifting trolley
checkpoint | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
Checklist | Contractor
checkpoint | Has contractors ITP been received - Please take a photo / up load checklist
Checklist | Temporary DB checklist
checkpoint | RCD
text | Date of testing
text | Next test due
checkpoint | Results and/or trip current (less 30mA) for Earth Leakage Device
checkpoint | Has a new tag been installed on the DB - please take a photo
checkpoint | Has the front cover been updated
label | Please take a photo of DB
text | License No.
Checklist | Installation of lighting cabling and fit off
section | Rough In
checkpoint | Confirm that the cable support system has been completed as per documentation
checkpoint | Electrical cables have been appropriately sized & selected to ensure that they will support currently installed & future equipment
checkpoint | Mechanical protection has been provided to minimise the likelihood of physical damage to cabling
checkpoint | Cabling has been concealed where possible in ceiling spaces, wall cavities or risers
checkpoint | All lights have been wired as per drawings
button | All lights & switches have been marked on the site as built drawings | Yes, No, N/A
button | Height & location have been confirmed for each switch | Yes, No, N/A
button | Lighting control system has been confirmed (DALI /2 40v) | Yes, No, N/A
section | Fit Off & Commission
checkpoint | Equipment/materials have been selected and installed as per drawings/specifications
checkpoint | Ceiling supports have been installed where required (ceiling fans / pendants
checkpoint | Terminations have been checked & all terminations are correct & secure in all outlets
checkpoint | Switches have all been secured in place & levelled
checkpoint | All lights are sitting flush & / or been levelled
checkpoint | All cablings has been tested for insulations resistance & continuity
checkpoint | Each circuit is terminated at the DB & protected by the correct protection device
checkpoint | Each switch has been labelled
button | Functional test carried out on each switch & light | Yes, No, N/A
checkpoint | Each circuit has been marked on the site as build's
checkpoint | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
Checklist | Installation of power cabling
section | Rough In
checkpoint | Confirm that the cable support system has been completed as per documentation
checkpoint | Electrical cables have been appropriately sized and selected to ensure that they will support currently installed and future equipment
checkpoint | Mechanical protection has been provided to minimise the likelihood of physical damage to cabling
checkpoint | Cabling has been concealed where possible in ceiling spaces, wall cavities or risers
checkpoint | All outlets have been wired as per drawings
button | All outlets have been marked on the site as built drawing | Yes, No, N/A
checkpoint | Height and location have been confirmed for each outlet
section | Fit Off & Commission
checkpoint | Equipment/materials have been selected and installed as per drawings/specifications
checkpoint | Terminations have been checked and all terminations are correct and secure in all outlets
button | Outlets have all been secured in place and levelled | Yes, No, N/A
checkpoint | All cabling has been tested for insulations resistance and continuity
checkpoint | Each circuit is terminated at the DB and protected by the correct protective device
checkpoint | Each outlet has been labelled
checkpoint | Functional test carried out on each outlet
checkpoint | Each outlet marked on the site as build’s
checkpoint | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
Checklist | Installation of in-deck/slab conduits
checkpoint | Confirm that the selected conduit is of adequate size for purpose
button | It has been confirmed that all outlets/fittings in slab have been captured | Yes, No, N/A
button | Conduit has been securely fixed | Yes, No, N/A
button | Conduit has been securely fixed to the box or volcano | Yes, No, N/A
button | Conduit box has temporarily been secured and tied down in place for pour | Yes, No, N/A
button | Alternative route has been supplied in case main route is damaged | Yes, No, N/A
button | Conduit runs have all been marked on as builts | Yes, No, N/A
checkpoint | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
Checklist | Installation of steel tray/basket
checkpoint | Confirm that the cable support system has been selected as per drawings and specifications
button | Cable support system has been selected to correctly hold the required weight | Yes, No, N/A
button | Each cable support has sufficient room for future expansion | Yes, No, N/A
button | Cable support system has been correctly installed and is secure in place | Yes, No, N/A
button | Height of cable support system has been confirmed and installed to that height in all areas | Yes, No, N/A
button | Cable support system is as per shop drawings and not impacting any other services | Yes, No, N/A
checkpoint | All threaded rods have been cut off to correct size
checkpoint | All nuts/bolts/channel nuts have been tightened
checkpoint | Any changes to drawings have been noted on the site as built drawings
checkpoint | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
Checklist | Installation of data cabling and outlets
section | Rough In
checkpoint | Confirm that the cable support system has been completed as per documentation
checkpoint | Data cabling has been selected as per drawings and specifications (Cat6/CatA & brand)
checkpoint | Mechanical protection has been provided to minimise the likelihood of physical damage to cabling
checkpoint | Cabling has been concealed where possible in ceiling spaces, wall cavities or risers
checkpoint | All outlets have been wired as per drawings
button | All data outlets have been numbered and marked on the site as built drawing | Yes, No, N/A
checkpoint | Height and location have been confirmed for each outlet
section | Fit Off & Commission
checkpoint | Equipment/materials have been selected and installed as per drawings/specifications
checkpoint | Terminations have been checked and all terminations are correct and secure in all outlets
checkpoint | Outlets have all been secured in place and levelled
checkpoint | All cabling has been tested using the Fluke data tester
checkpoint | Each cable has been correctly installed and terminated in the patch panel
checkpoint | Each outlet has been labelled
checkpoint | Each outlet marked on the site as build’s
checkpoint | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)