## Resources
Rich Type | Id | Warnings | type | name | values | prefix | postfix | Usage Count | User Addable | Template Name | Template Id
checklist-flat |  |  | checklist | ITP 180 Control Cabling |  |  |  |  | Yes | ITP 180 Control Cabling | 10670ebf-8932-4d0b-915f-e7c96b9c2052
checkpoint-status |  |  | checkpoint | Ensure that the latest revision drawings and specifications are being referred to
checkpoint-status |  |  | checkpoint | Ensure that all new installations have been coordinated with other services, both new and existing
checkpoint-status |  |  | checkpoint | Ensure all control circuits are designed to function under the necessary circumstances that they will be required to function under
checkpoint-status |  |  | checkpoint | Ensure segregation is maintained pending cable insulation and shielding ratings
checkpoint-status |  |  | checkpoint | Ensure cables can communicate the specific protocols over the distances installed
checkpoint-status |  |  | checkpoint | Ensure the correct amount of cores have been supplied
checkpoint-status |  |  | checkpoint | Ensure the requirements of the system and if it requires to be normally open/ normally closed for the control/status that is required
checkpoint-status |  |  | checkpoint | Ensure all spares are left in an open state and labelled accordingly
checkpoint-status |  |  | checkpoint | Ensure cable/cores can be easily identified for future works and maintenance
checkpoint-status |  |  | checkpoint | Low Level Inputs - Point to Point test individual cores at both the origin and the destination
checkpoint-status |  |  | checkpoint | High Level Inputs - Confirm the software can be seen on the head end system
checkpoint-status |  |  | checkpoint | Activate functional devices and programming and confirm that the control system functions correctly eg. Manually Pressing Emergency Stop - turns off designated equipment
checkpoint-status |  |  | checkpoint | Ensure that all changes made to the original drawing have been marked and noted on the Working Drawing located in the Site Office. These drawings MUST be kept updated for use as as built drawings.
checkpoint-status |  |  | checkpoint | Cross check and verify that the as built drawings are complete and correct.
checkpoint-status |  |  | checkpoint | Verify all inspections are complete and collate records.
checklist-flat |  |  | checklist | SYS - Fredon Compliance |  |  |  |  | Yes | SYS - Fredon Compliance | 1d0fe7f7-e94d-42db-96ce-c1620ef67d9d
checkpoint-status |  |  | checkpoint | Fully compliant, site specific Safety Manual and SWMS have been submitted and accepted by the Principal Contractor.
checkpoint-status |  |  | checkpoint | All Fredon electrical personnel undertaking these works have been trained and inducted in the Safety Manual and the relevant SWMS for these works.
checkpoint-status |  |  | checkpoint | All Fredon electrical personnel undertaking these works are qualified to carry out these works, and are trained, and competent in the use of all equipment and plant required to carry out these works.
checklist-flat |  |  | checklist | ITP 173 Fit Off Light Fittings |  |  |  |  | Yes | ITP 173 Fit Off Light Fittings | 207bef2b-c193-4b80-a8c7-8f889e3cb842
checkpoint-status |  |  | checkpoint | Ensure that the latest revision drawings and specifications are being referred to
checkpoint-status |  |  | checkpoint | Ensure that all new installations have been coordinated with other services, both new and existing
checkpoint-status |  |  | checkpoint | Ensure that the latest co-ordinated service drawings are being referenced
checkpoint-status |  |  | checkpoint | Ensure that the latest co-ordinated drawings are being referenced Not Required
label | e66badb7-f38c-51ff-a4d7-67fd774e1c6f |  | note | Understand physical characteristics of light fitting to be installed. Recessed fitting cut out dimensions. Lineal fitting lengths v fixings. Height of fittings. Architectural requirements - light spill direction
checkpoint-status |  |  | checkpoint | Ensure the fitting is compliant with Australian Standards
checkpoint-status |  |  | checkpoint | Install fittings as per manufacturer's recommendations
checkpoint-status |  |  | checkpoint | Ensure that the correct fitting is being installed for each location as per drawings
checkpoint-status |  |  | checkpoint | Ensure that the correct mounting method is being used i.e. surface, chain suspended, recessed etc. Check all drawings prior to installation
checkpoint-status |  |  | checkpoint | Ensure fittings are installed using the correct fixing type
checkpoint-status |  |  | checkpoint | Ensure that any required ceiling grid removal has been carried out by ceiling fixers only. UNDER NO CIRCUMSTANCE IS CEILING GRID / CHANNEL TO BE CUT BY FREDON ELECTRICAL PERSONNEL
checkpoint-status |  |  | checkpoint | Ensure that ceiling mounted fittings are adequately supported according to their weight. Additional supports added to the ceiling where necessary
checkpoint-status |  |  | checkpoint | Ensure that all terminations are correct including lighting control terminations and are as per manufacturer's requirements
checkpoint-status |  |  | checkpoint | All light fittings have been installed in a tradesman like manner (Straight & level etc)
checkpoint-status |  |  | checkpoint | Install fittings as per manufacturer's recommendations
checkpoint-status |  |  | checkpoint | Ensure that the correct fitting is being installed for each location as per drawings and visibility of escape lighting meets AS 2293. NOTE: Directional arrows show correct path of egress and the luminaire has the Emergency label attached
checkpoint-status |  |  | checkpoint | Ensure that the correct mounting method is being used i.e. surface, chain suspended, recessed etc. Check all drawings prior to installation
checkpoint-status |  |  | checkpoint | Ensure fittings are installed using the correct fixing type
checkpoint-status |  |  | checkpoint | Ensure that any required ceiling grid removal has been carried out by ceiling fixers only. UNDER NO CIRCUMSTANCE IS CEILING GRID / CHANNEL TO BE CUT BY FREDON ELECTRICAL PERSONNEL
checkpoint-status |  |  | checkpoint | Ensure that all terminations are correct including monitoring terminations and are as per manufacturer's requirements
checkpoint-status |  |  | checkpoint | Ensure that ceiling mounted fittings are adequately supported according to their weight. Additional supports added to the ceiling where necessary
checkpoint-status |  |  | checkpoint | All light fittings have been installed in a tradesman like manner (Straight & level etc)
checkpoint-status |  |  | checkpoint | Ensure all emergency lighting information is kept on As Built information. Fitting number. Circuit suppling fitting. Fitting serial numbers etc.
checkpoint-status |  |  | checkpoint | Ensure that the lighting control philosophy is understood. Cable requirements. Cable polarity. Cable connections.
checkpoint-status |  |  | checkpoint | Ensure all fitting information is kept on as built information. Fitting number. Circuit supplying fitting. Fitting serial number etc.
checkpoint-status |  |  | checkpoint | Visually inspect entire circuit for completeness Ensure fittings are protected if required Remove all rubbish - empty boxes etc.
checkpoint-status |  |  | checkpoint | Check that all ceilings, walls and floors are left neat and tidy and without any damage. IF DAMAGE OCCURS ADVISE FREDON SITE MANAGER IMMEDIATELY
checkpoint-status |  |  | checkpoint | Cross check and verify that the As Built Drawings are Complete and Correct
checkpoint-status |  |  | checkpoint | Verify all inspections are complete and collate records
checklist-flat |  |  | checklist | ITP 169 Mains & Sub Mains Installation |  |  |  |  | Yes | ITP 169 Mains & Sub Mains Installation | 456cedee-b0b3-4814-b342-5e8635ea177f
checkpoint-status |  |  | checkpoint | Ensure that the latest revision drawings and specifications are being referred to
label | 9919b156-2907-5cb5-baa6-83592534c38f |  | note | For sub main installation information follow Fredon sub main installation check sheet. The check sheet will have all necessary information such as; cable size, origin and destination. This sheet is to be followed and filled out to verify correct installation. COMPLETE ITC 169.1
checkpoint-status |  |  | checkpoint | All submains dressed in the formation specified on Fredon sub main installation check sheet.
label | 8002e059-930d-5fc4-a4c9-f436467a73af |  | note | When using a winch, maximum cable pulling tensions are not to be exceeded, refer to cable manufacturer's technical data for maximum pulling tension
checkpoint-status |  |  | checkpoint | All parallel submains dressed on cable tray/ ladder have been spaced correctly to minimise derating and satisfy all standards specs and regulations NOTE: AS3008 Table 23 & Table 24
checkpoint-status |  |  | checkpoint | All fire rated submains have been dressed with steel cable ties NOTE: Essential Safety Services require their own Fire Rated Support and cable pathway
checkpoint-status |  |  | checkpoint | Mechanical protection installed where required.
checkpoint-status |  |  | checkpoint | No cables to be tied to or supported by sprinkler / water pipes.
checkpoint-status |  |  | checkpoint | All submains have been kept clear of sharp edges during installation to avoid damage to insulation.
checkpoint-status |  |  | checkpoint | Visual inspection of rough in carried out to ensure completion
checkpoint-status |  |  | checkpoint | All relevant drawings checked to ensure that all services have been allowed for
checkpoint-status |  |  | checkpoint | Ensure that all changes made to the original drawing have been marked and noted on the Working Drawing located in the Site Office. These drawings MUST be kept updated for use as As Built Drawings.
checkpoint-status |  |  | checkpoint | Cross check and verify that the as built drawings are complete and correct
checkpoint-status |  |  | checkpoint | Verify all inspections are complete and collate records
checklist-flat |  |  | checklist | ITP 172 Light & Power Rough-In |  |  |  |  | Yes | ITP 172 Light & Power Rough-In | 58fd809e-d4a6-4f5b-9d85-2a785441a7a2
checkpoint-status |  |  | checkpoint | Ensure that the latest revision drawings and specifications are being referred to.
checkpoint-status |  |  | checkpoint | Ensure that all new installations have been coordinated with other services, both new and existing
checkpoint-status |  |  | checkpoint | Ensure that the latest service drawings are being referenced
checkpoint-status |  |  | checkpoint | Ensure that the latest co-ordinated drawings are being referenced
checkpoint-status |  |  | checkpoint | Cable locations marked on floors and walls, if required
checkpoint-status |  |  | checkpoint | Cable locations marked on drawings for ease of locating where required
checkpoint-status |  |  | checkpoint | Surface conduit correct size to house required number and size of cables
checkpoint-status |  |  | checkpoint | Surface conduit fixed correctly and all required draw boxes installed
checkpoint-status |  |  | checkpoint | Ensure that no PVC Conduit has been installed passing through fire rated walls, breaking the integrity of the fire rating.
checkpoint-status |  |  | checkpoint | Ensure that steel conduit has been installed in areas where mechanical protection is required or where called for by the project documentation.
checkpoint-status |  |  | checkpoint | All surface conduit installed in a tradesman like manner.
checkpoint-status |  |  | checkpoint | All penetrations are sized correctly
checkpoint-status |  |  | checkpoint | All penetrations are sprayed or painted with galvanising paint
checkpoint-status |  |  | checkpoint | All penetrations are bushed to prevent damage to cables passing through them
checkpoint-status |  |  | checkpoint | All penetrations are sealed to prevent the ingress of insects or vermin
checkpoint-status |  |  | checkpoint | All cable sizes selected correctly to suit the size of the supply required and to satisfy all standards, specs and regulations.
checkpoint-status |  |  | checkpoint | All cable sizes selected correctly to allow for Voltage Drop due to excessive cable run lengths to satisfy all standards, specs and regulations.
checkpoint-status |  |  | checkpoint | All cables fixed or supported correctly to satisfy all standards, specs and regulations.
checkpoint-status |  |  | checkpoint | Mechanical protection installed where required and minimum segregation from other services maintained
checkpoint-status |  |  | checkpoint | No cables to be tied to or supported by sprinkler / water pipes.
checkpoint-status |  |  | checkpoint | All feeds are marked and checked from the drawings to ensure that none have been missed.
checkpoint-status |  |  | checkpoint | All cables are marked with their circuit identification numbers at each point.
checkpoint-status |  |  | checkpoint | All cables installed on cable ladder/tray are dressed and spaced correctly to minimise derating and satisfy all standards, specifications and regulations.
label | dc1e6997-9612-5d26-90ec-672a9a57eddf |  | note | Do not leave any cable ends exposed / bare. Fredon Policy TWIST-PREPARE-TAPE
checkpoint-status |  |  | checkpoint | Visual inspection of rough in carried out to ensure completion.
checkpoint-status |  |  | checkpoint | All relevant drawings checked to ensure that all services have been allowed for.
checkpoint-status |  |  | checkpoint | Ensure that all changes made to the original drawing have been marked and noted on the Working Drawing located in the Site Office. These drawings MUST be kept updated for use as as built drawings.
checkpoint-status |  |  | checkpoint | Cross check and verify that the as built drawings are complete and correct.
checkpoint-status |  |  | checkpoint | Verify all inspections are complete and collate records.
checklist-flat |  |  | checklist | ITP 177 Horizontal Cabling |  |  |  |  | Yes | ITP 177 Horizontal Cabling | 643e0ec3-5955-4d93-9636-beb7e9dfd8cb
checkpoint-status |  |  | checkpoint | Ensure that the latest revision drawings and specifications are being referred to
checkpoint-status |  |  | checkpoint | The Updated / Superseded drawing register, located next to the drawing rack in the site office, has been checked to ensure the latest revision drawings are being referenced
checkpoint-status |  |  | checkpoint | Ensure that all new installations have been coordinated with other services, both new and existing
checkpoint-status |  |  | checkpoint | Ensure that all new installations numbering and labelling systems meet specification and have been approved by the client
label | 5fd6119c-fd36-524a-8da3-5076aa3c679c |  | note | Prior to installation submit numbered Communications shop drawings for review to the satisfaction of services engineer
checkpoint-status |  |  | checkpoint | Ensure that the latest services and co-ordinated drawings are being referenced
checkpoint-status |  |  | checkpoint | Ensure that the latest co-ordinated drawings are being referenced
checkpoint-status |  |  | checkpoint | Ensure the cable does need exceed manufacturer's bending radius and is segregated to other services as per AS S2009:2013
checkpoint-status |  |  | checkpoint | Ensure the cable has adequate support and the pathway is less than 90 m including service loops & goose necks before drops
checkpoint-status |  |  | checkpoint | Visual inspection of rough in carried out to ensure completion.
checkpoint-status |  |  | checkpoint | All relevant drawings checked to ensure that all services have been allowed for.
checkpoint-status |  |  | checkpoint | Ensure Cabinet Layouts are installed to the latest drawing layouts with door swing and clearances considered
checkpoint-status |  |  | checkpoint | Ensure cabinet is secured and and all accessories, panels and management installed correctly to latest RU Layout Drawings
checkpoint-status |  |  | checkpoint | Ensure all shielded equipment is earthed and the electrical contractor has supplied an earth with a maximum resistance of 0.5Ω
checkpoint-status |  |  | checkpoint | Ensure that all Field End Cabling has been labelled, terminated and is level to other services
checkpoint-status |  |  | checkpoint | Ensure that cables are bunched into their final looms and dressed throughout the communications room to individual patch panels
checkpoint-status |  |  | checkpoint | Ensure that all cabling is terminated according to communications rack lay out drawings
checkpoint-status |  |  | checkpoint | Ensure that all cabling is terminated has been labelled
checkpoint-status |  |  | checkpoint | Ensure that Fluke DSX Testing has the correct parameters as per manufacturer and client requirements all results are recorded with their correct label on cabinet and latest revision drawings
checkpoint-status |  |  | checkpoint | Ensure that all changes made to the original drawing have been marked and noted on the Working Drawing located in the Site Office. These drawings MUST be kept updated for use as as built drawings.
checkpoint-status |  |  | checkpoint | Cross check and verify that the As Built Drawings are Complete and Correct
checkpoint-status |  |  | checkpoint | Verify all testing are complete and collate records
checklist-flat |  |  | checklist | ITP 175 In Ground Works |  |  |  |  | Yes | ITP 175 In Ground Works | 75c4236d-92ca-4db3-996d-2e3944bfe5a4
checkpoint-status |  |  | checkpoint | Ensure that the latest revision drawings and specifications are being referred to
checkpoint-status |  |  | checkpoint | Ensure that all new installations have been coordinated with other services, both new and existing
label | 7cb9f505-ab1e-5315-9615-861cfe58b701 |  | note | Prior to installation submit conduit shop drawing for review to the satisfaction of structural engineer
checkpoint-status |  |  | checkpoint | Ensure that the latest service & co-ordinated drawings are being referenced
checkpoint-status |  |  | checkpoint | Ensure correct datum points are identified confirm datum points with building works supervisor. Use correct set out measurement tools and equipment
checkpoint-status |  |  | checkpoint | Engage certified surveyor for critical set out works
checkpoint-status |  |  | checkpoint | Identify circuit to be installed, confirm circuit cabling requirement. Select conduit size accordingly
checkpoint-status |  |  | checkpoint | Conduit to be measured and cut using correct tools
label | 24828341-9eea-546b-8487-c72792ff7d11 |  | note | All conduit bends to be sweeping using bending spring. Or large sweeping proprietary bends
label | c7ab69e8-b254-5540-8e56-bdcb07d6e981 |  | note | All joins to be glued using PVC jointing cement
label | 2b60f04e-20d2-58ad-9ccc-832bfcc6a9fe |  | note | All conduit boxes to be correct type with correct number of entry points i.e. 2way, 3way T, 4way
label | add6368e-44b5-5546-bcaa-1791492677e0 |  | note | Do not use corrugated conduit in decks
checkpoint-status |  |  | checkpoint | Ensure entire conduit installation is fixed to steel work using tie wire
label | f2742dbb-6d89-551b-a7ae-cbd5a1853e34 |  | note | Conduit should be tied to bottom mat of steel
checkpoint-status |  |  | checkpoint | Ensure conduit installation is supported from deck over entire length
label | a801afee-275f-57d0-8aab-6aa89253712e |  | note | Where deck is post tension and steel support is minimal, use deck chairs and spare steel
checkpoint-status |  |  | checkpoint | Ensure that the void/materials are fixed securely at its final location with the correct dimensions to allow the final equipment to be installed at FFL and Adjacent to walls Floor Boxes & Cast in Light's etc
checkpoint-status |  |  | checkpoint | Ensure sufficient concrete cover can be achieved
checkpoint-status |  |  | checkpoint | Complete as installed conduit drawing showing all conduits. Photograph area of works.
checkpoint-status |  |  | checkpoint | Ensure that if the slab may be used as a floor for showers and bathrooms have an equipotential bond to the steel reinforcement.
checkpoint-status |  |  | checkpoint | Observe concrete pour with particular attention to critical area
checkpoint-status |  |  | checkpoint | Ensure that all changes made to the original drawing have been marked and noted on the Working Drawing located in the Site Office. These drawings MUST be kept updated for use as As built drawings.
checkpoint-status |  |  | checkpoint | Cross check and verify that the As Built Drawings are Complete and Correct
checklist-flat |  |  | checklist | ITP 183 Lighting Protection |  |  |  |  | Yes | ITP 183 Lighting Protection | 78189768-f160-4d18-af4e-8d108a427d71
checkpoint-status |  |  | checkpoint | Ensure that the latest revision drawings and specifications are being referred to
checkpoint-status |  |  | checkpoint | Ensure that all installations have been coordinated with other services, both new and existing underground
checkpoint-status |  |  | checkpoint | Ensure the distance of 20m between Lightning electrodes is not exceeded and that all external corners of buildings are protected
checkpoint-status |  |  | checkpoint | Ensure down conductor is installed in the most direct path practicably possible
checkpoint-status |  |  | checkpoint | Ensure all conductor sizes meets the minimum requirements as per AS 1768 Table 4.6
checkpoint-status |  |  | checkpoint | Ensure each Down Conductor is fastened securely to the engineered attachment point
checkpoint-status |  |  | checkpoint | Ensure pit is installed to correct RL's and not above other underground services
checkpoint-status |  |  | checkpoint | Ensure Buried earthing conductors meet the requirements of AS 1768 Table .6
checkpoint-status |  |  | checkpoint | Ensure the correct length earth stake is used
checkpoint-status |  |  | checkpoint | Ensure all earth conductors are correctly lugged and Identified
checkpoint-status |  |  | checkpoint | Ensure all earth conductors and fastened/clamped to the down conductor securely
checkpoint-status |  |  | checkpoint | Down Conductor Testing - Project Specific Testing Requirement
checkpoint-status |  |  | checkpoint | Ground Resistivity Testing - Project Specific Testing Requirement
checkpoint-status |  |  | checkpoint | Ensure that all changes made to the original drawing have been marked and noted on the Working Drawing located in the Site Office. These drawings MUST be kept updated for use as built drawings.
checkpoint-status |  |  | checkpoint | Cross check and verify that the as built drawings are complete and correct.
checkpoint-status |  |  | checkpoint | Verify all inspections are complete and collate records.
checklist-flat |  |  | checklist | ITP 181 Fibre Optical Cabling |  |  |  |  | Yes | ITP 181 Fibre Optical Cabling | 87849b0a-4964-4545-9aeb-aac377647d1a
checkpoint-status |  |  | checkpoint | Ensure that the latest revision drawings and specifications are being referred to
checkpoint-status |  |  | checkpoint | Ensure all test equipment including leads have been calibrated within the previous 12 months.
checkpoint-status |  |  | checkpoint | Ensure that all new installations have been coordinated with other services, both new and existing
checkpoint-status |  |  | checkpoint | Ensure pit and underground piping are clear of obstructions and have the appropriate access and barricading
checkpoint-status |  |  | checkpoint | Ensure that all new installations numbering and labelling systems meet specification and have been approved by the client
checkpoint-status |  |  | checkpoint | Prior to installation submit numbered Communications shop drawings for review to the satisfaction of services engineer
checkpoint-status |  |  | checkpoint | Ensure that the latest services and co-ordinated drawings are being referenced
checkpoint-status |  |  | checkpoint | Ensure the cable does need exceed manufacturer's bending radius and is segregated to other services as per AS S2009:2013
checkpoint-status |  |  | checkpoint | Ensure the cable pulling strength is not exceeded as per manufacturer's recomendations
checkpoint-status |  |  | checkpoint | Ensure the cable been loomed in neatly along cable pathway and has adequate service loop's at both origin and destination
checkpoint-status |  |  | checkpoint | Ensure the area for splicing has the appropriate workstation and is in a dust free environment
label | 9a330634-7abc-565e-91d8-27e169ed6899 |  | note | Cut the last 2 meters of the fibre and remove it to avoid any dirt, or damage from the hauling that may have taken place.
checkpoint-status |  |  | checkpoint | Ensure the cable is stripped using the specialised tools and remove all Gel using telstra wipes if applicable and secure kevlar rope
checkpoint-status |  |  | checkpoint | Ensure all equipment (cleaver and splicer) has been visually inspected, self checked, cleaned and regular servicing has been maintained
checkpoint-status |  |  | checkpoint | Ensure all splicing follows the correct sequence and any cut off shards are accounted for and disposed of correctly
checkpoint-status |  |  | checkpoint | Ensure fobot is securely placed inside enclosure and dust caps installed
checkpoint-status |  |  | checkpoint | Ensure that OTDR Testing is taken from both directions and at multiple wavelengths and all results are recorded with their core/cable no as per label on cabinet and latest revision drawings
checkpoint-status |  |  | checkpoint | Ensure that Light Source Testing has the correct parameters as per manufacturer and client requirements all results are recorded with their core/cable no as per label on cabinet and latest revision drawings
checkpoint-status |  |  | checkpoint | Ensure that all changes made to the original drawing have been marked and noted on the Working Drawing located in the Site Office. These drawings MUST be kept updated for use as as built drawings.
checkpoint-status |  |  | checkpoint | Cross check and verify that the As Built Drawings are Complete and Correct
checkpoint-status |  |  | checkpoint | Verify all testing are complete and collate records
checklist-flat |  |  | checklist | SYS - Drawings |  |  |  |  | Yes | SYS - Drawings | 882c088c-90bd-4781-b09d-458f0539a3b5
checkpoint-status |  |  | checkpoint | Attach Drawings
checklist-flat |  |  | checklist | ITP 171 In Slab - Works |  |  |  |  | Yes | ITP 171 In Slab - Works | 8abd0c7b-4308-4ca7-a177-bcf6b8583fde
checkpoint-status |  |  | checkpoint | Ensure that the latest revision drawings and specifications are being referred to
checkpoint-status |  |  | checkpoint | Ensure that all new installations have been coordinated with other services, both new and existing
label | 487b1d83-419d-5117-b381-5de296d75c77 |  | note | Prior to installation submit conduit shop drawing for review to the satisfaction of structural engineer
checkpoint-status |  |  | checkpoint | Ensure that the latest service & co-ordinated drawings are being referenced
checkpoint-status |  |  | checkpoint | Ensure correct datum points are identified confirm datum points with building works supervisor. Use correct set out measurement tools and equipment
checkpoint-status |  |  | checkpoint | Engage certified surveyor for critical set out works
checkpoint-status |  |  | checkpoint | Identify circuit to be installed, confirm circuit cabling requirement. Select conduit size accordingly
checkpoint-status |  |  | checkpoint | Conduit to be measured and cut using correct tools
label | be7f5afb-0c1e-5685-af55-dfebb0d475a6 |  | note | All conduit bends to be sweeping using bending spring. Or large sweeping proprietary bends
label | cccf38cc-5628-5a83-90a7-a4ed62857e53 |  | note | All joins to be glued using PVC jointing cement
label | 0d65c222-a4fa-5690-98d5-66421ec4a559 |  | note | All conduit boxes to be correct type with correct number of entry points i.e. 2way, 3way T, 4way
label | d1a71981-d002-53aa-816c-0b7914432652 |  | note | Do not use corrugated conduit in decks
checkpoint-status |  |  | checkpoint | Ensure entire conduit installation is fixed to steel work using tie wire
label | 9bba34c3-945f-5e1b-a27b-3003b5ae2c43 |  | note | Conduit should be tied to bottom mat of steel
checkpoint-status |  |  | checkpoint | Ensure conduit installation is supported from deck over entire length
label | d23e9fc4-7fc5-569a-8b24-84100aeeda15 |  | note | Where deck is post tension and steel support is minimal, use deck chairs and spare steel
checkpoint-status |  |  | checkpoint | Ensure that the void/materials are fixed securely at its final location with the correct dimensions to allow the final equipment to be installed at FFL and Adjacent to walls Floor Boxes & Cast in Light's etc
checkpoint-status |  |  | checkpoint | Ensure sufficient concrete cover can be achieved
checkpoint-status |  |  | checkpoint | Complete as installed conduit drawing showing all conduits. Photograph area of works.
checkpoint-status |  |  | checkpoint | Ensure that if the slab may be used as a floor for showers and bathrooms have an equipotential bond to the steel reinforcement.
checkpoint-status |  |  | checkpoint | Observe concrete pour with particular attention to critical area
checkpoint-status |  |  | checkpoint | Ensure that all changes made to the original drawing have been marked and noted on the Working Drawing located in the Site Office. These drawings MUST be kept updated for use as As built drawings.
checkpoint-status |  |  | checkpoint | Cross check and verify that the As Built Drawings are Complete and Correct
checklist-flat |  |  | checklist | ITP 178 Lighting Control |  |  |  |  | Yes | ITP 178 Lighting Control | 8c80a08a-c8fb-443c-a696-480bc8cf65da
checkpoint-status |  |  | checkpoint | Ensure that the latest revision drawings and specifications are being referred to
checkpoint-status |  |  | checkpoint | Ensure that all installations have been coordinated with other services, both new and existing
checkpoint-status |  |  | checkpoint | Ensure segregation is maintained pending cable insulation and shielding ratings
checkpoint-status |  |  | checkpoint | Ensure cables can communicate the specific protocols over the distances installed
checkpoint-status |  |  | checkpoint | Ensure not exceed the maximuim number of devices per group
checkpoint-status |  |  | checkpoint | Terminations have been performed according to the manufacturer's requirements
checkpoint-status |  |  | checkpoint | Test for voltage on the dali line
checkpoint-status |  |  | checkpoint | Test for Short Circuit on the dali line
checkpoint-status |  |  | checkpoint | DALI flash each individual line to confirm all lights are communicating correctly
checkpoint-status |  |  | checkpoint | Test for voltage on the communication cabling
checkpoint-status |  |  | checkpoint | Test for Short Circuit on the dali line
checkpoint-status |  |  | checkpoint | Scan communication line and confirm all devices can be programmed
checkpoint-status |  |  | checkpoint | Address all DALI drivers/light fittings with their fitting ID number and update drawings
checkpoint-status |  |  | checkpoint | Address all devices/inputs with their device ID number and update drawings
checkpoint-status |  |  | checkpoint | Setup the the relationship between devices/ inputsand light drivers.
checkpoint-status |  |  | checkpoint | Program all Touchscreens using the approved graphical interface as per the clients requirements
checkpoint-status |  |  | checkpoint | Confirm all lighting and switches functions as per the latest specification, technical submissions and drawings. This may include Dimming, Motion, Lux, timing parameters etc
checkpoint-status |  |  | checkpoint | Program Head End PC/ Control system and backup all information for future maintenance and rectification
checkpoint-status |  |  | checkpoint | Ensure that all changes made to the original drawing have been marked and noted on the Working Drawing located in the Site Office. These drawings MUST be kept updated for use as as built drawings.
checkpoint-status |  |  | checkpoint | Cross check and verify that the as built drawings are complete and correct.
checkpoint-status |  |  | checkpoint | Verify all inspections are complete and collate records.
checklist-flat |  |  | checklist | ITP 170 Cable Tray & Ladder |  |  |  |  | Yes | ITP 170 Cable Tray & Ladder | 8e860642-0b67-4b2e-a03f-1d0e0e594f85
checkpoint-status |  |  | checkpoint | Ensure that the latest revision drawings and specifications are being referred to.
checkpoint-status |  |  | checkpoint | Ensure that all new installations have been coordinated with other services, both new and existing
checkpoint-status |  |  | checkpoint | Ensure that the latest service & co-ordinated drawings are being referenced
checkpoint-status |  |  | checkpoint | Correct fixings have been used for the installation of support rods e.g. HKDs, Drop In Anchors. Fixings have been knocked in correctly with appropriate punch tool.
checkpoint-status |  |  | checkpoint | Load bearing capacity has been calculated and confirmed - PM to have cable support technical submission to confirm.
checkpoint-status |  |  | checkpoint | For any trays with a high expected load a pull test could be requested and witnessed by customer (if required)
checkpoint-status |  |  | checkpoint | Cable tray / ladder has been supported at intervals not exceeding manufacturer's specifications.
checkpoint-status |  |  | checkpoint | Seismic restraints have been installed in accordance with engineered approvals.
label | b3538510-196f-54df-b8fc-4bbb4e165dfd |  | note | Has the Seismic consultant been engaged to inspect install and signoff against their design? Inspections to be complete inline with customer ceiling signoff and construction program.
checkpoint-status |  |  | checkpoint | Cable tray / ladder has been installed at the correct height in order to coordinate with other services and ceiling heights.
checkpoint-status |  |  | checkpoint | Cable tray / ladder, which will be carrying fire rated submains, has had fire rated ladder and supports installed to manufacturer's specifications
checkpoint-status |  |  | checkpoint | All threaded rods have been cut to a maximum of 30 mm below the fixing nut on completion of installation
checkpoint-status |  |  | checkpoint | All cuts to cable/tray ladder and supports have been galvanised to prevent corrosion
checkpoint-status |  |  | checkpoint | Ensure the Cable tray has been bonded to earth securely
checkpoint-status |  |  | checkpoint | Visually inspect the cable tray/ladder run to ensure all above requirements have been fulfilled
checkpoint-status |  |  | checkpoint | Ensure that all changes made to the original drawing have been marked and noted on the Working Drawings located in the site office. These drawings MUST be kept updated for use as as built drawings.
checkpoint-status |  |  | checkpoint | Cross check and verify that the As Built Drawings are complete and correct
checkpoint-status |  |  | checkpoint | Verify all inspections are complete and collate records
checklist-flat |  |  | checklist | SYS - Documents |  |  |  |  | Yes | SYS - Documents | 9f43875b-600a-4401-b8df-2fe15db8d226
checkpoint-status |  |  | checkpoint | Attach ITP / ITC
checklist-flat |  |  | checklist | ITC 183.1 Pit Install |  |  |  |  | Yes | ITC 183.1 Pit Install | d620d999-d9ae-4c11-86c4-37d75c1177f5
checkpoint-status |  |  | checkpoint | Installed to IFC Drawing
text | fed40605-ffa8-5151-9f38-96fe730b1a55 |  | textbox | Lighting Pit Reference Number ID
checkpoint-status |  |  | checkpoint | Pit Installed Correct RL
checkpoint-status |  |  | checkpoint | Down Conductor Identified
checkpoint-status |  |  | checkpoint | Earth Stake Correct Length
checkpoint-status |  |  | checkpoint | Test Link Installed
checkpoint-status |  |  | checkpoint | All Earth Cables Clamped / Terminated
checkpoint-status |  |  | checkpoint | Earth Pit Labelled
checklist-flat |  |  | checklist | ITP 184 Lux Measurements |  |  |  |  | Yes | ITP 184 Lux Measurements | d6d42bcc-3d14-4e70-97d1-4befeb7a3520
checkpoint-status |  |  | checkpoint | Ensure that the lighting exceeds the minimum requirements and meets the design criteria
checkpoint-status |  |  | checkpoint | Appropriately set out the area in a grid
checkpoint-status |  |  | checkpoint | Visually inspect the light meter and confirm the the calibration has not expired.
checkpoint-status |  |  | checkpoint | Architectural requirements - light spill direction
checkpoint-status |  |  | checkpoint | Ensure the Light meter is pointed directly at either the light source or the viewpoint/camera in which the light levels need to be recorded
checkpoint-status |  |  | checkpoint | Ensure all readings are taken at a consistent height and at the relative intervals to the grid setout
checkpoint-status |  |  | checkpoint | Ensure the Light meter is perfectly horizontal and no shadows from the technician are covering the meter
checkpoint-status |  |  | checkpoint | Ensure all readings are taken at a consistent height (Normally 1500mm) and at the relative intervals to the grid setout
checkpoint-status |  |  | checkpoint | Record all information & verify the Minimum and uniformity requirements
checkpoint-status |  |  | checkpoint | Verify all inspections are complete and collate records
checklist-flat |  |  | checklist | ITC 175.1 In Ground Works |  |  |  |  | Yes | ITC 175.1 In Ground Works | e962f39e-a24a-4bdb-ac91-9f29136a2a2b
checkpoint-status |  |  | checkpoint | Ensure that the latest revision drawings and specifications are being referred to
text | abd6d3e5-ae04-5cb5-92b5-e167d17834ed |  | textbox | Reference and Revision:
text | d1addea9-88a2-53b8-a10f-afaccb4291b1 |  | textbox | CCT Ref:
text | 89d0bdbe-f338-59b4-a311-7a73dc245c97 |  | textbox | Pour Location (e.g. Document Gridlines):
checkpoint-status |  |  | checkpoint | No Structural Implications
checkpoint-status |  |  | checkpoint | Marked Out Correctly
checkpoint-status |  |  | checkpoint | Glued & Tied Securely
text | f8bf5f0d-5f5e-5097-864d-ec2cc2c5b700 |  | textbox | Conduit Size
text | 2056980a-2f65-5bee-b27a-e7b7ff7ad352 |  | textbox | Approx Lengths of Conduit
checkpoint-status |  |  | checkpoint | As Installed Drawing Attached
checkpoint-status |  |  | checkpoint | Conduit Ends Capped
checkpoint-status |  |  | checkpoint | Signed off by Installing Tradesman
checklist-flat |  |  | checklist | ITC 171.1 In Slab - Works |  |  |  |  | Yes | ITC 171.1 In Slab - Works | f468d52e-21e3-4bf8-b3a6-4067474e5036
checkpoint-status |  |  | checkpoint | Ensure that the latest revision drawings and specifications are being referred to
text | 9ee5fdff-7f3a-56af-a937-9a15aa750fdb |  | textbox | Reference and Revision:
text | af37a30c-4285-55dd-9fd1-2417458c6f97 |  | textbox | CCT Ref:
text | 2ec69ea9-2635-509d-9002-8d7bb1fefefc |  | textbox | Pour Location (e.g. Document Gridlines):
checkpoint-status |  |  | checkpoint | No Structural Implications
checkpoint-status |  |  | checkpoint | Marked Out Correctly
checkpoint-status |  |  | checkpoint | Glued & Tied Securely
text | e78a93cc-3672-519d-8cc7-b9f0df0dc325 |  | textbox | Conduit Size
text | c086a5b2-0fc0-5c2e-b38f-abae4f655644 |  | textbox | Approx Lengths of Conduit
checkpoint-status |  |  | checkpoint | As Installed Drawing Attached
checkpoint-status |  |  | checkpoint | Conduit Ends Capped
checkpoint-status |  |  | checkpoint | Signed off by Installing Tradesman
checklist-flat |  |  | checklist | ITP 174 Fit Off-Power, Switches & Accessories |  |  |  |  | Yes | ITP 174 Fit Off-Power, Switches & Accessories | fd49124f-050a-478f-8077-c39077f7ca55
checkpoint-status |  |  | checkpoint | Ensure that the latest revision drawings and specifications are being referred to.
checkpoint-status |  |  | checkpoint | The Updated / Superseded drawing register, located next to the drawing rack in the site office, has been checked to ensure the latest revision drawings are being referenced.
checkpoint-status |  |  | checkpoint | Ensure that all new installations have been coordinated with other services, both new and existing
checkpoint-status |  |  | checkpoint | Ensure that the latest service drawings are being referenced
checkpoint-status |  |  | checkpoint | Ensure that the latest co-ordinated drawings are being referenced
checkpoint-status |  |  | checkpoint | Ensure all required distances are kept from other services as per AS3000, e.g. in damp situations
checkpoint-status |  |  | checkpoint | Ensure the fitting is compliant with Australian standards
checkpoint-status |  |  | checkpoint | Install GPOs / Switches as per manufacturer's recommendations
checkpoint-status |  |  | checkpoint | Ensure GPOS are installed using the correct fixings and brackets
checkpoint-status |  |  | checkpoint | Ensure the correct item is being installed at each location prior to fit off (Current rating and Phases required)
checkpoint-status |  |  | checkpoint | Use fire boxes, acoustic boxes etc. where required - if in doubt check with the site manager
checkpoint-status |  |  | checkpoint | Ensure correct weather proof fittings are used where required
checkpoint-status |  |  | checkpoint | All switches and GPOs are installed in a tradesman like manner, e.g. level
checkpoint-status |  |  | checkpoint | Ensure all Sensors and PE-Cells are terminated correctly and switch the approved lights. They should also be installed in a position that will not obstruct it's ability to function correctly.
checkpoint-status |  |  | checkpoint | Ensure all ELV smart/programmable switches have been terminated with correct polarity and to manufacturer's recommendations
checkpoint-status |  |  | checkpoint | Ensure that all penetrations through the steel structure have been properly bushed before fitting off item
checkpoint-status |  |  | checkpoint | Bushing installed is not able to fall off over time
checkpoint-status |  |  | checkpoint | Penetration is sealed to prevent ingress of vermin before fit off where required.
checkpoint-status |  |  | checkpoint | Ensure that all changes made to the original drawing have been marked and noted on the Working Drawing located in the Site Office. These drawings MUST be kept updated for use as As built Drawings.
checkpoint-status |  |  | checkpoint | Visually inspect entire circuit for completeness.
checkpoint-status |  |  | checkpoint | Ensure fittings are protected if required
checkpoint-status |  |  | checkpoint | Remove all rubbish - empty boxes etc.
checkpoint-status |  |  | checkpoint | Check that all ceilings, walls and floors are left neat and tidy and without any damage. IF DAMAGE OCCURS ADVISE FREDON SITE MANAGER IMMEDIATELY
checkpoint-status |  |  | checkpoint | Cross check and verify that the As built Drawings are Complete and Correct.
checkpoint-status |  |  | checkpoint | Verify all inspections are complete and collate records