## Resources
Rich Type | Id | Warnings | type | name | values | prefix | postfix | Usage Count | User Addable | Template Name | Template Id
checklist-sectioned |  |  | checklist | ITP009-6 - Trenching and Installation of Conduits |  |  |  |  | Yes | ITP009-6 - Trenching and Installation of Conduits | 1131d335-da5d-49de-b042-3212d412520f
checkpoint-group |  |  | section | 1.0 Trenching and Installation of Conduits (Primary and Secondary)
checkpoint-status |  |  | checkpoint | 1.1 - Preparation for the Works to be Undertaken
label | a8bf76c3-fbaf-59da-8f93-ed8ec85b9beb |  | note | Frequency: Prior to start
label | 1bc665c9-5770-517e-8c5c-01f5c90cfc53 |  | note | Acceptance Criteria: Ensure survey set out is undergone, trench route marked out, excavation permit obtained and (if required) services in work(s) area isolated.
label | 97e4f183-93f6-533c-ba01-defccda22eed |  | note | Reference Documents:
label | 2ecfa2d5-5436-5b10-a9d8-690cfaaf04a5 |  | note | • Drawing set ADE-EDAU21008-YMML-DD
label | d96f1026-d33e-5b37-a540-6bfefa2d2cb1 |  | note | • ADE-EDAU21008-TB-ver2.0
label | f21e933e-ea65-5395-857d-8bc62aa32340 |  | note | • Fulton Hogan Excavation Permit
label | 0dde45ad-62ad-5544-9f11-fd0c69bb6055 |  | note | Inspection/ Test Method: Verify
label | d4e579eb-ff47-5529-9859-4fd9b949bd9b |  | note | Record of conformity: This ITP Signed / Avionics Checklist 006
label | 9efaa5a9-582f-5a42-9759-c85f6b618340 |  | note | HP*
label | 39a171fa-3777-5161-af44-5914567eac10 |  | note | Responsibility: Project Engineer
text | 7c2dd73f-2254-53b1-9624-157519a5568c |  | textbox | Date Completed:
checkpoint-status |  |  | checkpoint | 1.2 - Isolation of Services
label | 97c682e2-623e-5df3-8e0a-1661dfed614d |  | note | Frequency: Prior to start
label | 58d959d3-ba60-5045-8217-71578e9ffacb |  | note | Acceptance Criteria: Any services in the vicinity of work area(s) to be isolated to the satisfaction of the Principal and other relevant authorities.
label | 8b2252e2-a383-5e00-8837-c9e00a0f6b6d |  | note | Reference Documents:
label | b3a44652-3434-570a-9232-accf387799ef |  | note | • Drawing set ADE-EDAU21008-YMML-DD
label | 88ba4020-d42d-50c4-80d1-b14fe9326fe9 |  | note | • ADE-EDAU21008-TB-ver2.0
label | a62c3cee-33ce-53af-af23-2f0abc632597 |  | note | Inspection/ Test Method: Verify
label | 4b6391af-ec21-546c-97a7-97e867e05d4d |  | note | Record of conformity: This ITP Signed / Avionics Checklist 006
label | 18f6366d-c3f5-5702-bb0c-2bfb08b73a66 |  | note | HP*
label | e6526722-c983-5e1d-8315-dd119f064d43 |  | note | Responsibility: Project Engineer
text | 2a7991a1-b1aa-57a6-ac25-bde083f86b56 |  | textbox | Date Completed:
checkpoint-status |  |  | checkpoint | 1.3 - Trench Excavation for Conduits
label | 9be529ec-5bdf-5766-a478-251f86e6292c |  | note | Frequency: Each Lot
label | e27cc1b1-eb17-5b44-bacc-6e56f30183dd |  | note | Acceptance Criteria:
label | c4767381-5117-5582-8138-2180018c189d |  | note | • Trenches for conduits shall be excavated to the width and depth required enabling construction of the conduits to the requirements specified on the drawings.
label | b660ae22-3921-54a6-8411-4cd4bf1f38df |  | note | • The level at the bottom of the trench shall not be above the required level at any point.
label | f2fa43d4-4ac6-56dd-9649-9d1b2a81019f |  | note | Reference Documents: Drawing set ADE-EDAU21008-YMML-DD
label | ecf41a9c-80f3-5f62-b75d-95a63d24a9c5 |  | note | Inspection/ Test Method: Verify
label | 744945c9-f5bb-54be-b1db-4d6e2d3b6921 |  | note | Record of conformity: This ITP Signed / Avionics Checklist 006
label | 4eb757d7-e96c-5139-8dbd-af7bd146ba96 |  | note | IP
label | bf8fd3ef-78a1-5097-8460-3a269830db84 |  | note | Responsibility: Project Engineer
text | 45adc14f-17bc-5e78-9f27-ed9d6e663ac4 |  | textbox | Date Completed:
checkpoint-status |  |  | checkpoint | 1.4 - Laying and Jointing of Conduits
label | b902c8ab-479a-5c9f-9a55-2b2c00a6c450 |  | note | Frequency: Each Lot
label | d5637c8a-cfdf-5701-888a-9b8547001bf5 |  | note | Acceptance Criteria: Where conduit ends are not open to a pit, UPVC end caps shall be temporarily fitted to each end. Number of conduits and duct route to be confirmed for conformity with design.
label | 6aa87934-8450-53bf-b0fc-8e89faefc905 |  | note | Reference Documents: Drawing set ADE-EDAU21008-YMML-DD
label | da20fef5-3566-5cca-b14e-3d4d5f7656dd |  | note | Inspection/ Test Method: Verify
label | 246af8e9-79b9-5b0f-bdc3-70a9e870df22 |  | note | Record of conformity: This ITP Signed / Avionics Checklist 006
label | 27fcacfc-6460-5cdd-b52b-492faa275b89 |  | note | IP
label | 05c49b59-ed90-51bd-9acc-00fd440f22bf |  | note | Responsibility: Project Engineer / Site Supervisor
text | 90fd1ce9-9ea8-519e-928f-98fe28e9b86d |  | textbox | Date Completed:
checkpoint-status |  |  | checkpoint | 1.5 - Survey As-built
label | e6a07b12-012c-5224-93da-fee97fa4bb21 |  | note | Frequency: Prior to backfilling each lot
label | 47a28473-7dde-590b-85b2-37a6a9e0aabf |  | note | Acceptance Criteria: Surveyor to pick up completed conduit runs before backfill
label | 793d3b02-0ec5-5a56-8d7d-a4c7c075be89 |  | note | Reference Documents: ADE-EDAU21008-TB-ver2.0
label | b8b17962-4bdf-5e06-8f06-ddd8425cd51a |  | note | Inspection/ Test Method: Verify
label | 216b8d4a-f359-545d-994e-fbdabd8d7f9d |  | note | Record of conformity: This ITP Signed / Avionics Checklist 006 / Survey Report
label | 864cc99e-8cfb-55e1-847c-9a23e5d48157 |  | note | IP
label | 28ffdd3a-c50d-53b4-b4ae-1fba285a8db3 |  | note | Responsibility: Project Engineer / Avionics
text | 18c3c427-56af-512f-be73-ae909d0d1af5 |  | textbox | Date Completed:
checkpoint-status |  |  | checkpoint | 1.6 - Backfill Trench
label | fc9a76a4-3739-5f46-9242-c37acebe7a73 |  | note | Frequency: Each Lot
label | b1709a22-b38c-5032-9ef2-e76ccac2cc03 |  | note | Acceptance Criteria: Trenches shall be backfilled with bedding sand as per construction drawings, followed by clean fill.
label | 793efacb-ae02-52d8-a0fd-0b5e2cac964d |  | note | Reference Documents: Drawing set ADE-EDAU21008-YMML-DD
label | 8778a55f-b520-5ffb-bbb1-31d54bea86dc |  | note | Inspection/ Test Method: Verify
label | 09a6c869-f574-5925-8863-2a934cd42cdc |  | note | Record of conformity: This ITP Signed / Avionics Checklist 006
label | 1a9b94ff-6f9e-59bd-8887-af35249eff90 |  | note | IP
label | eaae054a-f251-50a4-900f-f4523a1afc8e |  | note | Responsibility: Project Engineer / Avionics
text | b4eb031e-78d9-52fe-9170-abb18db58654 |  | textbox | Date Completed:
checkpoint-status |  |  | checkpoint | 1.7 - Conduit Warning Tape
label | cf3ee805-0b35-5cac-83e7-8c4ace7ae807 |  | note | Frequency: Each Lot
label | a85e6072-9e40-52fb-a258-a3a3abb314b4 |  | note | Acceptance Criteria:
label | 8f84c85d-568f-5cee-a5e0-40181d378d85 |  | note | • Prior to backfilling to top of trench, warning tape shall be installed on top conduits, not less than 150mm wide and 0.1mm thick.
label | 1b2711db-26ac-589b-839a-faae42912fef |  | note | • They shall be orange/white in colour and bear “CAUTION ELECTRIC / COMMUNICATION BELOW” or similar repeatedly in black letter not less than 30mm high.
label | a2b092aa-f5ca-5b1c-9c5f-0f465259771a |  | note | Reference Documents:
label | d89c7be7-abb9-5949-8844-b7cceb74b2fe |  | note | • Drawing set ADE-EDAU21008-YMML-DD
label | 24b3faa6-d7d1-5a6f-9b95-b7c0b6af3eaf |  | note | • ADE-EDAU21008-TB-ver2.0
label | bc7885b7-7e08-522f-b12a-a73f357d1c3d |  | note | Inspection/ Test Method: Verify
label | 6215677c-7d05-5b96-a0ae-82fddc36f142 |  | note | Record of conformity: This ITP Signed / Avionics Checklist 006
label | d02512e9-1857-5c71-9ff5-6be4ce401c97 |  | note | IP
label | c51b5c0f-92a4-5c84-850f-e608d478aebf |  | note | Responsibility: Project Engineer / Avionics
text | 1346468e-2dd6-5d63-8c15-7493d436cdca |  | textbox | Date Completed:
checkpoint-status |  |  | checkpoint | Final Inspection
label | d9013aa4-ea59-5564-ba3a-889167ac07a9 |  | note | The signature below verifies that this ITP has been completed in accordance with the Fulton Hogan’s Quality system Procedures and verifies lot compliance with specifications.
text | b4682922-2ce7-5009-b7e2-cb6dfe086111 |  | textbox | Print Name:
text | c7c91e07-4dc1-5563-b3d9-a02959fcdbf5 |  | textbox | Position:
text | 64a65d5c-e83b-56f1-a6aa-763fe64d6729 |  | textbox | Date:
checklist-sectioned |  |  | checklist | ITP003 - Wet Lean Mix Base Course | itp |  |  |  | Yes | ITP003 - Wet Lean Mix Base Course | 21665333-a9ba-4fe1-8d21-68e73fc16b61
checkpoint-group |  |  | section | 1.0 Approval of Materials, Mix Design & Trials
checkpoint-status |  |  | checkpoint | 1.1 Approval of Mix Design
label | 9f52a682-8451-5958-a914-853988b71d08 |  | note | Frequency - Prior to the works
label | 0c2037fb-eab8-54bd-af99-086c8e0229c5 |  | note | Acceptance Criteria - Hold Point: Mix Design Submission for the supply of all component materials including coarse and fine aggregates,
label | bbb97136-2872-504b-9035-a47681dfcb15 |  | note | cement, water, admixtures, fly ash (if used), and curing materials as soon as practical and prior to commencement of works.
label | 7cc20b1c-90f9-59fa-9308-011846997551 |  | note | Reference Documents - AECOM – MAPMP Spec Clause 7.6.2 7.6.3 7.6.4
label | c7da8388-3247-518e-b736-49bb81a79e4a |  | note | Inspection/ Test Method - Verify
label | b517da1e-9611-5f48-8839-97306ce6054f |  | note | Record of conformity - Aconex / This ITP Signed
label | 6cfae682-7dd5-5444-a83c-35d67b97a075 |  | note | HP
label | 60057a26-8de0-5625-8d42-7d2133e575d8 |  | note | Responsibility - FH Engineer/ Principal’s Representative
text | ae42ec3c-ab47-5b63-918e-aae020976a2d |  | textbox | Date Completed:
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 1.2 - Approval of Materials
label | 35bebe7d-e901-549b-902f-781f1200404a |  | note | Frequency - Prior to the works
label | f6815b76-2274-50f5-bb05-6765668a2a2d |  | note | Acceptance Criteria - Hold Point: All materials used in the works are approved
label | 66f6ef6a-126e-543c-b9e3-dae62de27620 |  | note | Confirmation and approval of material Sources
label | a60f11b6-4104-56bb-a169-bb85c1e56e35 |  | note | Submit NATA certified test certificates for cement
label | 34fe33ba-15cd-5674-adf0-25a4c77c19d4 |  | note | Submit NATA certified test certificates for water of questionable quality, where required
label | 7ae18eb4-0ee6-59d2-b01b-c8b5ab4927dd |  | note | Submit Admixtures details
label | 1a92feb0-b12a-5d63-8358-218b46da79f6 |  | note | Submit Fly Ash details if used
label | 487b2ce9-1bcf-5e7c-9e1b-46842d0f3eef |  | note | Submit consolidated Material Sources
label | ee5c55ef-8d96-57b2-b624-6f0e40db84d3 |  | note | Provision of reference samples
label | ba39e962-4ea7-5778-ae14-532d36d6fba1 |  | note | Reference Documents - AECOM – MAPMP Spec Clause 7.5.2, 7.5.7, 7.5.8, 7.5.10, 7.5.11, 7.5.12.1 & 7.5.12.2
label | cc8d934d-ce01-54d4-951d-94582e60fb4e |  | note | Inspection / Test Method - Verify
label | b6748e97-43b0-5095-a54a-3128c28b749c |  | note | Record of conformity - Aconex / This ITP Signed
label | 01e44474-ae7c-57b1-b910-d0e76524eb0c |  | note | HP
label | 9527fe7c-de7e-55f5-ae2b-de8609e25007 |  | note | Responsibility - FH Engineer/ Principal’s Representative
text | 8c72e7b3-7bb9-52bf-a170-37a45a7dee63 |  | textbox | Date Completed:
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 1.3 - Production and Manufacture of materials
label | bd8c43fb-7a51-5522-90ed-f24fcc90f741 |  | note | Frequency - Prior to the works
label | f091b6bf-91a1-57af-8a55-569b55ca0860 |  | note | Acceptance Criteria - Hold Point: Supply of concrete supplier certification
label | 98db640f-81d2-5df8-b2c8-356f159c07a4 |  | note | Notification for proposed concrete batching plant
label | aa606768-9050-5025-8a6e-8ff31ea2a25d |  | note | Submission of the report on the calibration of batching and mixing plant. Any re-calibration works will be Witness point.
label | a527ca8f-9a1d-5d72-8dcd-857acc629ab2 |  | note | Mixer Uniformity tests undertaken by concrete supplier
label | 10f63867-634d-581e-a60f-bd23894cc1af |  | note | Submission of production and process control program consisting of sampling and testing the materials and product
label | 2363cad6-2819-5c78-9083-5935c11c5579 |  | note | Submit test certificates for each batch of cement provided by concrete supplier
label | 0f3d329c-ec23-5f2d-bcbd-cec943d63285 |  | note | Submit test certificates for each month for fly ash and slag delivered to batching and mixing plant provided by concrete supplier
label | 9277f2c2-fca6-5850-8d13-14b8ddb817f3 |  | note | Submit NATA certified test certificates for water provided by concrete supplier
label | e92e741a-84d1-5846-ab9b-6ffefb0d5013 |  | note | Submit test certificates for each batch of admixtures provided by concrete supplier
label | 55f00145-d528-5958-9249-4ef5a4fac7e9 |  | note | Re-submission of the production material test certificates if the source/ material is changed.
label | 285af4d7-3c71-5740-b764-e9d914f9270e |  | note | Reference Documents - AECOM – MAPMP Spec Clause , 7.8.1, 7.8.5.1, 7.8.7, 7.8.8.2, 7.8.9.1, 7.8.9.2.2, 7.8.9.2.3, 7.8.9.2.4 & 7.8.9.2.5
label | 7f75bb42-e9f3-57ed-a831-3a290cc003a9 |  | note | Inspection / Test Method - Verify
label | f815635a-6283-57f1-885e-91f9f4eadde7 |  | note | Record of conformity - Aconex / This ITP Signed
label | f10ba0ae-cce9-59f4-ab6b-f664817bfd08 |  | note | HP
label | 3e1902e2-3b4d-5dcf-a82f-ee83ec912266 |  | note | Responsibility - FH Engineer/ Principal’s Representative
text | 6a928b93-d7fb-54bc-8097-25c069aa77b5 |  | textbox | Date Completed:
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 1.4 - Production Testing
label | 3b668a78-ec6d-5539-b443-8eadaa701199 |  | note | Frequency - As shown in acceptance criteria
label | 2de45f5a-8fd8-57f1-8933-06f452f6910d |  | note | Acceptance Criteria - Hold Point: Submission of the following production test results: Aggregate Particle Size Distribution of each fraction - With each corresponding Lot submission
label | 91da8071-517d-5b8c-9afd-dee2d5c2a863 |  | note | Concrete Mix Slump - Prior to commencement of the subsequent work period
label | 9e2e8eb4-d476-5078-9caa-b82ce540934d |  | note | Concrete Air Content and Mass per Unit Volume - With each corresponding Lot submission
label | 8461aa88-06db-5ef1-ab45-d86812e143d6 |  | note | Concrete Compressive Strength (7 and 28 day Strength) - With each corresponding Lot submission
label | 18e6b822-b42d-5ec6-8cb0-ecc4bf7d6dcb |  | note | Reference Documents - AECOM – MAPMP Spec Clause , 7.8.9.4
label | 3c2114e2-72dc-5665-affe-271ab47b7b82 |  | note | Inspection / Test Method - Verify
label | ad27b983-1bbd-5a09-a686-afdbb435211a |  | note | Record of conformity - This ITP Signed
label | f7e570a7-c0d2-558c-9cb3-e058fc133a06 |  | note | HP
label | 643ccb13-12ac-56ea-994d-5370b177e1bd |  | note | Responsibility - FH Engineer/ Principal’s Representative
text | 5e355e9b-a870-5f7a-b5e8-a9fef2634704 |  | textbox | Date Completed:
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-group |  |  | section | 2.0 Prior to commencement of works
checkpoint-status |  |  | checkpoint | 2.1 - Plant and Equipment
label | d7886a37-fa1a-5468-bb56-375dc59d789f |  | note | Frequency - Prior to placement
label | d780df82-5900-55c1-9efd-f54bed306865 |  | note | Acceptance Criteria - All plant used for the works shall be adequately inducted and risk assessed. FH to verify that the plant fully complies with the requirements of this Specification, and is in full working order by the completion of a daily plant verification checklist.
label | 35ee1332-949e-5242-a0a3-60eaa337ca82 |  | note | Reference Documents - AECOM – MAPMP Spec Clause, 7.4
label | 34e52997-fbd6-51a8-8cf4-a639e0adc4e0 |  | note | Inspection / Test Method - Verify
label | 5758bfe8-c7af-5ff2-8d62-088563511167 |  | note | Record of conformity - This ITP Signed / Daily Plant Verification Checklist
label | b0742a99-2759-5233-bc28-a5ef7e0a412d |  | note | HP*
label | 26ad58cf-26f7-5fb1-b61b-a4aec341f00a |  | note | Responsibility - FH Engineer/ Principal’s Representative
text | 0a04fe98-fbf8-51dd-b7b2-68b7984712f8 |  | textbox | Date Completed:
checkpoint-status |  |  | checkpoint | 2.2 - Project Documentation / Drawings
label | d4dedda7-eb70-59af-ad0a-d9e2b49c73b4 |  | note | Frequency - Prior to placement
label | 5c89693c-2ee8-5019-9d5c-4c6d3ce353f9 |  | note | Acceptance Criteria - The latest revision of the project documentation/ drawings sent to the subcontractors and supplier.
label | 92ed5b11-1ffd-5c43-96e4-675652c01b8e |  | note | Reference Documents - IFC Drawings and AECOM Technical Specs.
label | 19159788-1c64-57ef-88bb-7f25d981cd65 |  | note | Inspection / Test Method - Verify
label | d90d390c-f740-5901-8a5e-edda5df01aff |  | note | Record of conformity - This ITP Signed
label | 8df8cd47-d36e-59ac-83d5-61deab2544ed |  | note | HP*
label | af9f603d-ebc3-54b2-a565-8858a219824f |  | note | Responsibility - FH Engineer
text | 999ee37b-fd9d-5fbc-a58c-7f046f9f9025 |  | textbox | Date Completed:
checkpoint-status |  |  | checkpoint | 2.3 - Implementation of all measures and controls
label | 4f1fb988-c309-5c11-bf2d-5432b167ee23 |  | note | Frequency - Prior to placement
label | 4646effb-3728-5561-b9c2-dba790d2a4ba |  | note | Acceptance Criteria - All necessary measures and controls are being implemented, that is: EMP, TMP, JSEA, and SWMS & WP.
label | b22c2024-6359-54af-9f7f-dac478131c1b |  | note | Reference Documents - PSP, EMP, TMP, JSEA, SWMS, WP
label | 131b7766-7a67-5f88-a5ad-cec69ef2e1e8 |  | note | Inspection / Test Method - Verify
label | 2df4b82a-17a2-5ce6-9d7d-2118b99feff1 |  | note | Record of conformity - This ITP Signed
label | 59772c2c-0f78-554e-a172-52f7b75147c4 |  | note | HP*
label | 29886ee0-1353-5ba6-9fe8-d85ced946be6 |  | note | Responsibility - FH Engineer/ Site Supervisor
text | 23048d8a-a688-5af3-8c81-18b26409bb73 |  | textbox | Date Completed:
checkpoint-group |  |  | section | 3.0 Construction
checkpoint-status |  |  | checkpoint | 3.1 - Basecourse/ Sub basecourse/ Subgrade preparation and replacement
label | e690073d-c8d9-52df-a65f-635f698decc0 |  | note | Frequency - Each Lot
label | 7c2cac76-76c4-533b-a6cd-9516c2f3cbf3 |  | note | Acceptance Criteria - Witness Point: Prior to placing wet lean mix, sub-base to be inspected and tested as per specification. All test results of the underlying layer to be provided to Contract Administrator.
label | 5aa09bad-2d1d-59ed-b30f-ee0fb729a924 |  | note | Reference Documents - AECOM – MAPMP Spec Clause, 7.9.2.1
label | 88e2cdcd-b75a-5e63-a5f1-bcfac31217a9 |  | note | Inspection / Test Method - Verify
label | c8954c9f-15a0-5ab9-8cce-8d2b1bea2d88 |  | note | Record of conformity - This ITP Signed
label | 7ca00fe8-12f8-5f92-859c-60fdc3d50f63 |  | note | WP
label | b7093908-dd68-5925-8e9c-d071a4597d9c |  | note | Responsibility - FH Engineer/ Principal’s Representative
text | f2c1ab48-b148-5a64-a577-131d341db532 |  | textbox | Date Completed:
checkpoint-status |  |  | checkpoint | 3.2 - Forms
label | f9eef76d-f821-5677-9cd0-b1bae704194d |  | note | Frequency - Each Lot
label | e1625b66-6603-510b-bf3d-83d35dbd8b5c |  | note | Acceptance Criteria - The excavated pavement perimeter is to be used as an in-situ form.
label | b7a4e8e0-6a91-59fc-8841-9d132b6b1164 |  | note | However, when required, FH to provide and use fixed forms which have been designed
label | f63e9d10-ba60-51ff-b411-0ebb18d6d90e |  | note | and constructed so that they can be removed without damaging the Wet Lean Mix Base Course and shall be of such design that they do not visibly move during placing, spreading, compacting and finishing of the cemented layer.
label | 526e293b-898b-55b5-bca7-6762c653f44b |  | note | Witness Point: The form setting must be completed at least 4hrs prior to concrete placing to enable checking by the Contractor and Contract Administrator.
label | 6fe4f0d9-f1d0-53e2-8cc0-ea7523eb36f1 |  | note | Reference Documents - AECOM – MAPMP Spec Clause, 7.9.3.1, 7.9.3.2, 7.9.3.3
label | 26bf5427-4e47-5eeb-9d41-9b95145d6b7d |  | note | Inspection / Test Method - Inspect
label | 582db13a-658b-5a3c-a858-1432fca7987b |  | note | Record of conformity - This ITP Signed
label | 327457ed-ef30-5aa1-a0a6-1e9870cb36b2 |  | note | WP
label | 09e6bbeb-b91e-5c44-8715-0b5bed9a3f94 |  | note | Responsibility - FH Engineer/ Principal’s Representative
text | 78c36f64-c356-58cc-a53f-18ff91d8e953 |  | textbox | Date Completed:
checkpoint-status |  |  | checkpoint | 3.3 - Joints
label | 2d67c925-cdc6-5511-810f-ace0a1c14931 |  | note | Frequency - Each Lot
label | f61df4e6-1d14-50be-96f8-fe2b974c63c4 |  | note | Acceptance Criteria - Wet Lean Mix Base Course will be have a maximum offset of 300mm from the overlying PCC joints where possible. Transverse construction joints shall have a minimum offset of 600mm from the overlying PCC joints where possible.
label | ccadfc99-20a6-51cc-b663-a9f038a34342 |  | note | Reference Documents - AECOM – MAPMP Spec Clause, 7.9.4
label | ba3a0fa4-dca7-5e67-ab4b-e884e553ff7b |  | note | Inspection / Test Method - Verify
label | 33433b0f-9773-5c15-888b-bbb7da2e1a62 |  | note | Record of conformity - This ITP Signed
label | 55e38d9e-3fb0-5515-9b65-c25a35fff989 |  | note | HP*
label | 82096234-456d-5230-b1e2-3946229671b3 |  | note | Responsibility - FH Engineer
text | bf1f85bc-6dda-5e04-b3bf-484337e89c49 |  | textbox | Date Completed:
checkpoint-status |  |  | checkpoint | 3.4 - Weather Limitations & Evaporation Rate
label | 16dfaab5-aa1d-5d31-8987-c8796090bcf8 |  | note | Frequency - Each Lot
label | 216c1e5c-03be-5bd9-b5db-baef9aefda8b |  | note | Acceptance Criteria - Hold Point (if required): Air temperature, relative humidity, wind velocity and concrete temperature data will be determined and recorded every 30 minutes.
label | 79bfe527-53f7-5b5d-8c02-6f1d2165ff7b |  | note | When the meteorological conditions and concrete temperature are such that the rate of evaporation from the surface will exceed 1.0 kg/m2/h, then concrete paving will cease and a transverse construction joint will be constructed.
label | 8f767531-c192-5438-9002-413dcc8cbda7 |  | note | Resumption of paving in the same work period must only occur when the meteorological conditions and concrete temperature are such that the rate of evaporation from the surface is less than 1.0 kg/m2/h.
label | 88e35bec-6274-5052-95df-c8caf79230c7 |  | note | Reference Documents - AECOM – MAPMP Spec Clause, 7.9.5.2.1
label | 8ca390b4-8f98-5154-87e8-ed45595634b4 |  | note | Inspection / Test Method - Inspect
label | 2f967341-e5c0-58ec-90e2-0918055a7117 |  | note | Record of conformity - This ITP Signed
label | 10fa51e9-f3ae-5f5d-a681-4a3d4e9f8917 |  | note | HP
label | 3a0b4bd0-5e6e-5069-8a9c-579b10b257f2 |  | note | Responsibility - FH Engineer/ Principal’s Representative
text | 7fcf1f67-4448-58ce-bcc0-58c97a467986 |  | textbox | Date Completed:
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 3.5 - Hot Weather Requirements
label | b57cf502-efb4-5a39-9a8a-a98cb1bdd2c3 |  | note | Frequency - Each Lean Mix Pour
label | 6eda2266-f1ee-5994-80e6-145fc02f2407 |  | note | Acceptance Criteria - No lean mix can be poured if ambient temperature exceeds 32°C without Principal’s Representatives approval.
label | a9cb4c5e-0453-5b68-ace1-a9e0ba2d3cb0 |  | note | Reference Documents - AECOM – MAPMP Spec Clause, 7.9.5.2.2
label | a340fd38-5ff4-5325-bd88-3bbcfd3037d2 |  | note | Inspection / Test Method - Verify
label | 2bfd1bd4-6c46-58a8-a1bd-0cd7a0eb7bd7 |  | note | Record of conformity - This ITP Signed
label | ef84260f-22b6-51dd-b580-d1b5779ee72d |  | note | HP*
label | adf24411-a360-5284-8c3e-cc23ac37c046 |  | note | Responsibility - FH Engineer
text | fef58de4-d40c-579d-ac9b-3cbff8ac7c6c |  | textbox | Date Completed:
checkpoint-status |  |  | checkpoint | 3.6 - Cold Weather Concreting
label | 0d9f0dd9-c209-5a5c-a873-4a7e108aa6f1 |  | note | Frequency - Each Lean Mix pour
label | 3e248057-beb1-52b6-a04e-4c67ca9caf4e |  | note | Acceptance Criteria - Concrete shall not be placed when the ground temperature is below 5°C Concrete shall not be placed when the temperature of the air, aggregates or water is below 10°C FH to confirm temperature on site prior to pouring.
label | bdad18e3-b65f-51d3-adc6-12fdc6c81286 |  | note | Reference Documents - AECOM – MAPMP Spec Clause, 7.9.5.2.3
label | 5ba5ea9c-59a3-5e59-8c8b-68ea229fda2f |  | note | Inspection / Test Method - Verify
label | 5a928dd5-2bd7-57c8-af9f-00be2dcbd735 |  | note | Record of conformity - This ITP Signed
label | 174da49f-cbd7-5379-8fd8-873d6bd5a3c2 |  | note | HP*
label | 2c85f33c-bd44-5128-a0ec-71ef8755b20e |  | note | Responsibility - FH Engineer
text | 88917837-d279-5df6-ac09-5e18f1e046c9 |  | textbox | Date Completed:
checkpoint-status |  |  | checkpoint | 3.7 - Concrete Sampling
label | f24a971e-81a5-55e9-95c4-2d9d041918f9 |  | note | Acceptance Criteria - Samples of mix to be taken from delivery vehicles at the point of discharge for further testing:
label | c9729b62-f547-5803-a02b-05c55daf0e05 |  | note | Slump test from each delivery truck prior to discharge, slump to be within ±15mm.
label | 3abb5f31-e2ba-5fba-982e-42c954aad22b |  | note | Air content tests from the 1st two delivery trucks prior to discharge of the mix on each lot and from each 75 m3 of concrete thereafter. Air content to be within 1% of air content for the Job Mix.
label | baef67ec-79b7-593e-9a80-7f6cd9ce24b4 |  | note | Mass per unit volume testing must be undertaken at a rate of one test per production shift.
label | 00ee6ef2-994c-51cf-ae29-cf42a4528eba |  | note | The compressive strength of the concrete produced to be measured at 7 and 28 days.
label | a9a6214c-47da-5a97-b86c-0d7f5cd1bdaf |  | note | Testing must be produced from each 75 m3 of concrete, or part thereof with a minimum of two set of testing per day.
label | 4432f239-893d-5854-b223-7ec4bae2674e |  | note | Reference Documents - AECOM – MAPMP Spec Clause, 7.8.9.3/ SAT10 Clarifications Sheet – Rev 05 Item #61
label | 537fe154-35ad-581a-aad1-60abf0020628 |  | note | Inspection / Test Method - Verify
label | 272fec44-c7d3-593d-8f52-a4a9460a869a |  | note | Record of conformity - This ITP Signed
label | 2796929a-97eb-5b0e-8b76-f47eeb71bf83 |  | note | HP*
label | 6e688fcb-5253-5625-ac64-2c98417d8a51 |  | note | Responsibility - FH Engineer
text | b2642ca9-d9da-5972-be93-c2ec5f54cca2 |  | textbox | Date Completed:
checkpoint-status |  |  | checkpoint | 3.8 - Layer Thickness
label | 65cf4c88-035b-5cec-942f-37a1aba24989 |  | note | Frequency - Each Lot
label | c9b33b64-2e6f-5639-b28a-018708c6e40f |  | note | Acceptance Criteria - Average layer thickness to be determined by difference in survey data from underlying material and top of Lean Mix. Survey thickness report provided to Contract Administrator as part of Lot submission.
label | 5e70866f-62e6-5626-a66f-cda1e28969b3 |  | note | Reference Documents - AECOM – MAPMP Spec Clause, 7.9.6
label | 7d66b964-3376-5a14-9496-f8d329aa572f |  | note | Inspection / Test Method - Verify
label | bb082fb5-428c-54c8-ab0b-5beb7a5cc938 |  | note | Record of conformity - This ITP Signed / Survey Thickness Report
label | 184e95cd-b4f6-589d-8f4a-8157f941f4e8 |  | note | SCP
label | 8706851d-5852-59cb-b102-8080cd1bd20d |  | note | Responsibility - FH Engineer
text | 32d521ce-5de8-5728-8c62-f62faf559540 |  | textbox | Date Completed:
checkpoint-status |  |  | checkpoint | 3.9 - Curing
label | 7d8d8b53-7217-5123-b9ca-14d67e6beb5a |  | note | Frequency - Each Lot
label | 492be0b4-0ccd-5226-b649-3061a2775cc7 |  | note | Acceptance Criteria - As soon as possible after finishing operations have been complete and the Wet Lean Mix Base Course has set sufficiently to prevent marring of the surface,
label | 7b6a43d8-8376-5fbf-ab73-75e370f5ee55 |  | note | the forms and finished Wet Lean Mix Base Course will be cured for not less than seven (7) days using wet cotton or hessian mats for the first 24 hours and thereafter using an impermeable liquid membrane / impermeable blankets / curing compound.
label | d8a4efa6-5a15-5db3-b43f-4137a3fea47e |  | note | Reference Documents - AECOM – MAPMP Spec Clause, 7.9.9
label | f4aa650c-97c9-5413-aa42-74b7f58f3bf9 |  | note | Inspection / Test Method - Verify
label | 76f0b05d-e4e1-566c-ade5-91e799b4c3cf |  | note | Record of conformity - This ITP Signed
label | dba9221c-d53a-5af7-a308-dde062322f2e |  | note | HP*
label | f15f52b6-eda2-502c-a714-d190bc5dd50d |  | note | Responsibility - FH Engineer
text | 26188524-7c20-54ac-98e2-a834556ab8a5 |  | textbox | Date Completed:
checkpoint-status |  |  | checkpoint | 3.10 - Levels
label | 93b0d956-5641-5310-b983-95ab4f8a7f65 |  | note | Frequency - Each Lot
label | 7ec8102c-5444-5f4c-9d79-9b8195ff30ea |  | note | Acceptance Criteria - Hold Point: Submission of record of the finished surface levels,
label | d053453b-90dc-50d0-82dc-3268be6ed293 |  | note | together with a summary indicating the magnitude of the departures from the specified finished surface levels to the Contract Administrator within the corresponding Lot submission or at a time as agreed with the Contract Administrator.
label | 7b0d2550-33ba-54d4-aa09-5bd44555a064 |  | note | Reference Documents - AECOM – MAPMP Spec Clause, 7.9.10
label | 640a5044-fb57-5e06-9bd3-83675741b885 |  | note | Inspection / Test Method - Verify
label | 37f4f71f-642d-52e8-b33d-56e55dc5a5cd |  | note | Record of conformity - This ITP Signed
label | 993458a5-fb69-5c5d-bf6c-0d906e9c5352 |  | note | HP
label | ec19cb5b-45c2-5f01-b942-90cfc059c65a |  | note | Responsibility - FH Engineer/ Principal’s Representative
text | 91a2f283-0e6d-53b9-8913-50810abb413b |  | textbox | Date Completed:
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 3.11 - Surface Smoothness Testing
label | b36cb140-894d-554f-8ab0-9093f0c94d5a |  | note | Frequency - Each Lot
label | aadf1961-e3d0-50e8-b1a3-9794a7a8c953 |  | note | Acceptance Criteria - Witness Point: The finished surface of the Wet Lean Mix Base Course shall not deviate from the testing edge of an approved 3.0m straight edge by more 7mm, except in directions where a change of grade occurs.
label | 19204407-91db-56ba-819d-20e2d01e72f2 |  | note | The surface smoothness testing will be undertaken as soon as possible after completion of the concrete pavement.
label | 60b423e3-6761-563f-af5b-6bb2d61c8c7c |  | note | Reference Documents - AECOM – MAPMP Spec Clause, 7.9.12
label | 151bd2f3-aa2f-5645-a83d-80900cebd964 |  | note | Inspection / Test Method - Verify
label | b33ac291-4c4e-5c25-af15-ae0e2ca79038 |  | note | Record of conformity - This ITP Signed
label | 4b281554-a896-5ee0-913a-d8bd6e0e65f7 |  | note | WP
label | 9d9b3998-5d75-5572-aacd-a0543bad1c1b |  | note | Responsibility - FH Engineer/ Principal’s Representative
text | 38ffd772-fc7f-5e5a-a7f9-ffccf15a5255 |  | textbox | Date Completed:
checkpoint-status |  |  | checkpoint | 3.12 - Concrete Test Results
label | 392d940d-eaf9-551a-a3ea-dd2b18d88af4 |  | note | Frequency - Each Lot
label | 37687d6c-4067-5f41-881e-8245c848bd7f |  | note | Acceptance Criteria - Lean Mix 7-day and 28-day compressive strength results determined from UCS Samples.
label | 6b5cc7a8-93dc-560d-a76d-8fe553332a13 |  | note | Submission of test results of the following: Slump test to be within ±15mm.
label | 177d5463-2a6a-5af5-8a26-29bdb2550554 |  | note | Air content tests to be within 1% of air content for the Job Mix.
label | 14c1ff67-3ec3-5fc5-9c91-439a5d5202c5 |  | note | Mass per unit volume test result
label | 5f4b3dab-a355-528a-ae83-06f5f13d2893 |  | note | The compressive strength of the concrete at 7 days to be 5.0MPa and a maximum 15MPa at 28 days
label | 59c1792a-ad25-51cb-af76-69c03984d86b |  | note | Reference Documents - AECOM – MAPMP Spec Clause, 7.9.13 / SAT10 Clarifications Sheet – Rev 05 Item #60 & #67
label | 788844b1-5f9d-545f-8eec-477d3415b097 |  | note | Inspection / Test Method - Verify
label | 23aebecc-d3d2-562c-b037-a611def9040c |  | note | Record of conformity - This ITP signed & Test Results
label | 1a803348-cde2-5098-9383-1fdfdb70dbf8 |  | note | TP
label | 6f7cff0f-a3e7-5a6c-aa0e-49be2012ce91 |  | note | Responsibility - FH Engineer
text | 223a1152-3cdb-5f0b-8742-d4333e391c53 |  | textbox | Date Completed:
checkpoint-status |  |  | checkpoint | 3.12 - Post-Construction Maintenance
label | 5a39e153-4479-5407-8b70-1863e7baba05 |  | note | Frequency - Each Lot
label | ba5c5853-c8fe-52e5-8a97-03c87da9f511 |  | note | Acceptance Criteria - Hold Point: Wet Lean Mix Base Course shall not be covered by any further pavement layer until it has been accepted by the Contract Administrator as complying with the Specification.
label | 3c6e3826-bbe2-57c1-b277-89f2ab1db8b4 |  | note | Reference Documents - AECOM – MAPMP Spec Clause, 7.9.14
label | 692dc9fe-be93-5eeb-bb01-02335f1eef9a |  | note | Inspection / Test Method - Verify
label | 87e2c0de-61f6-5487-955f-b5749dec7737 |  | note | Record of conformity - This ITP signed
label | 87c599d6-0246-59d3-9b03-a12d96b50d2f |  | note | HP
label | 2d7e1d90-d942-53ad-a9fe-c0b0f5800474 |  | note | Responsibility - FH Engineer/ Principal’s Representative
text | b7cd9b0a-b4a7-599e-944f-54cdea5601ff |  | textbox | Date Completed:
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 3.13 - Quality Assurance
label | 3742f58f-82ac-5518-b080-cf15b9db6da4 |  | note | Frequency - Each Lot
label | 66d2af81-0778-5c57-a73e-76d744873cd6 |  | note | Acceptance Criteria - Hold Point (if required): The completion of remedial works for nonconforming Wet Lean Mix Base Course shall be a designated Hold Point.
label | 64b4a5b4-c078-5b8e-a516-fe5a9e88fa29 |  | note | Reference Documents - AECOM – MAPMP Spec Clause, 7.10.1
label | 5618c545-57c3-5f7e-9bd8-5f60ccac6a3e |  | note | Inspection / Test Method - Verify
label | d5ae8a91-26e5-5826-b7f2-3b2faca3575a |  | note | Record of conformity - This ITP signed
label | 59507c98-867f-5f5a-ade7-060e3d052610 |  | note | HP
label | a8eb3171-500f-5076-9fd6-9e7302dbc69e |  | note | Responsibility - FH Engineer/ Principal’s Representative
text | 438dd645-53c3-5121-8904-0a341cac2491 |  | textbox | Date Completed:
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | Final Inspection
label | bbe8742b-738c-5506-9343-64198fd1baf5 |  | note | The signature below verifies that this ITP has been completed in accordance with the Fulton Hogan's Quality system Procedures and verifies lot compliance with specifications.
text | 3862ec6b-307d-5c57-994e-7cdab13e201e |  | textbox | Print Name:
text | 5960e863-9167-5f5e-baf8-f9fda17c4288 |  | textbox | Position:
text | 6d0aa152-09a9-54f0-aa0a-c1d005b51c8a |  | textbox | Work Completed On:
text | 38953777-bfb7-51fa-b7c3-837efa3861f2 |  | textbox | Date:
checklist-sectioned |  |  | checklist | ITP006 - Joint Sealing of Pavement Joints |  |  |  |  | Yes | ITP006 - Joint Sealing of Pavement Joints | 3f20cca1-7aef-4b3d-875f-2ee04340442c
checkpoint-group |  |  | section | 1.0 Preliminary Activities
checkpoint-status |  |  | checkpoint | 1.1 - Check for correct documentation
label | 3fb54bd5-a96d-5d74-95af-3fa20315e9be |  | note | Frequency - Prior to commencing works
label | d5523430-4b48-5563-b0e8-307d390d2f0b |  | note | Acceptance Criteria - Current revision of drawings, technical specifications and any other construction documentation is being utilised by Fulton Hogan and subcontractors.
label | 29a30c19-ec14-542d-b5d1-5649936fb771 |  | note | Current revisions of these documents to be obtained via Aconex.
label | 3d72c650-4e9a-585c-9b72-9a917b81f0a7 |  | note | Reference Documents - Current Revisions in Aconex
label | 80f81d0e-2f72-584d-aeb0-121575bbaa9c |  | note | Inspection/ Test Method - Verify
label | 5c1006b4-95cb-58ee-bf7c-010cd2dc0445 |  | note | Record of conformity - This ITP signed
label | e7f53b9b-737d-5506-b62e-24380254b38f |  | note | HP*
label | 5222b076-610e-5dc0-8ae4-b4bc5e47fdf0 |  | note | Responsibility - Project Engineer
text | e93b8c7d-d1f4-5235-a40f-fa5085ac2f6f |  | textbox | Date Completed:
checkpoint-status |  |  | checkpoint | 1.2 - Implementation of all measures and controls
label | 574e8efa-5a18-5d9f-9969-1e5991402ed1 |  | note | Frequency - Prior to commencing works
label | 40396efe-a3d2-50c8-838d-3a6ccfb6ee9c |  | note | Acceptance Criteria - All necessary measures and controls are being implemented, that is: PSP, EMP, TMP, SWMS & WP
label | af099d86-6451-5289-93a8-2bd9fa2dbe00 |  | note | Reference Documents - PSP, EMP, TMP, SWMS, WP
label | e14a24d4-cc14-5498-8da2-db7f380c51e4 |  | note | Inspection/ Test Method - Visual Inspection
label | 41ca119e-6cb2-562b-bb76-d9283fff07b3 |  | note | Record of conformity - This ITP signed
label | 96deafc2-2386-50b1-908e-5242c0cc8b0d |  | note | HP*
label | 581f7342-0f51-5151-8672-d4c844cd0901 |  | note | Responsibility - Project Engineer / Site Supervisor
text | 42d6528a-87bb-5776-a47d-646df3da4cd2 |  | textbox | Date Completed:
checkpoint-status |  |  | checkpoint | 1.3 - Submission of material specifications
label | 2de6b997-1902-5b05-9108-2422f8393228 |  | note | Frequency - Prior to commencing works
label | 747ba509-5afd-5998-a4cf-57fc241a1ff5 |  | note | Acceptance Criteria - Fulton Hogan to submit material specification for nominated Joint Sealant at least six (6) weeks prior to commencement of the works
label | fd77baec-c625-5fba-be95-3eed1696430f |  | note | The joint sealer used to seal concrete joints must be Dowsil 888 silicone joint sealant or approved alternative. It must be grey in colour.
label | 3a4ba014-beed-53b4-a6e7-46f02855d063 |  | note | The joint sealer used to seal the joint at the asphalt – concrete interface shall be Dowsil 890-SL.
label | f6626792-8165-597f-88f7-9b0bf8fa9147 |  | note | Alternative equivalent joint sealants may be accepted subject to approval by the Contract Administrator and the Principal.
label | 5c1ef995-cd28-5b21-9ef7-11fd546fb835 |  | note | Reference Documents - AECOM – MAP MP Spec. Cl 13.5.11
label | 3ee09bf8-c003-5eff-9419-a4a78eb7126d |  | note | Inspection/ Test Method - Verify
label | 7fd69a1e-9bf3-5271-a20a-aa176c586ab9 |  | note | Record of conformity - Aconex Correspondence
label | 227a5e89-5b82-5e84-aa5f-8637ef97b8f5 |  | note | HP
label | 71faa13c-d11b-533d-986d-1c4b86072adc |  | note | Responsibility - Project Engineer / Contract Administrator
label | 9a0e3bf8-d919-563c-a105-df93404193bd |  | note | Hold Pont Released as per Aconex Reference: AEC ANZ-GCOR-001183
text | 8e5c6aa2-5717-5af9-8b8c-93cec99d4bb6 |  | textbox | Date Completed:
holdpoint |  |  | signoff | Authority Holdpoint
checkpoint-status |  |  | checkpoint | 1.4 - Submission of manufacturer’s installation instructions
label | 25c1f630-2bd2-54eb-a779-6a92a6257db8 |  | note | Frequency - Prior to commencing works
label | 5a7a6fb9-d7b7-5179-ac2b-e51197870d6f |  | note | Acceptance Criteria - Fulton Hogan to submit a copy of the manufacturer’s instructions for installation of the nominated Joint Sealant at least 7 days prior to commencing installation for review by the Contract Administrator
label | c95e283e-4a03-5ba0-bffb-6c51440dcc5d |  | note | Reference Documents - AECOM – MAP MP Spec. Cl 13.10.13.8
label | 30abe7bd-5c71-5d79-beb4-d5ea7b4872fa |  | note | Inspection/ Test Method - Verify
label | b34eb5c2-33df-5094-9a76-ebe0969de35b |  | note | Record of conformity - Aconex Correspondence
label | b824fcd5-f9b5-5f03-a3cc-a6f6ac918eee |  | note | WP
label | f03bac72-e209-552e-ae8b-44b4208048d7 |  | note | Responsibility - Project Engineer / Contract Administrator
text | 270fcb55-a240-52c5-b3a9-3ab4d3d34ddf |  | textbox | Date Completed:
checkpoint-group |  |  | section | 2.0 Identifying Scope of Works
checkpoint-status |  |  | checkpoint | 2.1 - Define area of works
label | 548c9912-0c52-546c-9638-803ee71da2e1 |  | note | Frequency - Prior to commencing works
label | b4f5b8fa-a8fe-5541-8176-bea91af34328 |  | note | Acceptance Criteria - All joints shall conform to the details and shall be constructed in the locations shown on the Drawings.
label | 2ab0da8a-ffa9-5f71-b874-e8111b88eae8 |  | note | Reference Documents - AECOM – MAP MP Spec. Cl 13.10.13.8
label | c9024448-2462-55e6-8892-a7f9a65ec85f |  | note | Inspection/ Test Method - Verify
label | a661e597-c91b-511b-8f9d-0867cd0e7e7d |  | note | Record of conformity - This ITP signed
label | 537c283c-d0b0-5b82-92b9-c467d7ad356f |  | note | HP*
label | c33b78e7-3672-5bc4-b537-6c430b5a2135 |  | note | Responsibility - Project Engineer
text | 8b9128d2-5f3c-5628-ac03-69df95470e1c |  | textbox | Date Completed:
checkpoint-group |  |  | section | 3.0 Installation
checkpoint-status |  |  | checkpoint | 3.1 - Check for adequate PCC curing
label | 857ef671-8b3d-59a4-9968-712707aa2a0b |  | note | Frequency - Each Lot
label | df86e404-ea3f-532d-8b79-6f7c8231dd41 |  | note | Acceptance Criteria - Check PCC pour lots for area of works to ensure concrete has been allowed to dry and cure. At least 7 days curing should be allowed prior to sealing.
label | 20445b30-e3ce-5d13-817c-c07cac182f86 |  | note | Reference Documents - AECOM – MAP MP Spec. Cl 13.10.11.1
label | 61470e6a-5984-5f41-9be6-c5bdc6aabc23 |  | note | Inspection/ Test Method - Visual inspection
label | e762d439-704b-5fb0-b12b-b9a141094e05 |  | note | Record of conformity - This ITP signed
label | b03c80be-3634-577f-b337-9ae9c3c409dc |  | note | HP*
label | 2a6a0426-5385-50c2-a603-58d65beb2e62 |  | note | Responsibility - Project Engineer
text | 66b6f2fe-440a-5387-b17a-e872649aa7f0 |  | textbox | Date Completed:
checkpoint-status |  |  | checkpoint | 3.2 - Sawing and Chamfering of Joints
label | 36c52803-646a-5f0d-bf6c-1d0b99a13077 |  | note | Frequency - Each Lot
label | 1d5d4217-1bb2-56b3-b471-d8bd190f1989 |  | note | Acceptance Criteria - Joints are sawn to the correct width, depth and chamfer as shown in the drawings.
label | c935bbcb-7585-51d5-bacc-eff23f61c63a |  | note | Reference Documents - Design Drawings
label | 0d03b962-a301-524d-91ab-aa679b5b20e5 |  | note | Inspection/ Test Method - Visual inspection
label | e27aae2d-3e78-5d8e-87a3-848c0edc39a8 |  | note | Record of conformity - This ITP signed
label | 8d627d4c-21d5-58ba-be44-1d3a9fb4fa35 |  | note | HP*
label | c1c7c172-2d8a-5db0-83f0-6aaa1552df05 |  | note | Responsibility - Project Engineer
text | 8dbd04b2-07ce-590c-8b66-c0d372b8ed25 |  | textbox | Date Completed:
checkpoint-status |  |  | checkpoint | 3.3 Cleaning and Drying Joints
label | df9c201d-f7bf-59be-8654-e3073c1e00ce |  | note | Frequency - Each Lot
label | d4d06a46-f497-50cf-b4bc-648db617052f |  | note | Acceptance Criteria - The joint faces shall be thoroughly clean and dry prior to sealing. High pressure air blasting shall be used to clean and dry the joints.
label | e4c80765-bcb1-55ad-b170-8f5bfe397bbc |  | note | Reference Documents - AECOM – MAP MP Spec. Cl 13.10.13.8
label | 1628da97-53ae-514f-878f-7a55f74da5c3 |  | note | Inspection/ Test Method - Visual Inspection
label | 25037551-1a7f-5dbc-a5f6-d1b354a04a70 |  | note | Record of conformity - This ITP signed
label | 10942036-d2d1-58b0-a896-d120caf9316b |  | note | HP
label | 11daab29-da7f-54f3-b9da-2ad88f13db31 |  | note | Responsibility - Project Engineer / Contract Administrator
text | d4c4e949-e9c8-59dd-9b0c-36783ce2b95a |  | textbox | Date Completed:
holdpoint |  |  | signoff | Authority Holdpoint
checkpoint-status |  |  | checkpoint | 3.4 Installation of Backing Rod
label | 64107510-052d-577b-8051-251e19c58856 |  | note | Frequency - Each Lot
label | 544a48f9-46ed-5d2d-a1dd-528f838ac321 |  | note | Acceptance Criteria - Inspect backing rod to ensure it is homogenous.
label | 5ceb7565-a03f-510d-b2b8-bb9172b1af73 |  | note | Ensure the correct diameter backing rod is installed at the correct depth for each joint as specified on the drawings.
label | a37eb3cd-bdc3-5750-8423-76135ee908db |  | note | Reference Documents - AECOM – MAP MP Spec. Cl 13.10.13.8
label | efcff99c-39c7-5279-b542-dac88a3859b6 |  | note | Design Drawings
label | bb5222e0-06a5-535e-b9f2-504475f7792f |  | note | Inspection/ Test Method - Visual Inspection
label | 3e8df312-ec6d-582a-ba1f-2bef6c184c67 |  | note | Record of conformity - This ITP signed
label | 31c7bc73-7b9a-5297-bd7a-658747f4a5de |  | note | HP*
label | 898a3be6-765f-5f41-af3d-d58c79379682 |  | note | Responsibility - Project Engineer
text | 3c0cf383-9ed0-528a-bcf6-58c78b5c8054 |  | textbox | Date Completed:
checkpoint-status |  |  | checkpoint | 3.5 Installation of Sealant (Concrete-Concrete Interface)
label | 08fb4c26-f746-58c8-be0e-c950c0fa311e |  | note | Frequency - Each Lot
label | 5464b9d5-80c4-51db-b118-2e5aa9681349 |  | note | Acceptance Criteria - Ensure Dowsil 888 (or an approved equivalent) is used for concrete to concrete interfaces.
label | 57c6470f-552c-55f3-8c88-c74a8a878366 |  | note | Check that the concrete at the joint is surface dry at the time of installation of sealing material.
label | 7d1483dc-fbb9-5a29-9c75-977f4253debb |  | note | Sealant is to be tooled off to the correct recess. Excess sealant should be removed and cleaned from the surface of the concrete (excess sealant must not be reused)
label | 3d8416e5-07c3-59e7-a40a-6b370c1cf78e |  | note | Sealant to be installed by an experienced installer in strict accordance with the manufacturer’s recommendations.
label | 99c8b23c-8289-558f-aa9e-746b16225b29 |  | note | Reference Documents - AECOM – MAP MP Spec. Cl 13.10.13.8
label | 4654f6f5-8a2b-5a83-9838-2b5fb6f6412e |  | note | Inspection/ Test Method - Visual Inspection
label | 7f56c218-168e-52e8-bcf5-99ba0729c78c |  | note | Record of conformity - This ITP signed
label | f9058458-8a32-5da5-a2db-f870aff4dae1 |  | note | HP*
label | c8f440ca-e80c-5f47-a148-956f11f5bb61 |  | note | Responsibility - Project Engineer
text | c063e29c-4bd1-5585-a426-3776dff30912 |  | textbox | Date Completed:
checkpoint-status |  |  | checkpoint | 3.6 Installation of Sealant (Concrete-Asphalt Interface)
label | 19462fec-d54a-5838-b483-8efeb9a6b97b |  | note | Frequency - Each Lot
label | 96d0874e-0e04-5b27-927b-28245cfb7cb1 |  | note | Acceptance Criteria - Ensure Dowsil 890-SL (or an approved equivalent) is used for concrete to asphalt interfaces.
label | 689b6747-c6ea-5b44-9ebd-c67d05debc95 |  | note | Check that the concrete at the joint is surface dry at the time of installation of sealing material.
label | 87831fb5-c5dd-59d1-b09c-5efac4dc1e97 |  | note | Sealant is to be tooled off to the correct recess. Excess sealant should be removed and cleaned from the surface of the concrete (excess sealant must not be reused)
label | 67c623b6-5cee-5bdf-add8-75acf172abb4 |  | note | Sealant to be installed by an experienced installer in strict accordance with the manufacturer’s recommendations.
label | 40be1e36-e9c7-5d89-8df1-bbc57c739405 |  | note | Reference Documents - AECOM – MAP MP Spec. Cl 13.10.13.8
label | 8dc00f81-a8f8-5752-9f03-0346e6e3342c |  | note | Inspection/ Test Method - Visual Inspection
label | 10634b8d-950c-554a-8fee-c0428f07c1c0 |  | note | Record of conformity - This ITP signed
label | d0e5dfcd-f8a4-50bb-bcc7-f2d14f896424 |  | note | HP*
label | f83e3cf6-efb6-5ddf-b416-f5ac3456dddf |  | note | Responsibility - Project Engineer
text | f39be100-9d26-5aa3-b56e-ccbe6d52e88e |  | textbox | Date Completed:
checkpoint-status |  |  | checkpoint | Final Inspection
label | 659b3358-6343-53d7-a8e9-9ad1b68ba30e |  | note | The signature below verifies that this ITP has been completed in accordance with the Fulton Hogan’s Quality \System Procedures and verifies lot compliance with specifications.
text | 5020f214-3a1d-5179-973c-fcd2498f1cf5 |  | textbox | Print Name:
text | 930ce2d1-9eb5-543f-a584-1e68d55233d6 |  | textbox | Position:
text | 5a613cf3-bbb2-595d-a260-e11404eda00a |  | textbox | Date:
checklist-sectioned |  |  | checklist | ITP002 - Sub-Base Preparation and Replacement | itp |  |  |  | Yes | ITP002 - Sub-Base Preparation and Replacement | 5f12cc9d-aea4-4278-8acb-520d0404c0b2
checkpoint-group |  |  | section | Preliminary Activities
checkpoint-status |  |  | checkpoint | 1.1 - Current Drawings being utilised
label | f5fa85b6-9ab8-5312-846d-3d96386873c8 |  | note | Frequency - Prior to commencing works
label | b0e28632-d5c9-5f2c-bf5b-9ccafaca17ea |  | note | Acceptance Criteria - Current revision drawing is being used including the subcontractors copy.
label | 900b3812-ccaa-5d92-8928-6c96283d0752 |  | note | Current Revision to be obtained via Aconex
label | 7ddadf72-096a-54cd-97ec-4e5238f90acb |  | note | Reference Documents - Aconex
label | b6807fce-df7a-5208-b7d6-9046052011a2 |  | note | Inspection/ Test Method - Visual Inspection
label | 304ffe44-2e1a-5037-a74b-22bf0495d340 |  | note | Record of conformity - This ITP signed
label | 62df7e81-552e-5589-ab8e-888df8085bad |  | note | HP*
label | 5065c7bc-85cf-5c45-84a4-822de7a59716 |  | note | Responsibility - Project Engineer
text | 4334cc24-0c3a-5387-b183-5700ec2d19d4 |  | textbox | Date Completed:
checkpoint-status |  |  | checkpoint | 1.2 - Exclusion Zones marked out on site
label | 2b9e3e51-8c5c-5e61-8feb-cb4b6fb6fb01 |  | note | Frequency - Prior to commencing works
label | cdc21522-71c1-5cec-9aa2-11a0a41d9570 |  | note | Acceptance Criteria - Area has been surveyed, highlighting any areas where excavations should not occur (e.g. exclusion zone)
label | 091e6c23-3b82-5422-8e5d-bfc8eefee8cb |  | note | Reference Documents - Drawings, Permits
label | fa199e32-ae91-5026-86b8-48c9257d08b1 |  | note | Inspection/ Test Method - Visual Inspection
label | 4d9117b0-2876-548b-b6c7-160f3b665823 |  | note | Record of conformity - This ITP signed
label | 3a8c5c75-65a3-596c-8655-34a14d881849 |  | note | HP*
label | 852bd142-6033-51b6-8451-ea8dccd033cc |  | note | Responsibility - Project Engineer
text | d2563ed6-741f-5efb-b4e0-54fc6e5e5ec0 |  | textbox | Date Completed:
checkpoint-status |  |  | checkpoint | 1.3 - Implementation of all measures and controls
label | 61c43c43-1932-5e86-83f0-3e438f988ce2 |  | note | Frequency - Prior to commencing works
label | 65b42725-1a85-5da8-8c5a-f75f2a4ab5eb |  | note | Acceptance Criteria - All necessary measures and controls are being implemented, that is: PSP, EMP, TMP, SWMS and WP
label | a2606159-7180-5769-a714-dec30a59e661 |  | note | Reference Documents - PSP, EMP, TMP, SWMS, WP
label | e6cfcc22-54db-5e78-824a-6df2554aa9b3 |  | note | Inspection/ Test Method - Visual Inspection
label | 3eaa116e-6973-5cef-be65-d064f4802ec0 |  | note | Record of conformity - This ITP signed
label | 06c3d6b7-910b-5abb-a00e-705c4c6d015b |  | note | HP*
label | 7487f934-3899-5ced-9a09-0122ea24f8ca |  | note | Responsibility - Project Engineer
text | 80dbfdc0-22d8-549a-8610-5f526f120c46 |  | textbox | Date Completed:
checkpoint-status |  |  | checkpoint | 1.4 - Current excavation and Isolation permit has been issued.
label | a18dbe01-2ae0-5a34-b6af-f6be1f0d662c |  | note | Frequency - Prior to commencing works
label | 8f9ab22b-58f9-5af8-952f-ac17082221b5 |  | note | Acceptance Criteria - An Excavation Permit and an Isolation permit issued by Melbourne Airport.
label | 3eff4a7c-c009-5ee5-97d5-522babdf7067 |  | note | A permit to work must be obtained from JUHI when working on or near their assets.
label | 01ae6259-8db0-5e2c-b223-4e08685b0434 |  | note | Fulton Hogan Excavation permit issued to plant operators
label | e3fa6b8a-c9bc-5a4b-b8f9-a08e40fbaaf8 |  | note | Reference Documents - Excavation Permit/ Work Permit
label | 1a92fbfc-6e58-5582-b747-713667ea8061 |  | note | Inspection/ Test Method - Visual Inspection
label | 938e1045-2aac-5274-bab0-bff2d0b06be7 |  | note | Record of conformity - Permits
label | c5173753-2c72-5994-88be-e1488f8d90e9 |  | note | HP*
label | 079ab874-08be-540d-941f-92d4ff293e07 |  | note | Responsibility - Project Engineer
text | 973ecd7b-abc8-54f2-b739-914616f0fa66 |  | textbox | Date Completed:
checkpoint-group |  |  | section | Sub-Base Preparation
checkpoint-status |  |  | checkpoint | 2.1 - Removal of Existing Sub-Base Materials
label | 72d6977a-a7ff-5be8-ba9d-bbf596edbd02 |  | note | Frequency - Each Lot
label | 74479528-8000-5a9a-b73b-0c6a03b1e967 |  | note | Acceptance Criteria - FH to remove existing sub-base materials to the required depth and shape as outlined in the design documentation. This will be the underside of the new PCC pavement, and is to allow for thickenings.
label | 3819a7f3-600f-5008-a7c1-dc3e196245df |  | note | Reference Documents - Design Drawings
label | e1ece651-1da3-5332-a3bf-880dc1533d36 |  | note | Inspection/ Test Method - Visual Inspection
label | 8ce2f3bb-95f6-5386-81fa-5ade26fb8ead |  | note | Record of conformity - This signed ITP
label | 28d17f5f-9c66-5ecd-bc77-c5811d28386f |  | note | HP*
label | d9de82b4-187c-5ab6-94db-afecf2100cf0 |  | note | Responsibility - Project Engineer
text | faced1ff-3c26-5113-a6b4-f9bc90132787 |  | textbox | Date Completed:
checkpoint-status |  |  | checkpoint | 2.2 - Existing Sub-Base Material Preparation
label | ec5d97c5-0ccf-59be-b5a5-723cc8b6fc19 |  | note | Frequency - Each Lot
label | 0fdb924d-7b8a-5e2e-ab09-a500f8b7f808 |  | note | Acceptance Criteria - Where existing sub-base material is deemed to remain, the material will be trimmed and sealed off with nominated rollers, as detailed below, to achieve a dense, compacted and level surface.
label | b32064bc-d35b-54ce-b98f-22e7a3703671 |  | note | PCC1 & PCC2: Compact with 12T Smooth Drum Roller & 24T-28T Multi Wheel Roller. Proof Roll with Watercart.
label | 7fd2319a-e81a-5596-94db-8494a66b9fa2 |  | note | PCC4 & PCC5: Compact and Proof Roll with Heavy Hand Held Compactor Plates (DPU’s).
label | 74b80b6e-2d2d-53c4-aa3a-3f951ad859c6 |  | note | Reference Documents - FH-SAT10-PM-WP002
label | 57dfb729-1baa-59fc-87fb-1e3acbbb43c7 |  | note | Inspection/ Test Method - Visual Inspection
label | f5588dc1-3b37-5465-9e50-e4a37e85f721 |  | note | Record of conformity - This ITP Signed
label | d47865e5-0b50-53d9-bf1d-5ae16e4685f0 |  | note | HP*
label | eb8a67af-9c1b-5117-a3a3-8d1671ab8f96 |  | note | Responsibility - Project Engineer
text | b5294a5c-2354-55cf-ab7b-7559cc0bf444 |  | textbox | Date Completed:
checkpoint-status |  |  | checkpoint | 2.3 - Sub-Base Preparation - Testing
label | 2e855697-ec7b-57d5-a625-5ebb9740f5fa |  | note | Frequency - Each Lot
label | c0f404c2-a710-5eb5-973d-62866d821771 |  | note | Acceptance Criteria - All existing sub-basecourse material shall be inspected, tested and approved by the Contract Administrator prior to placing concrete. This will include:
label | a9dbad95-82be-5935-b032-83093b9499b7 |  | note | • Nuclear densitometer on the prepared surface material (for information only but may be used to assess if additional work is required);
label | 47f28cd5-dd79-5cec-8cd0-da969f909921 |  | note | • Dynamic cone penetrometer (DCP) test:
label | f4d08ab4-9b1b-5718-865f-1a727c96998a |  | note | o PCC1 & PCC2: Frequency of 1 per 200m2.
label | e07ab316-636f-5a5f-a4f8-8882e1be7b06 |  | note | o PCC4 & PCC5: Frequency of 1 per PCC slab.
label | ab423a1c-f666-5757-af4a-2936d9dd1d0a |  | note | • Measurement of the depth of remaining basecourse/ sub basecourse material from the prepared surface to the natural subgrade. Frequency to align with DCP testing discussed above.
label | 38915aad-06eb-5788-9070-28b61a86afa9 |  | note | All values obtained are to be tabulated by the Contractor and reported to the Contract Administrator.
label | d700df70-a23f-5d8d-8d62-ffa887f5ffda |  | note | Reference Documents - AECOM – MAPMP Spec. Cl 7.9.2.1
label | 86bce96d-1746-57ff-940d-a68bfd11ff50 |  | note | Inspection/ Test Method - Testing
label | 344b95b2-dd93-5a03-9fa9-dd223e674651 |  | note | Record of conformity - This ITP Signed, and/or Test Results
label | 2e667e2b-c7a7-5d40-b998-9e52e9f53751 |  | note | WP
label | 95a09dca-2fad-58e3-8716-9dcd0d39fc50 |  | note | Responsibility - Project Engineer / AECOM
text | 602ee8ec-c91f-5a41-ae39-fe9febf9d8b3 |  | textbox | Date Completed:
checkpoint-status |  |  | checkpoint | 2.4 - Proof Rolling
label | fd227cbc-3022-5b99-b3c5-64c42d30af11 |  | note | Frequency - Each Lot
label | 2149c4a1-acae-571b-ad2c-a04f6e4a489a |  | note | Acceptance Criteria - Commencement of Proof Rolling in any area must be a designated Hold Point.
label | 8d83e210-6ac6-5823-93f9-b36241e7ed73 |  | note | Proof rolling with the roller/watercart will commence at one edge of the area being rolled and will be executed in a systematic manner such that the entire area being rolled is uniformly subjected to the required proof rolling, such that not more than four (4) passes of a roller/watercart tyre are applied on any line before it is moved to the next line.
label | 614b8853-b09a-5359-956b-a718f41226bc |  | note | If the Proof Roll fails, the extent of the failed area is to be determined on site, and the scope of works agreed between FH and Contract Administrator.
label | 34e8beec-ca2f-5fe8-8a1b-a9bd7250be94 |  | note | Reference Documents - AECOM – MAPMP Spec. Cl 5.6.3
label | f019eb7f-573e-5ff7-83dd-543cdfbe7365 |  | note | Inspection/ Test Method - Visual Inspection
label | cec12e5e-2458-5fd3-b8bd-ee72dc1da9ca |  | note | Record of conformity - This ITP Signed
label | da825d02-1a39-5f4d-be76-3979b5a1c646 |  | note | HP
label | a15538d2-b6b2-58e6-b4cc-1bf0eba08fae |  | note | Responsibility - Project Engineer / AECOM
text | cd435558-404e-5c53-ad01-2730efe39dd8 |  | textbox | Date Completed:
holdpoint |  |  | signoff | HOLDPOINT
checkpoint-status |  |  | checkpoint | 2.5 - Visual Assessment of Sub-Base Material (where Proof Rolling cannot be completed)
label | 5660425c-8d8e-525d-b1c8-35513cb8cdd2 |  | note | Frequency - Each Lot
label | b41883a4-3c90-5adb-a7ae-9f9b9d422e35 |  | note | Acceptance Criteria - If FH considers that proof rolling is impractical in any area, FH will notify the Contract Administrator so that a visual assessment of the existing sub-base condition can be undertaken in lieu of a Proof Roll.
label | f649a016-4d70-5249-bdaa-40b1f285ddd7 |  | note | Reference Documents - AECOM – MAPMP Spec. Cl 5.6.3
label | a7a11956-07fd-509c-b55a-d499c16edfa4 |  | note | Inspection/ Test Method - Visual Inspection
label | 8c067e2a-a8dc-5d3f-8a8f-2ec601ad5e2e |  | note | Record of conformity - This ITP Signed
label | 23200a9e-88e1-5cd5-bc90-83a001f0213b |  | note | HP
label | 1cc1eee3-c3e1-5742-a57a-0b7c9397b01c |  | note | Responsibility - Project Engineer / AECOM
text | 65d5dc16-48c8-5064-b529-4b93e1050535 |  | textbox | Date Completed:
holdpoint |  |  | signoff | HOLDPOINT
checkpoint-status |  |  | checkpoint | 2.6 - Undercutting Unsuitable Material
label | 04466c9c-d303-59fb-8230-4d03d4c4e0be |  | note | Frequency - Each Lot
label | 1b6cc02b-2433-5c10-b268-4284566d5422 |  | note | Acceptance Criteria - FH will draw the Contract Administrator’s attention to any suspected unsuitable material. FH and the Contract Administrator will determine whether the material is unsuitable, and agree the extent of the unsuitable material.
label | dedc2fe4-042c-57f0-bbf3-591f1f325689 |  | note | Any subgrade material which exhibits a DCP less than 2 blows/100mm shall be deemed unsuitable as sub-grade by the Contract Administrator. However, the depth to the subgrade is also an important consideration and will be assessed by the Contract Administrator before instructing a nominal increase in thickness Wet Lean Mix Base Course.
label | d68772e0-9688-5b63-b7b6-1be4b69fa6e8 |  | note | FH will excavate unsuitable materials from such areas and depths directed by the Contract Administrator. The resulting excavation to be filled with additional Wet Lean Mix Base Course.
label | 49279a57-4ae7-5cbe-8ffa-64380d159ea4 |  | note | Reference Documents - AECOM – MAPMP Spec. Cl 7.9.2.2
label | 72ddd076-ca12-56bf-9a72-e339a23527c0 |  | note | Inspection/ Test Method - Verify
label | 8e593bd9-f69e-5376-bc46-784fdd182e46 |  | note | Record of conformity - This ITP Signed
label | 50562084-1f22-5184-93b5-37fdc52c2b0f |  | note | HP*
label | 8b74b2b1-a6fa-50bf-b017-82275f832d24 |  | note | Responsibility - Project Engineer
text | a72488e4-988c-585b-9d36-6359a1f455aa |  | textbox | Date Completed:
checkpoint-status |  |  | checkpoint | 2.7 - Survey As-Built Report
label | 526821dc-bc43-588c-b66f-a2eb4f9bdce0 |  | note | Frequency - Each Lot
label | ac7fc134-f9c5-571c-ba72-e7b027717d7c |  | note | Acceptance Criteria - FH to provide a detailed and accurate survey report of a grid spacing no greater than 5m x 5m to prove the shape and level of the basecourse/sub-basecourse/ subgrade.
label | b3ca6fb9-b218-56c9-80f6-ddfdef837fa5 |  | note | The surface tolerance at any given point of the existing sub-basecourse material is: +0, -25mm.
label | cb86a3fb-4863-573d-b72c-31576c3f938e |  | note | Reference Documents - AECOM – MAPMP Spec. Cl 6.6.6.5
label | c467d60d-2faf-546a-b943-fdc0fabebf2c |  | note | Inspection/ Test Method - Verify
label | 15e37795-6522-543a-8bf8-06050d33e9a5 |  | note | Record of conformity - This ITP Signed, and/or Survey Report
label | 066286c4-83c5-582b-a4bf-6a8f1f8dcccb |  | note | HP*
label | 5abb8349-bc11-5667-8966-0c94ec986d73 |  | note | Responsibility - Project Engineer
text | 98aab4f0-4e99-5c06-8499-181150d9d7e2 |  | textbox | Date Completed:
checkpoint-group |  |  | section | Sub-Base Replacement with FCR
checkpoint-status |  |  | checkpoint | 3.1 - Provision of Material Sources Report
label | 11212d33-8977-5489-ac96-2bfe3037c091 |  | note | Frequency - Each Lot
label | a2913ff8-bfad-5ad4-af04-d2e1caadf9fd |  | note | Acceptance Criteria - Submission of the Class 1 Crushed Rock and Class 2 Crushed Rock material sources report shall be a designated Hold Point.
label | 6d33c75a-a417-59e7-b0b3-9b9183c9f709 |  | note | Reference Documents - AECOM – MAPMP Spec. Cl 6.5.2.2
label | 39d61f5f-8e98-5e4a-8721-d617a8b9dd06 |  | note | Inspection/ Test Method - Verify
label | 4cece591-ea80-5e51-b7bf-f90c6601cf7c |  | note | Record of conformity - This ITP Signed, and/or Test Results
label | 19be5ac3-b739-57af-b043-9db776449dd4 |  | note | HP
label | 7c17bc67-f949-5678-aaee-58e77e4cf73f |  | note | Responsibility - Project Engineer / AECOM
text | cc45ef85-dc30-5db1-a5af-0c7b2498b7dc |  | textbox | Date Completed:
holdpoint |  |  | signoff | HOLDPOINT
checkpoint-status |  |  | checkpoint | 3.2 - Provision of Material Production Test Data
label | 5b8e253a-627f-5466-b235-be4457a5a8a7 |  | note | Frequency - Each Lot
label | 12d5c339-1d1c-5592-9b48-a5a9288da7cb |  | note | Acceptance Criteria - Production Sampling and Testing Data of the FCR to conform to requirements of the specification (as set out in the material sources reports), and submitted to the Contract Administrator. Results will be submitted following the delivery of the FCR products to site.
label | 480a3f2d-089b-5b03-a2b3-3f61dfdf9a69 |  | note | Reference Documents - AECOM – MAPMP Spec. Cl 6.5.2.3
label | 2c66074b-173e-51c4-a701-dae559f6fdd9 |  | note | Inspection/ Test Method - Verify
label | 361196fe-b0eb-5380-93de-09c21331dcc1 |  | note | Record of conformity - This ITP Signed, and/or Test Results
label | 506f5980-1e67-5c45-8751-59669f473303 |  | note | HP
label | 6f00850c-71d2-5ff5-94d1-6423ca1812d8 |  | note | Responsibility - Project Engineer / AECOM
text | ee3b3193-4ab5-5254-a181-153575d201ea |  | textbox | Date Completed:
holdpoint |  |  | signoff | HOLDPOINT
checkpoint-status |  |  | checkpoint | 3.3 - Preparation of Underlying Layer
label | 5d19f376-f8ee-52c6-8f12-1e79b1285d2b |  | note | Frequency - Each Lot
label | e47d2e12-5375-5ed9-b94a-a1bb61077c5b |  | note | Acceptance Criteria - Prior to the construction of any FCR layer, the previously constructed underlying layer shall be cleaned of all debris and the surface shall be inspected for compliance with the specified requirements for that layer.
label | 2300438d-155a-5cb5-bb77-8e62e7391bba |  | note | Construction of any pavement layer shall not commence until the underlying layer has been completed in accordance with the Specification. This shall be a designated Hold Point.
label | a7380e56-b141-5d57-bc0a-69a39267cedc |  | note | Reference Documents - AECOM – MAPMP Spec. Cl 6.6.2
label | 9038f683-490b-5a80-93cc-e5bce647648e |  | note | Inspection/ Test Method - Visual Inspection
label | 4e0552e6-61b0-5057-925e-0e4186320a47 |  | note | Record of conformity - This ITP Signed
label | 41b96fda-fb09-5346-a03f-b3ad0e469a91 |  | note | HP
label | edd66f51-d01f-572f-bcf9-1d8d8afeffe7 |  | note | Responsibility - Project Engineer / AECOM
text | 2b2621da-aa78-57c4-889d-e2e0d64240b5 |  | textbox | Date Completed:
holdpoint |  |  | signoff | HOLDPOINT
checkpoint-status |  |  | checkpoint | 3.4 - Placement of FCR
label | 4548402d-d4d6-511f-a3f8-7fea3a039402 |  | note | Frequency - Each Lot
label | 3a4a1dd6-ca51-567e-bb15-7f60d625396b |  | note | Acceptance Criteria - FCR Layers to be placed such that:
label | 3ae8f74d-b4a5-51a2-93eb-fd2a3b53386d |  | note | • the moisture content of the materials is within 1% of the optimum moisture content for the material;
label | e4fcd24c-4107-5ba9-8ca6-d36ca2f94241 |  | note | • the compacted layer thickness is between 100 mm and 200 mm or other thicknesses approved by the Contract Administrator.
label | f08e7f2d-3934-57c1-9971-b156930254b7 |  | note | • the underlying layers are not disturbed during placing, compacting and trimming;
label | 29584af1-fe96-546c-b93e-e8846deefb16 |  | note | • the least possible surface disturbance is necessary to obtain the design shape, grade and levels within the tolerances specified;
label | 329a004a-2fcf-5cb5-aa26-b6b939f1493a |  | note | • placement commences at the crown or high side of the pavement with each lane spread adjacent to previously placed lanes;
label | f71349c3-28d6-592f-bafb-fd18e197f0dc |  | note | • the layer is at the finished level or it can be trimmed to level, shaped and smoothed by cutting off excessive material; and
label | 570ea5f0-1953-5b01-b8b3-afc47529fe25 |  | note | • the completed layer meets the specified compaction, thickness, surface level and surface shape requirements for that layer.
label | 2c75c339-fae9-5115-8a85-84f1eb3f2412 |  | note | Reference Documents - AECOM – MAPMP Spec. Cl 6.6.3
label | e72ed7fe-8208-5caa-b190-6ad7bf733143 |  | note | Inspection/ Test Method - Visual Inspection
label | d1c99fd4-0ef6-5e67-90f0-ba75ce96d3cf |  | note | Record of conformity - This ITP Signed
label | f1cdff67-8912-58c7-92ee-f544bf3f1995 |  | note | HP*
label | 3a07ecfe-1155-55a0-ab2c-7323d4739050 |  | note | Responsibility - Project Engineer
text | ed6e534f-f424-5bcd-8d7f-bb357199d90e |  | textbox | Date Completed:
checkpoint-status |  |  | checkpoint | 3.5 - Completion of FCR Basecourse and/or Sub-basecourse
label | 4495bf79-3532-5c62-8261-fe406f6f4075 |  | note | Frequency - Each Lot
label | 91b42dd4-8d1f-55e9-8f55-da7ed039eeab |  | note | Acceptance Criteria - At the completion of each layer of FCR, the Contract Administrator must be satisfied the Contractor has achieved the requirements of the Specification. If satisfactory, the Contract Administrator shall approve the Contractor to place the next layer. This shall be a designated Hold Point.
label | 9221bae4-d744-525f-8331-d438fa0fba3b |  | note | Reference Documents - AECOM – MAPMP Spec. Cl 6.6.3
label | b6b29524-5e47-50f6-86c7-b12798cd18f9 |  | note | Inspection/ Test Method - Visual Inspection
label | f90d0ae4-334d-5de9-9615-d050b33a4c7e |  | note | Record of conformity - This ITP Signed
label | 1868a465-ffaf-559d-b0d5-98b0e9a40eb6 |  | note | HP
label | 2971390e-b30b-579c-9312-ae08de970a3d |  | note | Responsibility - Project Engineer / AECOM
text | c7b01ee2-8b47-5154-ade3-cefb3e9ee4c2 |  | textbox | Date Completed:
holdpoint |  |  | signoff | HOLDPOINT
checkpoint-status |  |  | checkpoint | 3.6 - Proof Rolling
label | b68860a8-2482-531b-8537-6268f7a8b708 |  | note | Frequency - Each Lot
label | a2629218-0959-5ea8-8806-711100af4f6b |  | note | Acceptance Criteria - Commencement of Proof Rolling in any area must be a designated Hold Point.
label | 0df17bd0-e50b-502d-a70a-2469ee8be944 |  | note | Proof rolling with the roller/watercart will commence at one edge of the area being rolled and will be executed in a systematic manner such that the entire area being rolled is uniformly subjected to the required proof rolling, such that not more than four (4) passes of a roller/watercart tyre are applied on any line before it is moved to the next line.
label | 64b5ec80-9708-556e-beb3-81d3be55df2a |  | note | If the Proof Roll fails, the extent of the failed area is to be determined on site, and the scope of works agreed between FH and Contract Administrator.
label | dd1b4402-5ce1-537d-9df7-933fff0ad036 |  | note | Reference Documents - AECOM – MAPMP Spec. Cl 5.6.3
label | c0c1ca76-dc35-58ec-b5d4-d8a1ecb16967 |  | note | Inspection/ Test Method - Visual Inspection
label | 3ddf312b-299e-5327-83f7-5ddf23d47df1 |  | note | Record of conformity - This ITP Signed
label | 94ee17a6-7d67-5e5e-83df-49d5c289c6a3 |  | note | HP
label | 3af85fa7-8ec1-5775-bd43-4d9b7ad4a77c |  | note | Responsibility - Project Engineer / AECOM
text | d385cf50-b09d-5297-b6c4-613c65c5d016 |  | textbox | Date Completed:
holdpoint |  |  | signoff | HOLDPOINT
checkpoint-status |  |  | checkpoint | 3.7 - Survey As-Built Report
label | c53c996b-855d-5d79-8187-953f1acee5e2 |  | note | Frequency - Each Lot
label | 9bb45bfb-c40b-53e2-ad94-819f7e5a91e2 |  | note | Acceptance Criteria - FH to provide a detailed and accurate survey report of a grid spacing no greater than 5m x 5m to prove the shape and level of the basecourse/sub-basecourse/ subgrade.
label | b9391f94-f21f-5a89-bce7-0400df9c4f61 |  | note | The surface tolerance at any given point of the new sub-basecourse material is: +0, -25mm.
label | e894acdf-773a-5060-93d7-44af969d0ed3 |  | note | Reference Documents - AECOM – MAPMP Spec. Cl 6.6.6.5
label | 0a70dffb-a4dd-5485-a183-94a94e998e7d |  | note | Inspection/ Test Method - Verify
label | 47aa5384-d744-55f3-9b96-ae4c93da3b2c |  | note | Record of conformity - This ITP Signed, and/or Survey Report
label | 9a9540cd-7fba-5750-a9e4-e5b59cc383e1 |  | note | HP*
label | d27f05e2-5f11-5ac3-8c88-2e1a0df53fb5 |  | note | Responsibility - Project Engineer
text | c0e93858-1ec2-5ff6-b206-e3886ab67829 |  | textbox | Date Completed:
checkpoint-status |  |  | checkpoint | 3.8 - Smoothness Testing
label | a5cdaa14-f0b6-5526-a1c6-46fb513a21a6 |  | note | Frequency - Each Lot
label | 802ea9b3-e881-5974-bd67-5caf5db50161 |  | note | Acceptance Criteria - FH to conduct smoothness testing to ensure FCR will have a surface smoothness such that, in any direction, the surface of the FCR does not deviate from a 3.5 m long straight edge, placed on the surface, by more than 10 mm when the FCR is to be surfaced with bituminous concrete and 7 mm when the surface is to receive a bituminous seal except in directions where a change of grade occurs and the requirements of the grading design make it impossible to achieve the surface smoothness requirement.
label | 7999b93f-9877-5302-878b-4222199f6de6 |  | note | Smoothness testing shall be carried out by the Contractor on completion of each section of FCR and the documented results submitted to the Contract Administrator.
label | 75a9785d-5153-5f55-aaab-793735c16f86 |  | note | Reference Documents - AECOM – MAPMP Spec. Cl 6.6.6.2
label | 156f4c49-15a2-592e-9a35-48521615b5ab |  | note | Inspection/ Test Method - Verify
label | 95054b41-af4b-5850-8952-9f13a8c3c609 |  | note | Record of conformity - This ITP Signed
label | 7e4a5f0c-3f00-5c3d-9a4c-aa0907b5fbcd |  | note | HP
label | 13b4187e-512f-5f32-99b3-77cbd58272a9 |  | note | Responsibility - Project Engineer
text | be76aef1-ecff-5395-b257-723a3e085204 |  | textbox | Date Completed:
holdpoint |  |  | signoff | HOLDPOINT
checkpoint-status |  |  | checkpoint | 3.9 - Testing
label | ed10b72e-aead-57d1-95ab-ee45393ff837 |  | note | Frequency - Each Lot
label | de9c059c-4b17-53e8-a58d-9bb47dbe37fd |  | note | Acceptance Criteria - For subgrade repairs, Class 1 Crushed Rock shall be compacted to a Mean Modified Dry Density Ratio ≥98% (modified compactive effort), and the Class 2 Crushed Rock shall be compacted to a Mean Modified Dry Density Ratio ≥95% (modified compactive effort). Compaction MMDD tested at frequency of one 3-lot test per lot.
label | 36e857bf-915e-57ad-8fec-96ee2fcef71a |  | note | Post-Compaction PSD: At the completion of compaction and proof rolling, the fine crushed rock (FCR) material must comply with the particle size distribution requirement of the specification. The particle size distribution shall be determined in accordance with the requirements of AS 1289 3.6.1. The minimum number of tests is three (3) per lot with a maximum lot size of 1000 m².
label | 119cbee0-4b06-5521-b122-452b77ba6276 |  | note | Reference Documents - AECOM – MAPMP Spec. Cl 6.1.1, 6.1.2 & 6.6.4.2
label | ec74941e-286b-577e-9b27-d0534ce073c7 |  | note | Inspection/ Test Method - Verify
label | 07683df6-75c5-55a7-8a2a-9fcd2a20135b |  | note | Record of conformity - This ITP Signed, and/or Test Results
label | 30639e89-264f-5870-a993-01a882cb31e2 |  | note | TP
label | 23d45d0f-c2c4-5dca-a73d-bd104e083d7f |  | note | Responsibility - Project Engineer
text | 65cc7f6d-075f-5f90-a05a-6a3643ec975c |  | textbox | Date Completed:
checkpoint-status |  |  | checkpoint | 3.10 - Rejected Materials
label | e846c366-62ba-5de8-9949-858be62a8af5 |  | note | Frequency - Each Lot
label | e354ad96-6db4-5d4f-9cd8-63e38a5e6e17 |  | note | Acceptance Criteria - Any fine crushed rock material which does not meet all the requirements of the Specification shall be rejected. The outcome of rejected material or works may be requested to be removed, or may otherwise be agreed to leave as is, which will be determined through the NCR process. Any materials or works that do not conform to the project specification will be raised as a Hold Point.
label | f16c8028-80d3-510d-8fb4-a52ce8a5fc14 |  | note | Reference Documents - AECOM – MAPMP Spec. Cl 6.7.3
label | d4dbc7a2-15d0-581d-89f9-d63c968a5b6f |  | note | Inspection/ Test Method - Verify
label | c61cb8c3-c800-5ca7-b511-2811cee8ac6b |  | note | Record of conformity - This ITP Signed
label | e6c4c8ac-12cf-5474-9754-059a72f429b1 |  | note | HP
label | e60f7a0e-da33-50a6-a8c4-057f7aec6a64 |  | note | Responsibility - Project Engineer / AECOM
text | 5801aae8-1b16-5fbf-9fd5-caf6612e8103 |  | textbox | Date Completed:
holdpoint |  |  | signoff | HOLDPOINT
checklist-sectioned |  |  | checklist | ITP005 - PCC |  |  |  |  | Yes | ITP005 - PCC | 8db401c7-90f3-4796-851c-4fbd91e70c9e
checkpoint-group |  |  | section | 1.0 Approval of Materials, Mix Design & Trials
checkpoint-status |  |  | checkpoint | 1.1 - Work Method & Sequence
label | d04d0219-01c8-52b2-9012-fe598c92f1d4 |  | note | Frequency - Prior to the works
label | aab26723-b181-5e56-ba9f-40860a2cf33c |  | note | Acceptance Criteria - Hold Point
label | f1b666b1-0d54-5ee9-b4b5-bee3cc0c3b1e |  | note | Submission and approval of works method and sequence of works to avoid damage to existing and new concrete slabs prior to works commencing.
label | 2895e85a-ab0a-5423-97d0-adcb9c6ae943 |  | note | Reference Documents - Clause 13.2
label | 167ae177-7b8a-5451-a952-e02994c9ad9a |  | note | Inspection/ Test Method - Verify
label | f195d926-e634-5a06-978b-b26c0a3a2146 |  | note | Record of conformity - Aconex
label | 20e9aa19-e1a5-57e2-883e-4a7f78c1f658 |  | note | HP
label | 2a67358e-752c-57e9-9624-e5e46a2da331 |  | note | Responsibility - Engineer/Principal’s Representative
text | b86ba19d-d9e8-52f4-b914-7fdd7f5ce0cd |  | textbox | Date Completed:
holdpoint |  |  | signoff | Authority Holdpoint
checkpoint-status |  |  | checkpoint | 1.2 - Approval of Material Submissions
label | 5c49f1f5-780e-5a0c-b31a-c2b0062b9f2d |  | note | Frequency - Prior to the works
label | d6424f75-9fcb-5f01-955f-244613abf27f |  | note | Acceptance Criteria - Hold Point
label | 5af271fa-0b6d-5163-be30-e1c8d8e112d9 |  | note | All materials used in the works are approved
label | 15aa948e-64e9-5c5a-adf8-092c6b2b2130 |  | note | · Confirmation and approval of material Sources
label | 2e87a09a-141a-5456-9bf6-2d64b0357b08 |  | note | · Submit NATA certified test certificates for cement and flyash
label | f2322da9-27eb-5196-9353-82747e86ab8c |  | note | · Submit NATA certified test certificates for water
label | dc629d0e-01fa-5078-994b-b0731f2ccc89 |  | note | · Submit Admixture details
label | 5c7a2132-70a8-50ff-a12a-2071ea418078 |  | note | · Submit Curing Materials and methodology
label | 11025c1e-f7fc-58b2-bb7c-dc8ae14982bb |  | note | · Submit test certificates for nominated dowel bars
label | e27fa1e6-b600-5a73-a2af-d7e0d407c71a |  | note | · Submit material specification for nominated Epoxy Grout and joint sealant
label | d8906c85-add0-52a3-a5f9-d230d972d46e |  | note | · Submit consolidated Material Sources Submission
label | e9a45416-3f0f-5c9c-b738-aada34dbb833 |  | note | · Submission of reference samples (incl. 50kg ofaggregate)
label | 7b37cf75-1d12-5a2b-8e66-085715bcbea5 |  | note | Reference Documents - Clause
label | f391065b-dbde-5857-9519-80628342f26e |  | note | 13.5.2.1
label | 77bee696-b229-5295-a68e-5f9c39995bce |  | note | 13.5.3
label | 392aa500-d822-51d1-acc0-1240d6b1cedc |  | note | 13.5.4
label | c3058f59-036e-5ccc-abee-79dfb72ba17e |  | note | 13.5.5
label | 073dd9d9-d100-56d7-987b-82a6092ad085 |  | note | 13.5.6
label | ba14d973-aa54-5aa6-b4cf-c1f771a89b6d |  | note | 13.5.7
label | bb7eaea4-afcc-562a-ba21-ce680b01d964 |  | note | 13.5.9
label | 47356cda-a4fa-5340-a072-bf4219a62e27 |  | note | 13.5.11
label | a8420283-fcee-5c8e-ae41-0fc823a49268 |  | note | 13.5.12
label | 81d62791-5aad-5e55-8259-acd532dcb4c5 |  | note | 13.5.13.1
label | a22911fd-0304-52f8-a758-47f315907c7f |  | note | 13.5.13.2
label | f84c480a-8262-5370-8061-b729370c8d0c |  | note | Inspection/ Test Method - Verify
label | 845419cd-718a-58ea-bcbb-a81a4fd20e75 |  | note | Record of conformity - Aconex
label | a05bda89-307b-5a85-8e88-c7d9feccb2d6 |  | note | HP
label | fc6fb9a9-41d3-5352-bb55-c251e8345792 |  | note | Responsibility - Engineer/Principal’s Representative
text | 233628d6-8b1f-582c-8803-8ee632b5eb68 |  | textbox | Date Completed:
holdpoint |  |  | signoff | Authority Holdpoint
checkpoint-status |  |  | checkpoint | 1.3 - Approval of Mix Design & Submission
label | 49684c77-59b0-57a0-aaa0-ff8ed1a4ed40 |  | note | Frequency - Prior to the works
label | db3110f2-964b-5a24-987c-1515b816b6e7 |  | note | Acceptance Criteria - Hold Point
label | c55cab29-c6ff-5d97-92e3-3e7a6a737c85 |  | note | · Submit Contractors construction procedure
label | 90c1eae1-705a-5982-8725-53e4ed859dfa |  | note | · Submission and approval of Mix Design
label | 19f72682-9064-5537-bc07-2c2f505283ea |  | note | · The Contract Administrator’s acceptance of the concrete mix design report
label | cb1eee0a-612f-5c30-9e0c-a4757b74757c |  | note | · Submission and approval of the Job Mix
label | 6acef122-30b9-5303-ae04-0e8723db5220 |  | note | · Supply of concrete supplier certification
label | 14acf67a-ac02-5f5b-b6c5-ed5607ff620a |  | note | · Submission and approval including receipt of calibration report
label | 30dc4df8-d1d8-562d-8cc6-f6f7fe7dd204 |  | note | Reference Documents - Clause
label | daa10532-f3d6-51c0-a2d8-72440a0b1adb |  | note | 13.6.2
label | 9ae25dfc-f5f8-5ae7-8f47-10987807d915 |  | note | 13.6.3
label | bdd773f4-481c-5724-9d8c-f2f9de9aee4d |  | note | 13.6.4
label | 734b0f59-73ca-5028-8517-4deb50e6c771 |  | note | 13.8.4.1
label | 23329002-4911-5ecd-8b0c-f9a610b68396 |  | note | 13.8.6
label | d9ae7164-54e0-502d-820b-1bcce544ffab |  | note | Inspection/ Test Method - Verify
label | edd1c435-c0b6-5285-baf4-b3458c5414ca |  | note | Record of conformity - Aconex
label | 576157d3-f722-5b5c-8da8-0115c8ef0d6b |  | note | HP
label | 694b4888-f260-5e3b-9868-da6782aec0a1 |  | note | Responsibility - Engineer/Principal’s Representative
text | 729e490a-b91d-5319-b22b-00d797e44042 |  | textbox | Date Completed:
holdpoint |  |  | signoff | Authority Holdpoint
checkpoint-status |  |  | checkpoint | 1.4 - Production Testing
label | 52ddc9b8-2150-599f-be0b-28a6bf64336f |  | note | Frequency - As shown in acceptance criteria
label | dfb0fd05-9000-5b24-a91e-af281eae43b9 |  | note | Acceptance Criteria - Hold Point
label | 8ba6de2c-b65e-5cf7-b478-7be363764bb2 |  | note | Submission of:
label | 7678c727-330f-5a68-91f0-86e66b135929 |  | note | · Job mix production tolerance
label | 506c1f12-828b-5003-914d-15bf59bad0f0 |  | note | · Concrete plant process control system
label | 59eb0e35-390a-5384-b0d5-5055c3ea5e31 |  | note | · Test certificates for each batch of cement used inconcrete production
label | a883b072-76fa-5028-bb21-4898f6cccd6a |  | note | · Test certificates for water used in concreteproduction
label | e1499b26-f30f-5e29-b97c-5c2bf24161cc |  | note | · Test certificates for each batch of admixtures usedin concrete production
label | fb865327-1c44-581f-a1f1-48fa2fa772f7 |  | note | · Production test results
label | 15a5b64b-d40b-5907-a029-8c322753f290 |  | note | Reference Documents - Clause
label | 9c5df750-8ca6-5ebb-8d00-0935427054cd |  | note | 13.8.7.3.1
label | cf10cd35-b4e5-52ea-8260-603a658b78d6 |  | note | 13.8.8.2
label | ed1c1de3-6de6-5bd5-af2d-7bc85c9a54f9 |  | note | 13.8.8.3.3
label | d7cb3755-c1dd-562c-b3c5-f76c62f0d0cf |  | note | 13.8.8.3.4
label | 1667328b-c2fe-5849-aed4-01786f66ad4c |  | note | 13.8.8.3.5
label | 528aaa26-4f71-5acd-9b03-77031a3a1a0a |  | note | 13.9.3.7
label | a54fa5dc-e59e-5a76-aa72-b94d2506cf24 |  | note | Inspection/ Test Method - Verify
label | 916c5104-e102-5d62-948a-b1ba405f924a |  | note | Record of conformity - Aconex
label | 3496ebd9-ffa1-5b05-8e63-42191c974007 |  | note | HP
label | 760277b1-b8fb-5cbb-b637-a5f9851188f8 |  | note | Responsibility - FH Engineer/Principal’s Representative
text | 5493f287-4222-5f81-b268-38a0509ffab2 |  | textbox | Date Completed:
holdpoint |  |  | signoff | Authority Holdpoint
checkpoint-group |  |  | section | 2.0 Prior to Placing
checkpoint-status |  |  | checkpoint | 2.1 - Project Documentation/Drawings
label | 288a8e9d-167f-50a3-83dc-9ce2569b468d |  | note | Frequency - Prior to concrete pour
label | 0933587d-9cd4-507f-a305-797def8a21f1 |  | note | Acceptance Criteria - The latest revision of the project documentation/drawings sent to the subcontractors and reo supplier.
label | 15c8c194-d07e-5265-be08-79c12c2bab84 |  | note | The latest revision of the project documentation/drawings is being used on site (check the drawings register)
label | af094872-1577-580a-9744-7eaa7dca4c64 |  | note | TMP and EMP in place for pour.
label | 7eca64e6-362a-552b-9f7a-f1142a723a9c |  | note | Reference Documents - Drawing and drawing registers
label | af14574b-03f7-5ba3-b02b-be02edb97f08 |  | note | Inspection/ Test Method - Verify
label | 4f9d3806-d31c-5a64-860d-87ea6d5eeded |  | note | Record of conformity - Up to date drawing sets and this ITP signed
label | 3cbab383-6380-5b2c-a20a-65679508cf6f |  | note | HP*
label | fadbd1f5-6e02-5004-b322-6ea90e904702 |  | note | Responsibility - Engineer
text | 2e1778f6-7849-5ea8-9409-733a332ae902 |  | textbox | Date Completed:
checkpoint-status |  |  | checkpoint | 2.2 - Implementation of all measures and controls
label | de656fef-5122-5421-80dd-f4036b7efc29 |  | note | Frequency - Prior to concrete pour
label | d4036abe-41d4-544e-966b-f9e3277d8b47 |  | note | Acceptance Criteria - All necessary measures and controls are being implemented, that is: PSP, EMP, TMP, JSEA, SWMS & WP.
label | 30b0b9eb-27c8-586d-93c6-4a0a5dc7d9dc |  | note | Reference Documents - PSP, EMP, TMP, JSEA, SWMS, WP
label | a5e07324-9cc4-5514-88cb-be3c9e9b4611 |  | note | Inspection/ Test Method - Verify
label | dd997077-aac3-5e1f-955e-200ce0fc7690 |  | note | Record of conformity - Site and Office Inspection
label | e658c28d-de32-519b-8d80-df62ec7237be |  | note | HP*
label | 06a000bf-3fe2-5de6-a8e7-29481b3a4d6d |  | note | Responsibility - Engineer/ Site Supervisor
text | 414c86e1-e956-5ed5-b689-4ec1cf1367d2 |  | textbox | Date Completed:
checkpoint-status |  |  | checkpoint | 2.3 - Definition of the work area (survey)
label | 4cee4bbc-4fc8-5e5e-8b94-525b56c9d961 |  | note | Frequency - Prior to concrete pour
label | 62cd9d60-6d10-5c25-a853-24114e44b133 |  | note | Acceptance Criteria - Work area has been cleared and surveyed (marked on site)
label | 1e08563e-e9fc-50c7-ab35-6f13b3cad7b9 |  | note | Reference Documents - Drawings
label | 1265589a-1908-5613-9500-7aebfd9a95c4 |  | note | Inspection/ Test Method - Verify
label | 8cfc48ac-1d6c-5fe0-a7c6-d8d70fa6d376 |  | note | Record of conformity - Site Inspection
label | 67a4e9ba-d46d-5f24-8f1c-302742a0e188 |  | note | HP*
label | 44193d1f-b663-5f24-970f-ea61102d6682 |  | note | Responsibility - Site Supervisor/ Surveyor
text | 6af88ebc-5ba2-592d-b49c-d9ef772eb323 |  | textbox | Date Completed:
checkpoint-status |  |  | checkpoint | 2.4 - Construction Procedure
label | f75b7a87-04fe-5311-829f-09b7f4f3d82c |  | note | Frequency - Prior to Concrete pour
label | 6ce73b68-9298-5ec3-9826-e226731ed954 |  | note | Acceptance Criteria - Hold Point
label | 1a3ad0a1-18d4-56de-a24f-6da1544e44e2 |  | note | Submit contractor’s construction procedure
label | 1ab68d2a-4d7b-5ea1-a13d-dc896ae6f4fb |  | note | Reference Documents - Clause 13.10.1
label | efc8ff8e-d660-51c0-a0a7-6936f3294eb2 |  | note | Inspection/ Test Method - Verify
label | 4ca39714-531e-576e-a7c9-35cf085a6fba |  | note | Record of conformity - Aconex
label | d8b18f71-6d6b-5cf8-bb00-4d6b71faaba4 |  | note | HP
label | 94f90bc6-f159-51b3-93a7-35e461bec05a |  | note | Responsibility - Engineer/Principal’s Representative
text | d2f669de-aac3-5daf-9234-55e2eafdfb35 |  | textbox | Date Completed:
holdpoint |  |  | signoff | Authority Holdpoint
checkpoint-status |  |  | checkpoint | 2.5 - Placement Plan
label | 01aa0a20-ddad-5ffb-8164-e6842373d237 |  | note | Frequency - Prior to Concrete pour
label | 054f5667-7bf8-5150-8ef3-89da2c0dd474 |  | note | Acceptance Criteria - Hold Point
label | 52241108-372c-551f-ac3f-f6b0540b171b |  | note | Submit Pour Plan for review
label | 9cc87931-4943-5e72-a143-d6a04ae2db69 |  | note | Reference Documents - Clause 13.10.2
label | 948040ac-0c5d-52ca-a5ac-4e7815614f42 |  | note | Inspection/ Test Method - Verify
label | f1d36d5f-c1b8-5f8f-afe1-81d1e24ff65e |  | note | Record of conformity - Aconex
label | c1ab8c6b-0d4f-5b45-84c9-64ba0d5673f9 |  | note | HP
label | 532132d9-1289-56aa-9f95-b80bcd7a5aea |  | note | Responsibility - Engineer/Principal’s Representative
text | 70ab2a02-2890-56c9-94ec-0705488e92e9 |  | textbox | Date Completed:
holdpoint |  |  | signoff | Authority Holdpoint
checkpoint-group |  |  | section | 3.0 Construction and Formwork
checkpoint-status |  |  | checkpoint | 3.1 - Base Inspection
label | ef63d436-abf5-5698-a872-6e02e5d59313 |  | note | Frequency - Prior to Concrete pour
label | 2356d53e-c553-56d1-8bd4-29d94d49681a |  | note | Acceptance Criteria - Witness Point
label | c61b45cf-0c66-5a5a-be5f-2eb31e4b48a7 |  | note | Ensure that the finished surface of the sub grade has been surveyed and is to level. ITP002 has been completed. Ensure Principal's Representative conforms base is satisfactory.
label | 5835a5c8-345c-54fc-9a1a-eaf1e1338138 |  | note | Reference Documents - Clause 13.10.5.1
label | aa5f8313-52ba-5e91-b517-2a16e65441f4 |  | note | Inspection/ Test Method - Verify
label | 8ad71d64-de06-5237-95d6-0e22df04c232 |  | note | Record of conformity - Site Inspection, ITP002
label | de41f2f4-dfd0-5adc-ae45-04ddea2afdf4 |  | note | WP
label | 8ee9de71-e8ab-51f4-947d-89f630d22ad0 |  | note | Responsibility - Engineer/ Principal’s Representative
text | 22120b4d-dfc2-5f81-b35e-2e49527811c5 |  | textbox | Date Completed:
checkpoint-status |  |  | checkpoint | 3.2 - Formwork Installation
label | e4bcee47-3302-5f0d-b1ea-7a8b6dd45357 |  | note | Frequency - 4 hours Prior to Pour
label | 9d6950bb-9e6b-56ec-97ed-2197cdec15ba |  | note | Acceptance Criteria - Witness Point
label | 99b871cc-9b06-5f0f-8d27-c4da0d93c702 |  | note | Rigid, watertight, braced and tied together as to maintain shape during all construction activities.
label | f13a196c-e107-5e6a-99b3-0dbda65f328d |  | note | Forms must be free from warps, bends and kinks.
label | 68e76ec0-583c-53f8-a948-ae431a7504f2 |  | note | Formwork has been surveyed and is to the required level.
label | f797c8ce-9820-51e9-87ef-d429a7fdf05f |  | note | Reference Documents - Clause 13.10.4
label | a4ca442a-7905-5410-87b4-5c6071a8e046 |  | note | Inspection/ Test Method - Inspect
label | c4710b5b-aad1-5ccc-9f32-23561b3b5172 |  | note | Record of conformity - Site Inspection
label | c4ab1ae7-5461-5b71-aa44-dd248e671d34 |  | note | WP
label | 7574d71a-03d0-5c7e-85dd-a638124dc642 |  | note | Responsibility - Engineer/ Principal’s Representative
text | 0a6d0493-7e61-5da7-92db-43d63e351a33 |  | textbox | Date Completed:
checkpoint-group |  |  | section | 4.0 Pre Pour Planning and Inspections
checkpoint-status |  |  | checkpoint | 4.1 - Reinforcement Inspection
label | f3c21768-f1ec-5ae4-9afc-225a13f9fa72 |  | note | Frequency - Prior to concrete pour
label | cfea3867-da44-5a23-b3b7-4bcfc43fef7a |  | note | Acceptance Criteria - Witness Point
label | ef76f86b-1cab-522d-a42a-d2f9b4ae04b6 |  | note | Verify plant fully complies with the requirements of the Specification and is in full working order.
label | b928bfaa-e4a8-5c58-87cc-9d23849520bf |  | note | Reference Documents - Clause 13.4.1
label | 7f84312c-d0d1-5cf4-bc17-5089ab787c6e |  | note | Inspection/ Test Method - Inspect
label | e03edc85-874d-5a87-bcb5-a53e7d1ba5a3 |  | note | Record of conformity - Site Inspection
label | 49a1859e-7980-5bc6-99df-00d5f6f14fda |  | note | WP
label | 89feb6ec-0d3e-53cc-a9bf-f154803b859a |  | note | Responsibility - Engineer/ Principal’s Representative
text | 893ed25d-6245-5ecf-9c8c-ff6de3229592 |  | textbox | Date Completed:
checkpoint-status |  |  | checkpoint | 4.2 - Formwork Inspection
label | 8769569c-550e-581b-94bc-c736161dfacb |  | note | Frequency - Prior to concrete pour
label | 58f4a3cb-d605-576e-9ac1-6fbd1c2bab82 |  | note | Acceptance Criteria - Hold Point
label | b07762fd-6e58-5fc8-916b-abe1caa7f8e6 |  | note | Inspection of formwork at least one day prior to the commencement of works
label | 77a2f96f-2df7-54a6-8555-377c48a848b5 |  | note | Reference Documents - Clause 13.4.2.1
label | a729efa1-f7d0-5eba-96d0-074b6a4201f8 |  | note | Inspection/ Test Method - Inspect
label | dfb34899-699d-5906-b1c4-445a3fc3c730 |  | note | Record of conformity - Site Inspection & CL009A
label | 805ac799-1c3a-527f-b0fc-7062bb8f189d |  | note | HP
label | b46f32bc-3235-5b70-8ec6-2990c4db3c02 |  | note | Responsibility - Engineer/Principal’s Representative
text | 8f3622e1-8e61-55e4-ac5c-b611f5b4bb58 |  | textbox | Date Completed:
holdpoint |  |  | signoff | Authority Holdpoint
checkpoint-status |  |  | checkpoint | 4.3 - Reinforcement Inspection
label | bda8e1f7-c48e-5758-bf1d-13723b680bb5 |  | note | Frequency - Prior to concrete pour
label | ddf5744e-3910-5c89-9fe3-7272dd027f69 |  | note | Acceptance Criteria - Pre-pour Checklist Completed:
label | 02881f53-feec-5bf1-8c2a-f2b82304f2b4 |  | note | · Position and spacing check and recorded
label | bb26e34d-8c83-540a-812e-7752ab847a64 |  | note | · Cover checked and recorded (top 100mm +/-10mm, joints 50mm +/- 10mm)
label | bcdb39c9-0504-5754-92fc-6a5899ecb9c8 |  | note | · Reinforcing supports checked and recorded
label | b7506f82-d159-51a5-a9c3-f404a11b0957 |  | note | · Reinforcement overlapping by 300mm orsecurely fastened to prevent separation
label | 159faf66-4df4-59d1-aa3a-e16411527586 |  | note | · Reinforcement shall be free from mud, oil andother organic matters
label | 14d6a98b-b0bb-5105-9b1b-ab9ba490b478 |  | note | Reference Documents - Clause 13.10.8
label | 4c030a75-594c-5c9b-95cf-af3c8ce4b07d |  | note | Inspection/ Test Method - Inspect
label | 41ceccc5-ed82-577e-9d59-c65feb6ace25 |  | note | Record of conformity - Site Inspection & CL009A
label | 23273ac2-4fcc-5f91-a8db-9d16dec70cf5 |  | note | HP*
label | deacfafd-01f0-558d-acc2-e5ff380c76d2 |  | note | Responsibility - Engineer
text | 09b31c8a-70aa-574b-b58f-4a4e0997ac18 |  | textbox | Date Completed:
checkpoint-status |  |  | checkpoint | 4.4 - Stringline and tape measure checks
label | 6ce42b30-cfde-5eeb-9e45-aed9cf40c25a |  | note | Frequency - Prior to concrete pour
label | 4d55d399-0e9f-5029-9029-dcc7b0a753bd |  | note | Acceptance Criteria - The base of the pour shall be tested via stringline and tape measure to investigate correct depths & shall be corrected as necessary.
label | 7d978069-e6cc-5f62-b120-0d406f5702ee |  | note | Reference Documents - Clause 13.10.5.3
label | 2362bbef-c9cd-5c57-b00b-d227e7a20953 |  | note | Inspection/ Test Method - Verify
label | 77560ed4-68a2-543c-a321-94866bdc6d3b |  | note | Record of conformity - Site inspection and this ITP signed
label | 555aa647-f2bd-5e95-aa55-e952e207cd04 |  | note | HP*
label | 432e5d4a-b60d-5828-b0cd-b399f29e00f0 |  | note | Responsibility - Engineer
text | e0f9725e-f99e-5867-b4f0-e2ce38e55f30 |  | textbox | Date Completed:
checkpoint-status |  |  | checkpoint | 4.5 - Pre-pour inspection
label | 58c42ad7-bc6b-5a53-bed5-33ac148c3010 |  | note | Frequency - Prior to concrete pour
label | 42b3514d-9b35-5fe6-81d9-2c82836b55a3 |  | note | Acceptance Criteria - Witness Point
label | b0067f58-4343-59f0-8eed-6fc2d8792a23 |  | note | The area in which concrete is proposed to be placed must be inspected and checked immediately prior to commencement of placing
label | 06c7ed52-f25b-5436-8d8e-601a44196226 |  | note | Reference Documents - Clause 13.10.7
label | 1f04b187-8643-5e1e-ae36-d8d18a6d2fa6 |  | note | Inspection/ Test Method - Inspect
label | ef3db73f-bb92-5157-b9d8-da315a5537e7 |  | note | Record of conformity - Notification and this ITP Signed
label | 997e882f-4850-5a9c-b16a-7d17070922e1 |  | note | WP
label | 199a75bc-ecaa-59aa-ae86-213792bb7908 |  | note | Responsibility - Engineer/ Principal’s Representative
text | 426c6d87-fddc-55cb-ae33-4faecd977964 |  | textbox | Date Completed:
checkpoint-status |  |  | checkpoint | 4.6 - Check the weather forecast
label | 91d03b52-d22b-5856-b7df-8e601961a299 |  | note | Frequency - Prior to concrete pour
label | 5e80a5aa-d286-5b1d-b2b5-8dc8484e7a23 |  | note | Acceptance Criteria - Check weather forecast for unfavourable conditions - rain, cold or hot weather. To be checked the day before and immediately prior to confirmation of batching concrete.
label | 338ff0d1-56da-51e2-9211-d488beacdc82 |  | note | Reference Documents - Clause 13.10.12.1
label | b6d32909-4822-5625-8d83-27987bf5027c |  | note | Inspection/ Test Method - Inspect
label | 6d61cbd2-d655-5bea-b189-cc5546f0a3cd |  | note | Record of conformity - This ITP Signed
label | cc914e0e-3daf-5c4d-b4f9-e33e950d469e |  | note | IP
label | a3e126bb-4329-5f78-a0b6-2447e61f0665 |  | note | Responsibility - Engineer
text | f97e3e0a-4bb5-5145-a853-457d00be3a26 |  | textbox | Date Completed:
checkpoint-group |  |  | section | 5.0 Placing Concrete
checkpoint-status |  |  | checkpoint | 5.1 - Sampling concrete
label | f704491c-8814-5b3a-8b95-ae1c4346dd63 |  | note | Frequency - Each concrete pour
label | 021b77e6-c541-5073-890c-33244f9338ee |  | note | Acceptance Criteria - Sampling in accordance with MAPMP Specification.
label | 1eca007a-f60d-5991-9ede-7017d3ef157f |  | note | BEAMS
label | 0dd95e79-ed4f-5c14-a416-5752c03c9671 |  | note | • 7 Days – 2 beams every 75m3 or part thereof
label | 54e2e984-3463-5c3f-8f7e-f8d47be58e3a |  | note | • 28 Days – 2 beams per 75m3 or part thereof
label | 5ed08be2-e6ac-53ee-bc2b-2d6f98161270 |  | note | SLUMP
label | 45c9e343-0289-5727-a61a-dd42d49370a4 |  | note | • Slump to be performed on every truck (50mm for handplaced concrete +/- 10mm
label | 9302cfcd-dcb7-50d8-995a-170a53e80a1c |  | note | AIR CONTENT, MASS PER UNIT
label | 53368814-6a4c-54ed-8480-d2d2806604b4 |  | note | Air Content test (3% – 5%) to be performed on first two trucks, and each 75m3 thereafter.
label | 9327b5b3-b5ec-5fd8-976d-f3bbc7a79e8d |  | note | Mass per unit volume test is to be performed once per lot.
label | 22f8040b-3884-55bd-bd27-428321205d88 |  | note | All tests taken to be recorded in CL 009B - Concrete Pour Record Sheet
label | 4818e29d-8630-58f4-9063-3fa032a52203 |  | note | Check Number of tests taken during the shift / lots conforms to the testing criteria. (Beams cast, stored and secure).
label | 385d135c-6bed-5577-9b50-ff2dfb5e7f92 |  | note | Reference Documents - Clause 13.9
label | a0cadd6e-8c4c-5df9-a7d6-f485328e3a74 |  | note | Inspection/ Test Method - Test and Verify
label | c0ec4041-53a7-551b-8c90-62810145db47 |  | note | Record of conformity - This ITP signed & CL009B
label | e9091053-192e-56ad-8c84-74264ecb88bc |  | note | IP
label | f722b00e-1852-5e39-b808-d68ed2061639 |  | note | Responsibility - Engineer
text | 87597fec-f607-5630-927b-d426d5484f4b |  | textbox | Date Completed:
checkpoint-status |  |  | checkpoint | 5.2 - Place Concrete
label | cfc310c2-3ba5-566c-9538-b3d52aed83f4 |  | note | Frequency - Each concrete pour
label | 0bbd6b76-30e5-5cba-ac84-142d5366755f |  | note | Acceptance Criteria - Discharge time must be < 90 minutes (with a target of 60 minutes) from batch time.
label | 53012bdb-7a37-5fd4-b3ea-9463a7888232 |  | note | Concrete must be poured at a rate greater than 20m3 per hour.
label | 2691e2d7-00aa-5628-babc-2f18b777f6ec |  | note | Concrete must not be dropped from higher than 1m
label | 3df4f1a9-214a-5765-a6ed-274848d0c59b |  | note | Ensure there are no breaks greater then 60min between concrete placement.
label | abe68c01-a6c8-5a4a-a132-71de9965e623 |  | note | All delivery times to be recorded in CL 009B - Concrete Pour Record Sheet
label | a68be525-dad3-5b5a-be98-019e4a1f95e6 |  | note | Reference Documents - Clause 13.10.7 CL009B
label | a12e1bd0-5b71-557e-b856-f5cbd897c2ee |  | note | Inspection/ Test Method - Verify
label | d6e731d9-7782-5dcb-8dba-7c50cb6ffa9b |  | note | Record of conformity - This ITP signed
label | 6263d89f-c027-5f11-bc33-1a0909fe02f4 |  | note | IP
label | 3270232f-7d04-53e1-8d2a-25a758cde227 |  | note | Responsibility - Engineer
text | dbeb40bf-9f22-560a-bc00-b0cd70b16372 |  | textbox | Date Completed:
checkpoint-status |  |  | checkpoint | 5.3 - Hot Weather Requirements Met
label | c8d38ce0-f240-5b1f-9987-ed3b09fe958b |  | note | Frequency - Each concrete pour
label | 88c8e0e6-94a0-5066-98e1-0b9a97e16fed |  | note | Acceptance Criteria - No concrete can be poured if air or concrete temperature exceeds 30°C without Principal’s Representatives approval.
label | e7db2212-5cc1-5969-82d4-4f3f7c336650 |  | note | Reference Documents - Clause 13.10.12.2
label | c23013fc-f7e8-5ae4-ba29-f0541395c907 |  | note | Inspection/ Test Method - Verify
label | bff1e462-9698-52e4-b123-ce5276f5b2cd |  | note | Record of conformity - This ITP signed & CL009E
label | 9f627105-058e-5efd-9b86-203a6a75123e |  | note | IP
label | bcfec949-5081-5e6b-9af6-728639170472 |  | note | Responsibility - Engineer
text | 57828c26-988c-53da-94ca-101846eae562 |  | textbox | Date Completed:
checkpoint-status |  |  | checkpoint | 5.4 - Cold Weather Concreting
label | d7b01aa6-a109-51b9-9401-7a7459b82305 |  | note | Frequency - Each concrete pour
label | 858cba8e-c559-50bb-8c53-293c7b17e71e |  | note | Acceptance Criteria - Concrete shall not be placed when the ground temperature is below 5°C unless precautions are in place.
label | 131e401e-525f-5cda-bc2b-33bd5cc5455b |  | note | Concrete shall not be placed when the temperature of the concrete mix is below 10°C unless approved
label | 4259f0b4-f75f-5b5f-b336-8cbacc3d165b |  | note | FH to confirm temperature on site prior to pouring.
label | 2a4205e7-01f2-568b-b0f5-1d5134aa3b9b |  | note | Reference Documents - Clause 13.10.12.3
label | a3e7213b-5508-5ac0-8cde-e1faae04e5b1 |  | note | Inspection/ Test Method - Verify
label | cf890bdc-1361-5775-ac74-2c74c2356ad2 |  | note | Record of conformity - This ITP signed & CL009E
label | 01625693-1df7-503b-9c3b-d14578ad6433 |  | note | IP
label | 5040b14d-3314-5705-858b-ce3e0d185b2d |  | note | Responsibility - Engineer
text | df14d877-10ee-578a-8e08-d25e0cc4cf08 |  | textbox | Date Completed:
checkpoint-status |  |  | checkpoint | 5.5 - Recording Pour Location
label | 4c197073-b698-526e-987e-30a310c29f89 |  | note | Frequency - Each concrete pour
label | b31000c0-fe1e-5967-9383-bcaef306ca55 |  | note | Acceptance Criteria - Pour location recorded on plan at the completion of pouring each lot – CL 009C. Include progress with times.
label | 752d46b7-b412-5923-9099-8e7b5a51735f |  | note | Reference Documents - CL009C
label | 92eba3eb-90c3-5f74-ace2-714bbc13a392 |  | note | Inspection/ Test Method - Verify
label | 1e66a619-64b1-575c-ab30-6d12840aefc2 |  | note | Record of conformity - This ITP signed & CL009C
label | 00a5b374-51b5-5337-a8cb-b35871f9e18a |  | note | IP
label | fee9df66-f0f1-58b3-8658-47aecb32e138 |  | note | Responsibility - Engineer
text | f7ba1f73-3126-578d-9e0d-d39955ce3fc3 |  | textbox | Date Completed:
checkpoint-status |  |  | checkpoint | 5.6 - Evaporation Rate
label | fac95abe-954b-57aa-bcd0-b9e5a5d27cf0 |  | note | Frequency - Each Concrete Pour
label | 9b651398-2da0-5df9-98fc-5e94427eb44a |  | note | Acceptance Criteria - Evaporation rate recorded every half hour. If evaporation rate is >= 1kg/m2/h works must cease and a transverse construction joint installed
label | 26e219d9-f924-5e48-8088-95aa4f183540 |  | note | Reference Documents - Clause 13.10.12.1
label | 5f93daf9-e838-5b63-8a90-f53d4bcde191 |  | note | CL009E
label | 03d7b9ea-5ea0-564c-b5dc-8da49efe916f |  | note | Inspection/ Test Method - Verify
label | f7df44fc-343f-51b9-8deb-261604a6e1a5 |  | note | Record of conformity - This ITP signed & CL009E
label | f3a5dfaa-98ce-5238-93e6-756bf2e75bd1 |  | note | IP
label | 5b76dd2b-df21-510c-85e8-a6277ba8004c |  | note | Responsibility - FH Engineer
text | 4760ab93-4a2e-550e-9ace-aed036fe0421 |  | textbox | Date Completed:
checkpoint-status |  |  | checkpoint | 5.7 - Surface finish
label | e082f11e-162c-5a92-91ba-e3d0ac4a941e |  | note | Frequency - Each Concrete Pour
label | 8fa82c0d-fb25-5347-8f12-f4afe622b145 |  | note | Acceptance Criteria - Concrete to be shall comprise traverse finishing, longitudinal straight-edge finishing, floating and then broom finishing, in that order.
label | 6e86cd20-f01e-54e3-ad39-f07e0b77da97 |  | note | Brooming shall be in a direction at right angles to the direction of the placing of the concrete.
label | b3c638d7-d7ec-5b02-a7d6-d82a2b0c1e8b |  | note | Reference Documents - Clause 13.11.2.6
label | 13e30961-3001-516a-9dbe-abdc2f1f5f29 |  | note | Inspection/ Test Method - Verify
label | 5cdf1dd3-67ea-5157-ac76-e7e29b551873 |  | note | Record of conformity - Site Inspection
label | 02da6677-249a-55cb-b62d-f7d2c955e5fd |  | note | IP
label | abbb08cd-4be7-5ea1-a95c-81a8f1613310 |  | note | Responsibility - Foreman
text | a056bc81-5abe-54b1-ab70-9e2705aaf6f4 |  | textbox | Date Completed:
checkpoint-group |  |  | section | 6.0 Post Placement
checkpoint-status |  |  | checkpoint | 6.1 - Curing
label | bc195e99-35bd-530f-a56b-a147ed04959e |  | note | Frequency - Each concrete pour
label | 30e6a64b-82e7-5821-9855-c2a675c9e1fc |  | note | Acceptance Criteria - Concrete to be wet cured for a minimum of 7 days.
label | 96705e73-9fb4-52b2-bb80-c8fda27e7e0d |  | note | Initial Curing shall commence immediately after finishing operations have been completed.
label | dfa3da2a-8190-58db-be58-01fb6d9a6b9f |  | note | Moist curing to commence as soon as possible after finishing. This will be wetted hessian mats covering the pour. The mats shall overlap to ensure sufficient coverage. Mats shall be kept saturated for not less then 7 days.
label | 705d5e9e-0261-5ab9-93ae-207a8075cbff |  | note | Curing methods and details shown on post pour checklist CL009D.
label | 2a5bd1c0-f52e-5aba-b7bf-8f16ed58c828 |  | note | Details to be recorded in CL 009D
label | 568cc385-65f1-5aa8-b840-f96efcd21288 |  | note | Reference Documents - Clause 13.10.11
label | 03fca481-ee7d-57b0-a267-1cbb2e3ce268 |  | note | CL009D
label | f170a449-ede5-5030-b446-b7328df696a9 |  | note | Inspection/ Test Method - Verify
label | 8b501fd1-68de-54c3-8709-c3ae3b0adc58 |  | note | Record of conformity - Site inspection & CL009D
label | 8a6e9186-7678-545b-94a7-80f0be3fe2ca |  | note | IP
label | 9d43c3d0-1712-5baf-8c20-4e0e573f5fc1 |  | note | Responsibility - Engineer
text | 4bbc47e6-77d2-57c9-8633-e79adb4bce10 |  | textbox | Date Completed:
checkpoint-status |  |  | checkpoint | 6.2 - Cold Weather/Wind Concrete Protection
label | 01c64f00-e509-5d5c-8f41-6b7308f8bebf |  | note | Frequency - Each concrete pour
label | 49ec9aee-fb56-5996-bde5-21c596c2309b |  | note | Acceptance Criteria - In the event where the air temperature is below 10oC or the completed pavement is expected to be exposed to freezing conditions, concrete placing must only take place with the prior approval of the Contract Administrator.
label | 608aa859-f5ee-52f1-a50f-68dea14aef25 |  | note | Reference Documents - Clause 13.10.12.3
label | 990383c4-e3c6-5b8c-aad6-87580b65b755 |  | note | Inspection/ Test Method - Verify
label | 27ce0612-ed1f-56a1-9a6b-eb047e1b468c |  | note | Record of conformity - Site Inspection
label | 7b89cbb4-3e0c-590c-a231-f97cc06b4f9c |  | note | IP
label | 93459913-e283-558d-9e2e-8039e28aac9e |  | note | Responsibility - Engineer/Principal’s Representative
text | d5788865-4873-548f-8301-1cda1246a550 |  | textbox | Date Completed:
checkpoint-status |  |  | checkpoint | 6.3 - Inducement Saw Cutting
label | 1b6e42a4-417f-5644-9e71-3057b202c62a |  | note | Frequency - Each concrete pour
label | eac2ba98-85af-5ef7-af35-3e0705373335 |  | note | Acceptance Criteria - Initial 3mm-5mm wide x 207mm (Type A) or 155mm (Type C) deep saw cuts to be carried out as soon as possible. Details recorded on post pour checklist CL 009D.
label | a9857641-436b-5a61-8279-f19b0e763c7d |  | note | Reference Documents - Clause 13.10.13.6.1
label | 7af59db7-c896-5816-8391-d7cd580fd8cf |  | note | CL009D
label | 8ebbff69-d53b-553b-87b1-a90c636360ec |  | note | Drawings
label | 3832922b-3e7b-5560-802c-f5493420f720 |  | note | Inspection/ Test Method - Verify
label | 5819c0d5-7626-5a0f-9c6e-c1c4447c756e |  | note | Record of conformity - Site inspection & CL009D
label | b8b3dd45-3c0c-5030-ae6a-5b45d346beee |  | note | IP
label | 5c7648ab-ccd5-53a7-bebd-46600873a2d1 |  | note | Responsibility - Foreman or Engineer
text | 02700f7a-1658-5057-b8f8-c38e7f3b733f |  | textbox | Date Completed:
checkpoint-status |  |  | checkpoint | 6.4 - Formwork Removal
label | 233f8f5a-283f-5bbd-9edc-280c42fee092 |  | note | Frequency - Each concrete pour
label | 191f32d2-ec13-51c1-9c19-0f29a52416ce |  | note | Acceptance Criteria - Formwork may only be removed after a minimum of 12 hours after concrete placement.
label | f4e89843-5896-507c-acde-f3f959381277 |  | note | Details to be recorded in CL 009D.
label | bc83bce0-5330-530e-8c52-e52489e7732e |  | note | Reference Documents - Clause 13.10.15
label | 58617e92-64cb-598a-9cfd-e1987b8bb458 |  | note | Inspection/ Test Method - Verify
label | b170e8a8-1533-5dfd-bca8-e5c86a3d0056 |  | note | Record of conformity - Site inspection & CL009D
label | 926ed2de-da29-5a1f-b25a-9cfcb02249cc |  | note | IP
label | f414a8dc-c507-53a7-a43b-33f3b41676fd |  | note | Responsibility - Foreman
text | f032fa69-ce2a-52ff-bdbe-55b4bec3096e |  | textbox | Date Completed:
checkpoint-status |  |  | checkpoint | 6.5 - Positional Tolerance and dimensions of concrete (finished surface levels)
label | 06b2eabd-d1ac-53fa-b73e-f970deabe964 |  | note | Frequency - Each lot
label | bfe8441b-2c0d-5bd0-b3c1-904ce6e6fd5c |  | note | Acceptance Criteria - Survey done and report prepared: +5mm, -5mm tolerance from design required.
label | e10b0457-73e4-57ad-bf1c-1c81c3babb16 |  | note | Dimensions within the tolerances – details recorded within CL009D.
label | 87beb91f-5060-5088-9944-c3979f825675 |  | note | Reference Documents - Clause 13.11.2.1
label | 6ba3de81-14ea-523e-a2d6-155181d8904a |  | note | CL009D
label | e4637a4a-2327-5f83-8e1f-86c5fbb3c478 |  | note | Inspection/ Test Method - Inspect
label | f4a26ade-6670-504c-81b9-b1beb94d7322 |  | note | Record of conformity - Survey & CL009D
label | c9db8858-87bf-5cea-a89c-0d921d445b56 |  | note | SCP
label | 35fc8d6f-772b-5f70-8afb-a61096d0edb2 |  | note | Responsibility - Engineer/Survey
text | 0d2810d3-aa18-5fab-a037-7530c06f5e8e |  | textbox | Date Completed:
checkpoint-status |  |  | checkpoint | 6.6 - Pavement Density
label | 60bdb7c1-adf4-533f-9c9c-1568ac95430c |  | note | Frequency - Each Lot
label | 3d18d743-4fc7-57d9-89fe-8869e5ef1490 |  | note | Acceptance Criteria - DENSITY
label | 5be44226-bbe8-551d-a2b4-bd8759f4bb10 |  | note | · Core (120mm dia x full pavement depth) to be cut and tested for density.
label | 1e47d66a-4639-58f3-8d81-ae901b35047c |  | note | Frequency
label | 92b88a36-5372-58a9-ba36-74adfda089a1 |  | note | · 6x cores per lot. The rate of coring may berevised after the first four (4) lots arecompleted.
label | 167eb588-b825-5f4c-b437-e422e13656c0 |  | note | Reference Documents - Clause
label | 0d7488fc-7e37-5cf2-b084-6cf9494fef4a |  | note | 13.11.2.3
label | 56a2b751-47a4-5da3-9666-049a9e2e9d2a |  | note | 13.11.2.4
label | 29a237db-2975-5fd3-a9ae-9736625d537f |  | note | Inspection/ Test Method - Test and Verify
label | b12ea7a3-6a42-5ba4-92a7-41cd420c5f8d |  | note | Record of conformity - Test Report
label | 3979af5b-8504-51d9-85d0-ef296c5e8e5b |  | note | IP
label | ac5ccfb7-1fab-5f4d-8385-1380d50ba465 |  | note | Responsibility - Engineer
text | b2235b4e-6999-5420-9590-c07371ccad9f |  | textbox | Date Completed:
checkpoint-status |  |  | checkpoint | 6.7 - Surface Smoothness Testing
label | 73203f6f-6613-5a87-8d31-d00da0746a50 |  | note | Frequency - Each lot
label | 97ecafaf-7457-501f-b199-6deb15c53dd5 |  | note | Acceptance Criteria - Hold Point (if required)
label | 3505edbe-8e76-55ef-af65-ac48cee45cb2 |  | note | The surface smoothness of the finished surface shall be checked using a straight mobile edge, and the minimum of the finished surface is that it shall not deviate from the testing edge of a 3.5 m straight edge by more than 5 mm.
label | 055eb240-d714-573a-bad3-7f3a4ff56ba5 |  | note | Any deviations greater than the tolerance a hold point shall be installed
label | e13da7dc-a687-5bba-b75f-0cc79729f8c0 |  | note | Reference Documents - Clause 13.11.1.2
label | d2b4b36a-378b-55b1-af7d-790403957671 |  | note | CL009F
label | 62e355b7-042a-57f9-90c6-a4b96fa0f39e |  | note | Inspection/ Test Method - Inspect
label | 09f887e7-a20e-5e93-8890-e21b9aeff2d0 |  | note | Record of conformity - Site inspection & CL009F
label | 13d066c9-4947-5a19-a741-2432a5bb3f28 |  | note | HP
label | 06e0e582-3603-532b-8260-afb732bc52ab |  | note | Responsibility - Engineer/ Principal’s Representative
text | c4d9605c-f49a-5f8a-82ef-c50d341e3e78 |  | textbox | Date Completed:
holdpoint |  |  | signoff | Authority Holdpoint
checkpoint-status |  |  | checkpoint | 6.8 - Defects in the concrete
label | fca4983d-9626-55fc-b6bd-f7a8cbb07f75 |  | note | Frequency - Stripping of Forms
label | 86f941c5-55e6-5b03-bfb2-ed30ff5c8831 |  | note | Acceptance Criteria - Check for any non-conforming or defects (cracks) in the concrete slabs.
label | 125a113a-318e-54eb-814e-41f92185b9bc |  | note | Any locations identified to be recorded in the post pour checklist - CL 009D.
label | f3c3f034-557c-5eec-916e-af74ffa7d56d |  | note | Reference Documents - Clause 13.11.1
label | 8d8abd99-d050-5272-90f7-785cc7b24431 |  | note | Inspection/ Test Method - Inspect and Verify
label | 31e66e0d-c22c-5d5c-892c-c3f247423ce9 |  | note | Record of conformity - Site inspection & CL009D
label | 38fd347b-961c-54f2-90b9-7a1070b8561a |  | note | IP
label | 8e22fb53-4294-5722-9bdc-eb2fb587e4c9 |  | note | Responsibility - Engineer
text | e37eb108-dfc9-5a5d-94d9-49d00a01b55a |  | textbox | Date Completed:
checkpoint-status |  |  | checkpoint | 6.9 - Spalling or honeycombing
label | 317a3077-bbf9-57d6-89e4-f07356d97522 |  | note | Frequency - Stripping of Forms
label | 2d43a483-4272-5e46-9422-560d7afdf668 |  | note | Acceptance Criteria - Check for spalling or honeycombing during and after curing of the concrete slabs. (Must be less than 5% of surface area).
label | f83c5a13-a5a0-58b5-a1ba-e6e1c1671ceb |  | note | Any locations identified to be recorded in the post pour checklist - CL 009D.
label | fc473a5d-3fd8-5875-b24c-cb3f4dc0df7a |  | note | Reference Documents - Clause 13.11.2.5
label | d5f631dc-dbb5-59c4-9cb2-898ed74f47b4 |  | note | Inspection/ Test Method - Inspect and Verify
label | 39502ad5-4c71-570d-a895-436258116a1d |  | note | Record of conformity - Site inspection & CL009D
label | f0ccd245-d76d-556c-9095-aebaf865500f |  | note | IP
label | e2319f46-343d-5fc3-a83b-7dafede1610a |  | note | Responsibility - Engineer
text | b9c53cf1-8287-5c85-a228-e09e398b78c5 |  | textbox | Date Completed:
checkpoint-status |  |  | checkpoint | 6.10 - Protection of Concrete Pavement
label | 73145348-2dff-525c-bc3a-0a00a881010f |  | note | Frequency - Each Lot
label | bdae3865-8cd2-5703-81f1-3238e79b52ad |  | note | Acceptance Criteria - Concrete pavement not to be trafficked until 7 days old or early strength results are obtained (3.2MPa min)
label | abfbd637-7fb2-59fc-9231-cfbab39e13b6 |  | note | Steel tracked or wheeled equipment is not to be used
label | bc54cc5c-2e10-5fcb-9d31-de1ed45aa3cd |  | note | Reference Documents - Clause 13.10.16
label | 79666858-5527-5d9b-bba6-4b451851a14d |  | note | Inspection/ Test Method - Verify
label | f68d4143-becc-5d9a-8322-e306a3ab9501 |  | note | Record of conformity - Test Report
label | b7a4744a-9f42-558f-a71f-a3d1071696c9 |  | note | IP
label | 254cdfd8-c215-55c2-96b2-f0ec3fd2360d |  | note | Responsibility - Engineer
text | 355060ac-8965-5971-855e-4077c38482ab |  | textbox | Date Completed:
checkpoint-status |  |  | checkpoint | 6.11 - Concrete Test Results
label | 91b059d3-3ac7-557a-8afc-1d85c7fbcf4a |  | note | Frequency - Each concrete Pour
label | 710fb1cd-9821-5ae6-ac6f-39e22c905fe0 |  | note | Acceptance Criteria - All concrete test results obtained and attached to ITP.
label | 3deff127-5e96-56fe-891e-db6b1fb87267 |  | note | All concrete test results submitted on Aconex
label | 8a01d308-a77c-5d37-b2bc-0bab50348a88 |  | note | Check results of concrete tests are compliant as per specifications (e.g. graphical plots, Analysis of Flex. Strengths)
label | 28709c95-5157-5340-8cb9-44e13d0139a7 |  | note | Reference Documents - Clause 13.9.3.7
label | a244d7bb-2609-5b5d-8b1b-b27816e4cb28 |  | note | Inspection/ Test Method - Verify
label | 094fc7fc-cf01-542e-bce9-0cb9c625d33d |  | note | Record of conformity - Test Report
label | 6672f669-2edd-522f-9959-a8349a27290c |  | note | IP
label | 7b45a649-9367-5519-915f-1fb36534749d |  | note | Responsibility - Engineer
text | f0d42d15-0d2c-516d-9ccc-05e8cb5d1094 |  | textbox | Date Completed:
checkpoint-status |  |  | checkpoint | 6.12 - Post-Pour Checklist
label | a1ab6c4c-98a3-592f-9929-fd2b36db0dee |  | note | Frequency - Each concrete pour
label | 41bd37d4-2fa2-5166-8407-03a1293e562e |  | note | Acceptance Criteria - CL 009D – Post-pour Checklist completed and signed.
label | 7cc6747e-00ac-5cc6-8552-d4ace22db194 |  | note | Reference Documents - CL 009D
label | b3aa82ac-b2ae-56b5-8c81-7830557cc04e |  | note | Inspection/ Test Method - Verify
label | 91b57516-d06d-5a9e-aab6-d08c4c52513d |  | note | Record of conformity - CL009D
label | 8ee66d44-d8f9-5732-8293-8213a932dbb5 |  | note | HP*
label | f4e9005b-d8ba-5f7c-852e-5b607ac38ae0 |  | note | Responsibility - Engineer
text | dc99bb6a-3c4c-5fd2-af89-4b1e56ce6819 |  | textbox | Date Completed:
checkpoint-status |  |  | checkpoint | Final Inspection
label | 00e6537b-d14c-5b72-b403-ea769660a69a |  | note | On behalf of Fulton Hogan it is hereby certified that the Works represented by the items of work listed have been tested in accordance with the Project Quality Plan and conform in all respects with the requirements of the Contract.
text | 77ca74f2-bfc2-5841-bfaa-01be7584db47 |  | textbox | Print Name:
text | 4c9f4f70-c03d-5cc1-a81d-15b2e6c2a0cd |  | textbox | Position:
text | 13735128-92d8-5a7e-829e-853c714204a6 |  | textbox | Date:
checklist-sectioned |  |  | checklist | ITP001 - Demolition | itp |  |  |  | Yes | ITP001 - Demolition | b9341f97-0048-4355-bdf9-7d1e0f43c816
checkpoint-group |  |  | section | Preliminary Activities
checkpoint-status |  |  | checkpoint | 1.1 The current revision drawings are being used including subcontractors copy.
label | 5e4bc0ef-e95c-5e04-b950-437b30a86e28 |  | note | Frequency: Prior to commencing works
label | cfc72b82-4a0c-5d6d-a69d-c0a3e6323de7 |  | note | Acceptance Criteria: Current revision drawings are being used, including the subcontractors copy. Current revision to be obtained via Aconex
label | adf4ad03-039a-58a8-8d00-cdfd07cd5b16 |  | note | Reference Documents: Current Revision Drawings in Aconex
label | 6525b8a1-a212-558d-8e70-b6db4ef172e3 |  | note | Inspection / Test Method: Visual Inspection
label | 79c50700-f8dc-5599-b6ee-8ef195546178 |  | note | Record of Conformity: This ITP signed
label | 63c25937-9391-51c8-89a5-db203133725c |  | note | HP*
text | c20a2ad7-6f76-5c03-9a48-335e2f69e3d1 |  | textbox | Responsibility: Project Engineer
checkpoint-status |  |  | checkpoint | 1.2 Dilapidation Report
label | 83790506-f8b3-5977-9e06-faa3a577e7cc |  | note | Frequency: Prior to commencing works
label | b4e2e040-0a00-5e18-81b5-55e67ab357ba |  | note | Acceptance Criteria: Prior to the Works, the Contractor shall provide the Contract Administrator with a fully detailed dilapidation survey recording the current condition of aircraft pavements, aircraft pavement surface features, underground services, roads, drives, footpaths and adjoining premises.
label | 2f30d290-b7db-5f87-969e-013ac023c7f8 |  | note | Reference Documents: AECOM – MAP MP Spec. Cl1.17.1
label | 09907cf4-b1eb-554e-ac75-acef179e40ec |  | note | Inspection / Test Method: Verify
label | e4919630-c561-5a30-bb2f-ca3fb773ac6e |  | note | Record of Conformity: Aconex Correspondence
label | 86fa0b9e-9540-56da-b850-a6db0425c23b |  | note | HP*
text | aa4d1e80-1f9e-5c8e-8cad-d611d4c1f6f1 |  | textbox | Responsibility: Project Engineer
checkpoint-status |  |  | checkpoint | 1.3 Current excavation and isolation permit has been issued.
label | d1b09357-851f-550e-af0c-9f89459ee93c |  | note | Frequency: Prior to commencing works
label | 3f4ce99d-f94d-54e0-9766-cf5c094dee9e |  | note | Acceptance Criteria: An Excavation Permit and an Isolation permit issued by Melbourne Airport. A permit to work must be obtained from JUHI when working on or near their assets. Fulton Hogan Excavation permit issued to plant operators.
label | c2e5fb5a-f7c7-5ee1-b551-4e95ddff4a83 |  | note | Reference Documents: Excavation Permit/ Work Permit
label | d33c8029-8acc-5992-80b0-cd1f42b537b6 |  | note | Inspection / Test Method: Visual Inspection
label | 2bb48af8-c233-5e39-9530-d20d0ae7986d |  | note | Record of Conformity: Permits
label | 5708f452-6f75-5532-98a8-5b57892eef5f |  | note | HP*
text | dd3c96e2-98b8-58cf-8835-476ef3ebdf3d |  | textbox | Responsibility: Project Engineer / Foreman
checkpoint-status |  |  | checkpoint | 1.4 Service Location and Detection Methodology
label | 2253bd72-be9c-5656-8dd7-6c302da70a78 |  | note | Frequency: Prior to commencing works
label | 60cd21e1-6c82-5101-9a0e-4ab5318be133 |  | note | Acceptance Criteria: The Contractor shall submit a methodology of service detection to the Contract Administrator for review. This methodology is contained within the work procedure for demolition.
label | 94c9f4df-bb83-5d85-9d02-17088883375f |  | note | Reference Documents: AECOM – MAP MP Spec. Cl3.2.1 FH-SAT10-PM-WP001 Section 3.2
label | b6bd8db3-8663-52a3-be33-b629c7b3339a |  | note | Inspection / Test Method: Verify
label | f85870d6-3ea2-550c-8c38-7df31eeb2f6e |  | note | Record of Conformity: This ITP signed
label | c82754d6-406b-51ee-bb2c-f2a5082a3f0e |  | note | WP
text | 785fb161-07bf-5abc-ad72-b2a55b5a6eae |  | textbox | Responsibility: Project Engineer / Contract Administrator
checkpoint-status |  |  | checkpoint | 1.5 Demolition Work Plan
label | 2a95ddd9-2ebe-5112-9af7-e49d71818305 |  | note | Frequency: Prior to commencing works
label | 5822d8fb-ac55-54d2-8ada-ab5293a57037 |  | note | Acceptance Criteria: The Contractor shall prepare a Demolition Work Plan in accordance with AS 2601 and shall submit this plan to the Contract Administrator at least seven (7) days prior to the works commencing for approval.
label | 12ddbae1-379a-5aed-a904-992209b5d06f |  | note | Reference Documents: AECOM – MAP MP Spec. Cl4.5
label | 984b3ff4-1472-52c1-9f73-dd384afbda8c |  | note | Inspection / Test Method: Verify
label | 57750a55-282c-5001-8e8d-b69baec03374 |  | note | Record of Conformity: This ITP signed
label | 02a2b337-2195-536b-9e88-ce35eb56678b |  | note | HP
text | 3b0003f2-d1a8-571c-ab93-e13c23830ca6 |  | textbox | Responsibility: Project Engineer / Contract Administrator
holdpoint |  |  | signoff | HOLD POINT
checkpoint-status |  |  | checkpoint | 1.6 Obtain approvals to start works
label | a833b00f-aa29-5369-a1e3-ce176a34d6ee |  | note | Frequency: Prior to commencing works
label | ceaa6594-7336-5291-92a9-0dab3a31d2ad |  | note | Acceptance Criteria: The Contractor must obtain a "Work Approval" from the Principal as required. It is deemed that the “Work Approval” required is the Permit to Commence Work (PERCOW).
label | 14cee819-f2a5-58bc-8954-33b2bbf44556 |  | note | Reference Documents: AECOM – MAP MP Spec. Cl4.4
label | ca3c079a-0b98-5ae5-b29d-4b2257b61e1e |  | note | Inspection / Test Method: Verify
label | db810ffd-278f-595b-a57d-25219169ae95 |  | note | Record of Conformity: This ITP signed
label | 49d84437-5b61-5649-89f0-35a2aba11a57 |  | note | HP
text | 5c040a32-840a-5d5b-a8f3-cd0be6f820c7 |  | textbox | Responsibility: Project Engineer / Contract Administrator
holdpoint |  |  | signoff | HOLD POINT
checkpoint-status |  |  | checkpoint | 1.7 Obtain JUHI approvals to start works
label | 4f01997d-626a-5483-9fa6-ac29c834ae94 |  | note | Frequency: Prior to commencing works
label | 40ca17f9-0722-5907-b2db-dc3b5512bf5f |  | note | Acceptance Criteria: The Contractor must obtain a permit to work from JUHI when working on or near their assets.
label | bd9e8960-b782-572e-bb4e-2daf32882837 |  | note | Reference Documents: AECOM – MAP MP Spec. Cl4.4
label | cc823891-0ea5-5df2-a160-49b83cf3f2d0 |  | note | Inspection / Test Method: Verify
label | 1e4d80ac-cac3-538d-816c-931882ad3588 |  | note | Record of Conformity: This ITP signed
label | b71ade04-6619-5507-8604-5357832a2b1b |  | note | HP
label | e9f7bd81-128d-5728-b8d8-888a3b0e014a |  | note | Responsibility: Project Engineer/ Contract Administrator
holdpoint |  |  | signoff | Hold Point
checkpoint-status |  |  | checkpoint | 1.8 Implementation of all measures and controls
label | abe5ed25-abba-55de-9f63-3895a5cc2480 |  | note | Frequency: Prior to commencing works
label | e81c0600-eb29-59d4-a99a-509e333d1070 |  | note | Acceptance Criteria: All necessary measures and controls are being implemented, that is: PSP, EMP, TMP, SWMS & WP
label | cd8c6965-8317-57b9-9f9b-42f70fa1bc98 |  | note | Reference Documents: PSP, EMP, TMP, SWMS, WP
label | 7f9916a1-7e41-56a7-95c0-664f9781b76c |  | note | Inspection / Test Method: Visual Inspection
label | f3faa738-a131-53c2-ace2-30f95ec35a43 |  | note | Record of Conformity: This ITP signed
label | 0dc16281-33b4-5f83-964f-729a1651f146 |  | note | HP*
text | acb9d1d2-897d-5c96-94be-a9ede72e4386 |  | textbox | Responsibility: Project Engineer/ Site Supervisor
checkpoint-group |  |  | section | Demolition Works
checkpoint-status |  |  | checkpoint | 2.1 Services Detection
label | 012f20e6-754c-53f5-9b31-4ee00c3c0c63 |  | note | Frequency: Each Lot
label | 55c5018f-2f47-57cd-8d2d-d89a2868c29f |  | note | Acceptance Criteria: Confirmation that Services Detection has been Completed for the Works area(s)
label | 4266d61b-b095-5a0d-9c76-7f03b93b7814 |  | note | Reference Documents: AECOM – MAP MP Spec. Cl3.3.1
label | 99962858-bc5a-510a-82d9-f23f0ae1614b |  | note | Inspection / Test Method: Visual Inspection
label | 0257f803-7259-525d-bc22-b986068e9235 |  | note | Record of Conformity: This ITP signed
label | 8b046d2e-eb01-54d9-9b8d-24ffa73c0d65 |  | note | HP
text | 2cd604ab-ec36-53cb-bfec-402a07a6756c |  | textbox | Responsibility: Project Engineer / Foreman
holdpoint |  |  | signoff | HOLD POINT
checkpoint-status |  |  | checkpoint | 2.2 Existing JUHI Services
label | 50057892-8e14-511a-9cef-d7531c9fa9ac |  | note | Frequency: Each Lot
label | 0e82a707-068e-52a2-ace6-72373c0e6fbb |  | note | Acceptance Criteria: The Contractor shall give the fuel pipeline operator (JUHI) a minimum of five (5) days written notice of his intention to work in the vicinity of existing JUHI fuel line.
label | 0edf71f3-c68a-5985-87a9-a0e86bfdfc7f |  | note | Reference Documents: AECOM – MAP MP Spec. Cl4.6.1
label | b59a2eae-9c49-57b4-ad7c-f38466d911c2 |  | note | Inspection / Test Method: Verify
label | 66f184e9-a06d-594e-abb2-c251f789c8e4 |  | note | Record of Conformity: This ITP signed
label | 2858d2eb-d3a8-5d5f-be12-5b98e28b09ca |  | note | HP*
text | c6d7bd33-bda2-5b64-be54-a8475802bd9e |  | textbox | Responsibility: Project Engineer / JUHI Representative
checkpoint-status |  |  | checkpoint | 2.3 Temporary Supports
label | f25fc30c-73a3-51fd-9999-778f7deca538 |  | note | Frequency: Each Lot
label | b55a71e9-70d2-5b28-bc27-21fe7783a5e6 |  | note | Acceptance Criteria: Where demolition and removal of obstructions removes or weakens support for any other part of the site including structures and services, the Contractor shall be responsible for providing temporary support until it is no longer required. The Contractor shall be responsible for protecting and supporting all existing services to remain within the works during excavation, filling and pavement construction operations.
label | 167d4e27-c445-5db9-b032-8b7783aba129 |  | note | Reference Documents: AECOM – MAP MP Spec. Cl4.6.2
label | bec09bee-5c54-5f65-a1e8-d2fff22a0438 |  | note | Inspection / Test Method: Verify
label | 58b0bf39-d4de-5173-a7b1-06ac71c8b32e |  | note | Record of Conformity: This ITP signed
label | c47f1d15-7c7f-57b3-9925-95d5af5fb227 |  | note | HP*
text | fbb2da65-86bb-53af-b521-4e1ef88483f8 |  | textbox | Responsibility: Project Engineer
checkpoint-status |  |  | checkpoint | 2.4 Removal of Existing Concrete Slabs
label | 2deddc20-69d5-5c76-8818-940e531c4b9a |  | note | Frequency: Each Lot
label | 5825dde5-bae4-57f6-8334-8a9990c53c5a |  | note | Acceptance Criteria: Where shown on the Drawings, the Contractor shall demolish and remove existing concrete slabs.
label | f8b657b8-b76c-5897-8c7a-72ea6f5e49c4 |  | note | Reference Documents: AECOM – MAP MP Spec. Cl4.6.3
label | 19b8f70c-dc06-53ac-8f09-f341b65c16e5 |  | note | Inspection / Test Method: Verify
label | 17b2101e-7fe7-5ff7-b3ac-9af1ea10dd3f |  | note | Record of Conformity: This ITP signed
label | d5b0ec20-54b7-5199-8e54-ee4a72b08aba |  | note | HP*
text | ad1533fe-e962-5736-96b9-14590d94f358 |  | textbox | Responsibility: Project Engineer / Foreman
checkpoint-status |  |  | checkpoint | 2.5 Discovery of Contaminated Materials
label | b9776bf3-4d16-5bbf-ae54-f598689a12a7 |  | note | Frequency: Each Lot
label | 2489b2c4-559b-5f4a-a236-086a8a0daba5 |  | note | Acceptance Criteria: If contaminated or hazardous materials are found, immediate notice is to be given to the Principal’s Representative. These include the following;
label | fffb07b9-4b81-53e0-9490-e4d9d1a77209 |  | note | Asbestos or material containing asbestos;
label | bd3360ea-c2d2-5d83-af24-bfc4e52de735 |  | note | Flammable or explosive liquids or gases;
label | df92ecb5-076f-5f71-a10a-637e6726e54b |  | note | Toxic, infective or contaminated materials;
label | 3253eb78-992a-56d4-a8fe-9f8ddbdc9c0a |  | note | Radiation or radioactive materials;
label | 46249e56-cc99-54c5-a556-ebb5bf79c2cd |  | note | Noxious or explosive chemicals; and
label | 062d01eb-33d0-564f-9529-337efe4dea68 |  | note | Tanks or other containers which have been used for storage of explosive, toxic, infective or contaminated substances.
label | f9a6ae22-4f66-57ba-bea6-4486c723e22c |  | note | A proposal for the procedure to remove contaminated or hazardous materials from the site to be agreed between FH, APAM and AECOM in accordance with all statutory and contractual requirements to approved locations.
label | c52889e6-3282-546a-a350-632a9bb439a7 |  | note | Reference Documents: FH-SAT10-PM-WP001 Section 3.3.12
label | 709185a9-7b07-51ba-92c7-e4f4b51e504d |  | note | Inspection / Test Method: Verify
label | 6f677ee2-dff8-5efc-85df-3c0c823432ed |  | note | Record of Conformity: This ITP signed
label | fa605ab8-a5c9-525e-bd10-3ef4edc4ecad |  | note | HP*
text | 229b5bbf-2dbf-546d-91c1-dac30c437355 |  | textbox | Responsibility: Project Engineer/ Contract Administrator
checkpoint-status |  |  | checkpoint | 2.6 Disposal of Demolished Materials
label | f8a7ae28-2bb5-5bd3-b13a-9a8437e7dafd |  | note | Frequency: Each Lot
label | 9ee927be-82d0-5cec-9f56-d0f79d7255f3 |  | note | Acceptance Criteria: The disposal of demolished materials is to be managed under the approved Construction Environmental Management Plan (CEMP).
label | 6b7c35a6-46c1-56a7-9731-81170ce4094f |  | note | Reference Documents: AECOM – MAP MP Spec. Cl4.6.5
label | 97d68a9b-96eb-5dda-936a-e943f1e6f567 |  | note | Inspection / Test Method: Verify
label | 65c3e56d-3839-5881-95f0-6875f22879f1 |  | note | Record of Conformity: This ITP signed
label | e4a3364f-6206-57cc-ad04-d212412e43b0 |  | note | HP*
text | d5dc29bb-86ba-5e29-8628-d5f7cccce997 |  | textbox | Responsibility: Project Engineer/ Foreman
checkpoint-status |  |  | checkpoint | 2.7 Completion
label | f1a67863-2b2e-593c-9ae8-4d6d1bd8f7c7 |  | note | Frequency: Each Lot
label | b4418853-4bdf-52e9-8510-8a8a9d473b2e |  | note | Acceptance Criteria: The Contractor to make the area safe and clean post completion of works. All temporary supports are to be removed at completion of demolition.
label | de928b14-7d40-5ad0-aeb7-58f515a7239d |  | note | Reference Documents: FH-SAT10-PM-WP001 Section 3.3.14
label | 9fd3cfe7-b1fc-5458-ad54-228e271ae682 |  | note | Inspection / Test Method: Inspection
label | 549ac244-e5f7-5715-b474-df56907104c0 |  | note | Record of Conformity: This ITP signed
label | 799863dc-a16e-5135-9e78-685e549f4cde |  | note | HP*
text | 02563815-3278-5248-9b28-04cc02f99c70 |  | textbox | Responsibility: Project Engineer
checkpoint-status |  |  | checkpoint | 2.8 Final Inspection
label | 55850191-5fc3-5354-9162-ae84840f0366 |  | note | The signature below verifies that this ITP has been completed in accordance with the Fulton Hogan’s Quality system Procedures and verifies lot compliance with specifications.
text | 94779ffc-7815-55b9-a453-abb74b6dbaa2 |  | textbox | Name
text | a87711dc-a41e-5d0f-b426-59c3baf12275 |  | textbox | Position
text | fcca90d0-4234-5000-83a1-7bd4cc3b083e |  | textbox | Date
holdpoint |  |  | signoff | Signature
checklist-sectioned |  |  | checklist | ITP007 - Subsoil Drainage | itp |  |  |  | Yes | ITP007 - Subsoil Drainage | e57734f0-294d-4cef-b558-ac0e4bbeeeb3
checkpoint-group |  |  | section | Preliminary Activities – Permits, Documentation, Approvals, Survey Documentation
checkpoint-status |  |  | checkpoint | 1.1 - Check for correct documentation
label | 5b6a2e2a-b403-5e02-8c56-5d3bbaf9ff0d |  | note | Frequency: Prior to commencing any activity
label | 4542c0d6-a259-5a6e-aa26-f25569602e11 |  | note | Acceptance Criteria: Current revision drawing is being used including the subcontractors copy.
label | c534a585-8964-568b-8b90-96765110ac22 |  | note | Current Revision to be obtained via Aconex
label | 7dd84eda-b8e0-5e51-a7e1-ee57a81a5312 |  | note | Reference Documents: Drawings and drawing registers on Aconex
label | 7e76edde-f0a6-51fa-9425-d96ffa380f91 |  | note | Inspection/Test Method: Visual inspection
label | 3a56c975-8561-52e9-87e3-f613e2321656 |  | note | Record of conformity: This ITP signed
label | def5e27a-18fe-57bf-b2a8-3e278cc1024e |  | note | HP*
label | 3fd9e1d9-4600-5e3a-88a2-c4247b4422f4 |  | note | Responsibility: Project Engineer
text | 23174c38-f61b-5a60-8990-ddd9b605fddc |  | textbox | Date Completed:
checkpoint-status |  |  | checkpoint | 1.2 - Implementation of all measures and controls
label | 18c2c59f-b251-57c5-be70-a4add3aa145d |  | note | Frequency: Prior to commencing any activity
label | 4091bbc0-1f38-5649-837e-39cff75be06c |  | note | Acceptance Criteria: All necessary measures and controls are being implemented, that is: PSP, EMP, TMP, SWMS & WP
label | ca746995-2b37-5b9c-b7b7-68381f1f0e28 |  | note | Reference Documents: PSP, EMP, TMP, SWMS, WP
label | bd9d9bc7-b200-5f98-9d11-10a6a230e704 |  | note | Inspection/Test Method: Visual Inspection
label | a897fe10-d3d2-5bbf-8661-df3882af1783 |  | note | Record of conformity: This ITP signed
label | a042d9c1-633a-565d-a3e7-a2631a7e66a2 |  | note | HP*
label | 2fb41ec1-9859-5684-80fe-ef1e7b00b615 |  | note | Responsibility: Project Engineer
text | 49334a5b-8974-54c5-b25e-855bbcd1004a |  | textbox | Date Completed:
checkpoint-status |  |  | checkpoint | 1.3 - Definition of the work area
label | 2f5b2dd6-e0c0-5798-b367-ad6b684440da |  | note | Frequency: Prior to commencing any activity
label | f40b5390-6b3f-58e7-8867-1fdf80552911 |  | note | Acceptance Criteria: Work area has been cleared and surveyed (marked on site). Limits of excavation clearly defined.
label | 0313104d-546b-516a-9ba3-f13a365f54ab |  | note | Reference Documents: Drawings
label | a9401fc3-4051-5f34-99dd-933f4567a579 |  | note | Inspection/Test Method: Visual Inspection
label | ac510b73-4371-54b9-8a50-811c8f730dca |  | note | Record of conformity: This ITP signed
label | e4a2fb78-9733-5bb5-a1fc-a7d2d7f1e8d3 |  | note | HP*
label | cf9165ae-4f8e-560b-959c-65b4a70bef83 |  | note | Responsibility: Project Engineer
text | 6e313e29-d036-5555-a414-0242723c0cd7 |  | textbox | Date Completed:
checkpoint-status |  |  | checkpoint | 1.4 - Service Locations
label | cb1c063e-2d9a-5ff1-bcca-4decf64b99aa |  | note | Frequency: Prior to commencing any activity
label | 7bd409a2-bdf2-5c17-8e5c-7a94508b7dda |  | note | Acceptance Criteria: The location of services are to be found and marked on the ground within the works, and within 20m on any intrusive works.
label | 3a3e7704-901b-51bc-986c-8e9951f894e2 |  | note | Services located within the works area to be exposed using approved locating methods, in the presence of an Airport Rep. where required.
label | 5fd1c13a-f826-54b9-baf4-004972a6013d |  | note | Service Locations and Depths recorded by surveyor where required
label | aafe9466-d9a2-5796-9aaa-36da5ded1840 |  | note | Ensure no mechanical excavation within 5m of Fuel Lines if applicable.
label | 289578b6-c5b9-5e57-aae3-67b00ab16129 |  | note | Reference Documents: AECOM- MAPMP Spec. Cl 3.2.2
label | 6dd79550-d84b-5ee0-80dd-5cdce5991dea |  | note | Inspection/Test Method: Visual Inspection
label | 797dc0ef-e87b-54a3-a55b-6cd31e3dec06 |  | note | Record of conformity: This ITP signed
label | e9cb3850-c3f8-5fd6-a88d-bc605ac07d20 |  | note | HP*
label | 9b236dcf-47fc-5e31-833b-863f41370f79 |  | note | Responsibility: Project Engineer
text | 167b416e-f71b-5936-8aa0-6b0361838917 |  | textbox | Date Completed:
checkpoint-group |  |  | section | Subsoil Material
checkpoint-status |  |  | checkpoint | 2.1 - Subsurface Drainage Pipes
label | a508b945-24d2-5771-8a67-a777afae5b2f |  | note | Frequency: Prior to Start
label | 9d8887a7-528f-5727-8f86-59566008cd97 |  | note | Acceptance Criteria: Subsoil Pipe material to be 160mm Slotted Agi Class 1000 SN20, or approved alternative.
label | df46b0e9-5a6e-5f61-bf35-7c5f494719ae |  | note | Reference Documents: AECOM- MAPMP Clarifications Register #128
label | 44996c64-5c3b-529c-b768-395c5b86b38b |  | note | Inspection/Test Method: Verify
label | f9b80023-eb1f-55f2-819a-ad6703855dd5 |  | note | Record of conformity: This ITP signed
label | 4f2a083a-f10d-5673-9978-7696983d01b6 |  | note | HP*
label | 7f630d80-af5b-59d3-9413-bf93fbbb3fa0 |  | note | Responsibility: Project Engineer
text | d6df6a40-e0c3-5824-9523-7d5c479d200f |  | textbox | Date Completed:
checkpoint-status |  |  | checkpoint | 2.2 - Bedding & Backfill Material
label | c14e6f8c-8688-59ce-80ce-fba68f6a7f5f |  | note | Frequency: Each Lot
label | 2e2bf9e0-5dea-5062-b1a2-82a8cd22e904 |  | note | Acceptance Criteria: Bedding material: 20mm Aggregate from Holcim, or approved alternative
label | a5340757-b60e-5198-b735-cbc7c2593d99 |  | note | Backfill material: 5% cement 40mm No Fines Concrete from Hanson, or approved alternative.
label | 303365c7-177e-5d14-805e-126a71b81204 |  | note | Reference Documents: AECOM- MAPMP Spec. Cl 17.4.2 & Design Drawings
label | ba202f4a-579e-5a4f-b828-8fa78f208268 |  | note | Inspection/Test Method: Verify
label | a215026c-95bb-56ba-9742-09e1a188b30e |  | note | Record of conformity: This ITP signed
label | 30fa87f9-26a4-5840-94cf-909b5ac7e811 |  | note | HP*
label | 6b5d364e-e753-5c5f-8b15-7190fb8497ae |  | note | Responsibility: Project Engineer
text | 03435f51-76b3-51a2-b721-883197891907 |  | textbox | Date Completed:
checkpoint-group |  |  | section | Excavation and Installation
checkpoint-status |  |  | checkpoint | 3.1 - Trench Excavation
label | 0a776f7e-c723-5f05-8604-2abe2a27ef9a |  | note | Frequency: Each Lot
label | 8e9b16d8-1d1c-51dd-9b01-071980edef32 |  | note | Acceptance Criteria: Trenches excavated to dimensions and grades shown on design drawings. Excavation to allow for 100mm bedding material.
label | 9018ff92-630a-5621-a94a-7f94138c0816 |  | note | The base of the trench shall be inspected to verify compliance with the requirements in this clause prior to placing bedding in completed excavations.
label | eaaa948f-c0d5-5a96-88f2-97c5aa212482 |  | note | Excavated material disposed per approved CEMP.
label | 10745fc3-336c-5d4a-82bb-f2c2da85021d |  | note | HP: Base of trench inspected prior to placing bedding material.
label | 980c5d61-6901-54d2-bad8-a8505cea8152 |  | note | Reference Documents: Drawings & AECOM – MAP MP Spec. Cl 17.5.3, 17.5.4, 17.5.5 & 17.5.7 & Vic Roads 702.08
label | 2acb3a43-33b9-54ae-9a44-ff2c19cc0e5c |  | note | Inspection/Test Method: Verify
label | 0580821d-f7c9-5d6b-a562-75d269f47484 |  | note | Record of conformity: This ITP Signed
label | c062ecd0-2f53-58c6-a024-abc79c3ce336 |  | note | HP
label | 39ae18ca-0b48-5433-9f96-a95beb76915e |  | note | Responsibility: Project Engineer / Principal’s Representative
text | 4039f813-38fc-54a0-a78c-97167fb177d8 |  | textbox | Date Completed:
holdpoint |  |  | signoff | HOLD POINT
checkpoint-status |  |  | checkpoint | 3.2 - Geotextile Filter Wrap
label | e79be39c-2d5f-5ed3-a942-30dcb5325997 |  | note | Frequency:
label | 9cddc13f-c45a-5356-9c99-fc50ab50fb73 |  | note | Acceptance Criteria: A24 or approved equivalent (Refer to drawings).
label | 8571017d-3f68-5004-800b-84cc1ef14661 |  | note | Geotextile wrap to be in contact with a trench wall, the trench wall shall be excavated to allow the geotextile to be in close contact with the wall when the granular filter material is placed against the geotextile.
label | 112b90a3-8d24-53be-b3f9-f796ded1c8b7 |  | note | Reference Documents: Drawings & Vic Roads 702.08
label | e0b3389a-35c0-5e5c-a2b0-9c4c0bc2e348 |  | note | Inspection/Test Method: Verify
label | 1e4f7c5b-f085-5ac2-b471-b6be70cad73b |  | note | Record of conformity: This ITP Signed
label | d8d05dbe-a198-5c19-9178-a47bd147c170 |  | note | HP*
label | d6646740-265d-502b-941e-f14654745d41 |  | note | Responsibility: Project Engineer
text | bd286cb8-e39d-5eeb-a200-ebccb6ac2de8 |  | textbox | Date Completed:
checkpoint-status |  |  | checkpoint | 3.3 - Bedding, Laying Pipes & Backfill
label | 8084b596-d7e4-53e0-86e1-0afa51e6a05d |  | note | Frequency: Each Lot
label | 4633bd2d-4c6f-59e6-af4b-b97227aeed64 |  | note | Acceptance Criteria: In accordance to the dimensions outlined in the drawings.
label | f427e462-594d-55ee-974f-ab2e9a89474e |  | note | Tolerances:
label | 9f8779fd-b50c-566e-89d5-f2a0758544e9 |  | note | +/- 50mm from specified line
label | f5214cca-9f72-547f-8fa2-acfbc7d01bdb |  | note | +/- 25mm from specified level
label | 75b146c8-44fb-5075-9a50-8e312608880d |  | note | Minimum Grade 1 in 250, unless approved or designed otherwise.
label | 8085079f-cdba-553f-aca8-30832a0eae81 |  | note | Bedding to be tamped and screeded or graded to level.
label | 7ecea380-ad54-57e2-8a4a-a38d5ff21fdc |  | note | Reference Documents: Drawings & AECOM – MAP MP Spec. Cl 17.4.2, 17.5.4, & Vic Roads 702.03
label | 1b6881d7-c020-559d-8c9d-89b4e99c817c |  | note | Inspection/Test Method: Visual Inspection
label | ebad9195-643b-57ad-b4f0-2108a3de6f3f |  | note | Record of conformity: This ITP Signed
label | 5ddda5be-3419-5885-a676-2820af24ccc9 |  | note | HP*
label | 982d8c8f-86a3-5d5c-8a61-eda59b1f7855 |  | note | Responsibility: Project Engineer
text | 01435ac2-3330-5746-8375-e3e586b2e6b4 |  | textbox | Date Completed:
checkpoint-status |  |  | checkpoint | 3.4 - Laying and Jointing of Pipes
label | 15d492fe-d912-5a3c-ba1b-3349833f24cb |  | note | Frequency: Each Lot
label | 938e8cae-6309-5fee-9705-80ac7a04d9ea |  | note | Acceptance Criteria: Pipes laid at the depths and lines indicated on drawings.
label | 9bd245a6-3118-54ab-9166-8e9d215dc249 |  | note | Reference Documents: Drawings
label | 734abcb4-bcf4-5e70-88f5-bc15ba527e69 |  | note | Inspection/Test Method: Visual Inspection
label | 79f7cbe1-f274-5966-a776-3959e9a17bd8 |  | note | Record of conformity: This ITP Signed
label | 86c7289a-2d3d-5f6c-9855-c814e9313800 |  | note | HP*
label | 4e376054-e1f0-5da1-901a-3480a40a752d |  | note | Responsibility: Project Engineer
text | c13b99e0-8696-5fbc-af1a-9cd575cec592 |  | textbox | Date Completed:
checkpoint-status |  |  | checkpoint | 3.5 - Subsoil Drain Outlet
label | 36c77c59-34fa-559a-a544-e5f558a4b6df |  | note | Frequency: Each lot
label | 748fc75c-be93-50e0-b82d-da2a506ca492 |  | note | Acceptance Criteria: Outlets from subsoil drains shall be constructed to discharge into stormwater drainage system.
label | 8d6e2e3a-f842-5d91-9d8a-3a43e197e92c |  | note | Reference Documents: AECOM – MAP MP Spec. Cl 17.5.6
label | c8bee04e-f3ae-50f5-81aa-0f40ddd9758c |  | note | Inspection/Test Method: Verify
label | 83c7d23d-f4dc-5f4f-b0fd-8416339c0474 |  | note | Record of conformity: This ITP Signed
label | d0dea2d6-487b-5645-a52e-b41bf0f78bd4 |  | note | HP*
label | 79a41126-3159-5cb3-89d0-556ed4653f15 |  | note | Responsibility: Project Engineer
text | 2e92ea2a-dfea-5e4f-adc6-39cb0de9dc98 |  | textbox | Date Completed:
checkpoint-status |  |  | checkpoint | 3.6 - Flush out risers
label | 5630e286-1700-56a0-9076-5cb9e8aa8850 |  | note | Frequency: Each Lot
label | 54184dab-c79e-5b16-b76c-a2dd43354bcd |  | note | Acceptance Criteria: To be the same diameter as the subsoil pipe and be installed in locations indicated on the drawings.
label | ecde259f-5d71-5ce9-b889-0c50252933c8 |  | note | Reference Documents: Drawings & Vic Roads 702.10
label | 3b160625-3552-53c8-93e7-6266d19e901a |  | note | Inspection/Test Method: Visual Inspection
label | 78c84937-6174-5989-8732-a7104378f084 |  | note | Record of conformity: This ITP Signed
label | 7744943e-6f26-5c89-9fb7-ce62712dd0e6 |  | note | HP*
label | a0786261-fe31-5d2e-beb1-b33cf967bfbf |  | note | Responsibility: Project Engineer
text | 1df0b0f1-f36c-50d0-ac3a-1be55c2a43a7 |  | textbox | Date Completed:
checkpoint-status |  |  | checkpoint | 3.7 - Flushing Test
label | 4829e033-5804-5426-832f-6e959a94cebe |  | note | Frequency: Each Lot
label | 8678ba07-7c02-5348-b43d-83e5e93eaaa6 |  | note | Acceptance Criteria: A flushing test shall be carried out on each subsurface drainage line after completion of subsurface drains, flushers and outlets.
label | 3d2ec975-3391-53bd-9bad-f2dee1249170 |  | note | The test shall be witnessed by the Principal’s representative.
label | 7edae30c-dc18-57c6-84c1-655174d7774e |  | note | Reference Documents: Drawings & Vic Roads 702.09
label | 22a6288e-3b45-543f-b61d-863103942f8a |  | note | Inspection/Test Method: Visual Inspection
label | cab3d557-59cb-5824-a3db-eb625233813d |  | note | Record of conformity: This ITP Signed
label | fa510215-31bb-551d-9d98-e0181172e9bd |  | note | WP
label | 1b0f5055-1500-527b-bdbb-c1d6e9a09164 |  | note | Responsibility: Project Engineer/ Principal’s Representative
text | bb96f267-fb5e-5a06-9848-116f2cb16ca7 |  | textbox | Date Completed:
checkpoint-group |  |  | section | Post Construction
checkpoint-status |  |  | checkpoint | 4.1 - Records
label | fc7c71ca-6c3c-5b7b-96c2-c1b4a3b2e741 |  | note | Frequency: Each Lot
label | e8185930-b708-555c-a37b-e63029a9fed9 |  | note | Acceptance Criteria: Levels and alignment recorded in as built documentation and provided to superintendent.
label | 3748c4b8-7ad2-5f69-8d26-56557f6e8265 |  | note | Reference Documents: Vic Roads 702.03
label | 2d6edebc-fd9e-5be9-9a04-862a59871adb |  | note | Inspection/Test Method: Inspection
label | d66638aa-0b2f-5d11-82e4-de34a65fe4c1 |  | note | Record of conformity: Aconex Correspondence
label | 93b1a84e-3f0a-5e18-b0e5-022828dbfe55 |  | note | SCP
label | 84a2c200-8955-5d1e-9d52-ce2f2e8bcabc |  | note | Responsibility: Project Engineer
text | 278f70ec-c2d4-517e-b87c-4c1dff607a82 |  | textbox | Date Completed:
checkpoint-status |  |  | checkpoint | Final Inspection
label | 23be32d7-9996-502c-9d71-74193f749afe |  | note | On behalf of Fulton Hogan it is hereby certified that the Works represented by the items of work listed have been tested in accordance with the Project Quality Plan and conform in all respects with the requirements of the Contract.
text | c007c705-0273-5953-aff1-f27e0121d636 |  | textbox | Name:
text | 7cfd5512-b189-56fc-a4a7-5f7ceb3d99ca |  | textbox | Position:
holdpoint |  |  | signoff | Add Signature
checklist-sectioned |  |  | checklist | ITP029 - Native Grass Inspection | itp |  |  |  | Yes | ITP029 - Native Grass Inspection | f8154b30-bc33-4ec3-88f4-576d421b5503
checkpoint-group |  |  | section | ITP 029 - Native Grass Inspection
checkpoint-status |  |  | checkpoint | 1.1 Check for correct documentation
label | e89a71d8-1812-5ebf-893e-fe66a7b5ebcd |  | note | FREQUENCY: Prior to site establishment
label | 9150a0b7-eded-50b8-a6e7-73b4a3d46b4d |  | note | ACCEPTANCE CRITERIA: Review whether a preliminary report has been completed for the project which will outline where the Significant native grasses are and what protection has been specified. (Example: Biosis report for the EPBC referral for a Part13 permit to remove native grasses)
label | bff5cfb0-d8fe-5d48-b3bd-e13ddc83ea1d |  | note | REFERENCE DOCUMENTS: Consultant reports
label | 8c1b9474-82d7-5179-a286-b4c5252c5dca |  | note | INSPECTION/TEST METHOD: Visual inspection
label | 30309ca6-cf6b-57bf-8b27-7aabb9f75c2a |  | note | RECORD OF CONFORMITY: This signed ITP
label | a5cc649a-11f6-5d30-b9f1-52f2f96cff18 |  | note | HP*
label | acb0cd19-13af-51f2-b919-c144b6a7eddd |  | note | RESPONSIBILITY: Project Engineer
text | c1ef5105-9877-5442-9e6b-2daac305375c |  | textbox | Date Completed:
checkpoint-status |  |  | checkpoint | 1.2 Check the Biosis Google Earth Mapping
label | 2b2c7d77-1b9d-5975-85c0-0439d3e20624 |  | note | FREQUENCY: Prior to site establishment
label | 77d23e6c-aa55-5da5-90ff-359aed2fb9e5 |  | note | ACCEPTANCE CRITERIA: Review the Biosis Google mapping which outlines the boundary of the native grasses at the time they were mapped. (Note: that mapping only occurs approximately every 5 years, so the exact boundary will need to be defined)
label | fd648229-4d9b-5e58-bd12-a3686553ee56 |  | note | REFERENCE DOCUMENTS: Biosis Google Earth Mapping
label | 46f5f9e1-9eea-59a2-a13e-7797c2e01909 |  | note | INSPECTION/TEST METHOD: Visual inspection
label | 20d83f7c-c0b9-5f0f-88f6-80c40f765a00 |  | note | RECORD OF CONFORMITY: This signed ITP
label | 70015dd0-d8f0-5fdf-a6ce-87e551acaf51 |  | note | HP*
label | b6ac956a-c290-50c1-ac9e-d0c305569612 |  | note | RESPONSIBILITY: Project Engineer
text | 57fd02e7-cb07-5fce-92c8-edb039ec08c0 |  | textbox | Date Completed:
checkpoint-status |  |  | checkpoint | 2.1 Biosis Inspection
label | dda023b1-be24-5913-b3b6-4758b25e6eba |  | note | FREQUENCY: During site establishment
label | c434d618-e691-586f-b9ac-2a18630c3bb0 |  | note | ACCEPTANCE CRITERIA: On approval from APAM, arrange for Biosis to conduct an inspection of the site to confirm the boundary of the Significant native grasses which need to be protected. The surveyor can then mark out these areas with Biosis to ensure the boundary is being protected. Place bollards along the boundary area.
label | 01e73935-1462-545c-a846-04471215f6f6 |  | note | REFERENCE DOCUMENTS: Biosis Google Earth Mapping
label | 87b79302-c38d-5509-af7d-bb79a4c780ac |  | note | INSPECTION/TEST METHOD: Visual inspection compared against the Google earth mapping
label | 9f40b4ca-c7d5-55dd-9f42-3247deb6f156 |  | note | RECORD OF CONFORMITY: This signed ITP
label | 82e80c47-7a8b-56cc-bcb5-57c645a00bc1 |  | note | HP
label | c03c178c-33ab-5aa8-a881-41367096e7ad |  | note | RESPONSIBILITY: Environmental Manager / Biosis Botanist Surveyor
text | 6ec20f9f-b987-5d17-9e89-c7639d58aa5c |  | textbox | Date Completed:
holdpoint |  |  | signoff | REQUEST HOLD POINT SIGN OFF
checkpoint-status |  |  | checkpoint | 3.1 Mark out the exact significant Native Grass Boundary Area
label | 7fa31439-23f1-50a4-b8de-e56d357ea116 |  | note | FREQUENCY: Prior to commencing any activity
label | d0ec0b00-53b5-535c-8913-a0bf555ba3f5 |  | note | ACCEPTANCE CRITERIA: Work with the surveyor to mark out the Significant Native grass boundary. Signage will be placed onto the bollards stating ‘Native Grass Boundary Area.’ NTGVVP Nationally Significant Grasses to protect within this area.
label | bfa56d8f-1756-5515-8afc-28800dcafc12 |  | note | REFERENCE DOCUMENTS: EMP
label | 72185d2a-126d-5115-b612-f76f84d62f91 |  | note | INSPECTION/TEST METHOD: Inspect
label | 91f92438-569a-520b-83b6-316f9ff8056d |  | note | RECORD OF CONFORMITY: This signed ITP
label | 386d547c-18ea-5838-80dd-e469dfb68583 |  | note | HP*
label | 9ce694a8-e022-585e-91b8-92a8d2a62add |  | note | RESPONSIBILITY: FH Environmental Manager Surveyor FH Project Engineer
text | 32ee6ee4-c1b8-5aae-b5c1-2204ac4f41f4 |  | textbox | Date Completed:
checkpoint-status |  |  | checkpoint | 3.2 Use temporary fencing and signage to block access to the Significant native grasses where we are working in close proximity.
label | e0dbf85f-f9c1-5fe9-b92d-2d3dbb7657a5 |  | note | FREQUENCY: Prior to commencing any activity
label | 7a75d10f-5db8-5f19-9511-1f7fd84f107f |  | note | ACCEPTANCE CRITERIA: The Botanist (Biosis) report may define what type of protection is required for the Native grasses. For works in close proximity to the native grasses, use temporary fencing to block access with signage stating “Vegetation Protection – No Go Zone.” This fencing will be installed at a distance away from the actual native grass boundary to act as a ‘buffer zone’ but still allows works to progress.
label | 0623a0c2-9aca-5b6a-9fc5-cefe56c64564 |  | note | REFERENCE DOCUMENTS: Biosis report, EMP
label | 629f4e89-7eac-57ea-b977-68fa77936048 |  | note | INSPECTION/TEST METHOD: Inspect
label | b80d6f7b-5a1e-59e8-9420-d39140ec04d6 |  | note | RECORD OF CONFORMITY: This signed ITP
label | f9c78cbc-dcc9-5548-a18c-36ed2b6f3ab8 |  | note | HP*
label | a8041c53-c56e-5cde-87ed-dd7b1ba6fdf9 |  | note | RESPONSIBILITY: FH Project Engineer Surveyor
text | 754a31e9-ed7d-5121-b0f1-7677ec5beab7 |  | textbox | Date Completed:
checkpoint-status |  |  | checkpoint | 3.3 Implementation of control measures required to protect the significant native grasses around our project area
label | 1baa585b-7ce1-54bd-8bfd-5ec0073cd1da |  | note | FREQUENCY: Prior to commencing any activity
label | 5eef8a68-bb97-5e67-b84b-43ff7b5ad61d |  | note | ACCEPTANCE CRITERIA: An exclusion zone will be set up with bollards and signage stating “Vegetation Protection – No Go Zone” between our works area and the native grass boundary area to act as a ‘buffer zone.’ Allow a minimum 2.5m buffer zone.
label | 38216f3c-a78e-5be3-90a4-583df62365c6 |  | note | REFERENCE DOCUMENTS: Biosis Zulu report, EMP
label | f3a158ac-90cb-581d-aa23-0d4986e3de82 |  | note | INSPECTION/TEST METHOD: Inspect
label | a91a0c92-0b30-5fab-9331-557fdb42204a |  | note | RECORD OF CONFORMITY: This signed ITP
label | b91dd3a7-dd39-5adc-b908-1c803369548f |  | note | HP
label | 13cc02ba-12a5-57c8-8dc4-0494f90e0b8c |  | note | RESPONSIBILITY: FH Project Engineer
text | 36c90da2-8ea2-536a-9f3d-ea062d8c6ee8 |  | textbox | Date Completed:
holdpoint |  |  | signoff | REQUEST HOLD POINT SIGN OFF
checkpoint-status |  |  | checkpoint | 4.1 Release of Hold Point for Native grass Protection
label | 8455e692-7786-5149-b761-3760dc89917a |  | note | FREQUENCY: Prior to commencing construction
label | 22005afc-7df3-55ce-846a-50dca9178719 |  | note | ACCEPTANCE CRITERIA: Arrange a joint inspection with APAM and the botanist (Biosis) to conduct a visual inspection to confirm that the native grasses are protected with the required temporary fencing or bollards and correct signage where required. All parties are to sign off on the separate Hold Point Release document
label | 11c09682-e796-5cfc-80a3-46658326aef9 |  | note | REFERENCE DOCUMENTS: EMP Botanist report
label | 99e4bf18-7704-51c7-8340-ce4ff6c7be97 |  | note | INSPECTION/TEST METHOD: Visual
label | d606f6ba-4222-5770-8dfc-6488e0055cfb |  | note | RECORD OF CONFORMITY: This signed ITP
label | a6d01b1e-16a1-5e64-a4d9-934e6ed3129a |  | note | HP
label | 4672703b-d4a1-50ab-86e7-11631c27d9e6 |  | note | RESPONSIBILITY: Biosis APAM Fulton Hogan Environmental Manager or Project Manager
text | ef568c5b-41a9-5dcf-a80f-dfbe15744958 |  | textbox | Date Completed:
holdpoint |  |  | signoff | REQUEST HOLD POINT SIGN OFF
checkpoint-status |  |  | checkpoint | FULTON HOGAN FINAL INSPECTION - "On behalf of Fulton Hogan, it is hereby certified that the Works represented by the item of work listed have been tested in accordance with the Project Quality Plan and conform in all respects with the requirements of the Contract".
text | 9bb01fc9-20cd-59d3-b03e-201ea6c9ca0c |  | textbox | Name:
text | 2c8d4bfe-d095-5aaa-b52d-9528d3a51307 |  | textbox | Position: