## Structure
Tier 1 | Tier 2 | Tier 3 | Tier 4 | Tier 5 | Tier 6 | Tier 7 | Instruction to CONQA | Checklist Name
ELECTROLUX
| Stage 1 | site services | [5 empty] | ducting checklist
office area
Cable containment
|  |  |  | Catenaries |  |  | please add: | Catenaries
|  |  |  | Cable tray |  |  | please add: | Cable tray
|  |  |  | conduit |  |  | please add: | conduit
|  |  |  | floor boxes |  |  | please add: | floor box
|  |  |  | trunking |  |  | please add: | trunking
First fix
|  |  |  | Flush boxes |  |  | please add: | Flush box
|  |  |  | Cabling | Power |  | please add: | Power circuits first fix
[5 empty] | Lighting |  | please add: | Lighting circuits first fix
Second fix
|  |  |  | Switchboard |  |  | please add: | Switchboard
|  |  |  | Power |  |  | please add: | Power circuits second fix
|  |  |  | Lighting |  |  | please add: | Lighting circuits second fix
|  |  | Documentation |  |  |  | please add: | Documentation
| Stage 2 | same as stage 1
| main switchboard | [6 empty] | MSB checklist

## Checklists
Type | Name | Values
checklist | underground services
checkpoint | Md, hd, orange, green, size
checkpoint | Depth = >600 power >450 comms
checkpoint | Set out marked, and all services located
checkpoint | Draw tape present
checkpoint | Ends covered (future) & exposed (light posts, signs etc)
checkpoint | Danger tape @200mm cover / mag slab
checklist-flat | Catenaries
checkpoint | Supported correctly
checkpoint | Correct locations
checklist-flat | Cable tray
checkpoint | Installed correct location
checkpoint | Installed correct height
checkpoint | Installed correctly
checklist-flat | floor box
checkpoint | floor box type identified Surface/ recessed
checkpoint | cut out size correctly marked for bulider
checkpoint | location marked
checkpoint | duct size correct for cable
checklist-flat | Trunking
checkpoint | size / type / category correct
checkpoint | location and height confirmed
checkpoint | droppers / cable acess installed
checkpoint | installed level and flush
checklist-flat | Conduits
checkpoint | level / square
checkpoint | correct size
checkpoint | fixings
checklist-flat | Flush boxes
checkpoint | Correct location
checkpoint | Correct height
checklist-flat | Power circuits first fix
checkpoint | Cable schedule
checkpoint | Cable size correct
checkpoint | Cabling to correct locations
checkpoint | droppers / starters wired
checkpoint | Tv locations wired
checklist-flat | Lighting circuits first fix
checkpoint | Cabling to correct location as per plan
checkpoint | Emergency lighting cabelled
checkpoint | Number of fittings correct
checkpoint | Local switch wire installed
checkpoint | Sensor control wire installed
checkpoint | Cabinet lighting confirmed / cabled
checklist | Data 1st fix
checkpoint | data cables inplace to location
checkpoint | labelled correctly x 2
checkpoint | cables to floor box
checkpoint | data tv locations
checkpoint | wap locations wired
checklist-flat | Power circuits second fix
checkpoint | Outlets installed, level and labelled
checkpoint | Starters installed
checkpoint | Floor boxes fit off
checkpoint | droppers / starters wired and installed
checkpoint | Tv locations fit off
checklist | data 2nd fix
checkpoint | outlets installed and labellled
checkpoint | data floor boxe installed
checkpoint | cabinet fit off
checkpoint | wap installed
checklist-flat | Lighting circuits second fix
checkpoint | Correct light type installed
checkpoint | Correct number installed
checkpoint | Correct location
checkpoint | Local switching installed
checkpoint | Sensor installed
checkpoint | Emergency lighting type installed
checklist-flat | Switchboard
checkpoint | Cables dressed
checkpoint | All cables terminated
checkpoint | Circuits labelled
checkpoint | Circuits tested
tickbox | IRT Mohm
tickbox | Earth Loop
tickbox | Rcd
tickbox | Polarity
tickbox | Visual
tickbox | bonding
tickbox | Earth cont.
checklist-flat | Documentation
checkpoint | C.O.C.
checkpoint | R.O.I.
checkpoint | Test sheets complete
checkpoint | As builts complete
checkpoint | PS3
checkpoint | Emergency lighting labelled
checkpoint | EM test sheets
checklist | MSB checklist
checkpoint | as built refrenced
checkpoint | materials ready
tick box | lugs
tick box | heat shrink
tick box | crimp links
tick box | cable for sub circut joints
checkpoint | polarity correct
checkpoint | terminals tight
checkpoint | Insulation test
checkpoint | subcircuts labelled
checkpoint | earthing / bonding

## Blank - New Project Structure
Tier 1 | Tier 2 | Tier 3 | Tier 4 | Tier 5 | Tier 6 | Tier 7 | Instruction to CONQA | Checklist Name