## Resources
Rich Type | Id | Warnings | type | name | values | prefix | postfix | Usage Count | User Addable | Template Name | Template Id
checklist-sectioned |  |  | checklist | LM-FOR-50-ITR-303.3 Ewis Installation Fit Off |  |  |  |  | Yes | LM-FOR-50-ITR-303.3 Ewis Installation Fit Off | 115fe391-8065-4bc0-8df1-50bc0fae3738
checkpoint-group |  |  | section | EWIS Fit-Off
checkpoint-status |  |  | checkpoint | Have all devices been installed in the correct position with no obstructions
checkpoint-status |  |  | checkpoint | Have all speakers / horns been installed in the correct location
checkpoint-status |  |  | checkpoint | Have all warden intercom points been installed in the correct location
checkpoint-status |  |  | checkpoint | Have all emergency call points been installed in the correct location
checkpoint-status |  |  | checkpoint | Have all strobes been installed in the correct location
checkpoint-status |  |  | checkpoint | Have all background music points been installed in the correct location
checkpoint-status |  |  | checkpoint | Have all microphone points been installed in the correct location
checkpoint-status |  |  | checkpoint | Have the ELV and LV segregation rules been applied as per AS/CAS 009 (including 90 degrees crossovers) – Double check to make sure no other trades have been in after warning system works
checkpoint-status |  |  | checkpoint | Have all cables and conduits been installed in the correct position for devices
checkpoint-status |  |  | checkpoint | Have all devices been terminated for testing purposes
checkpoint-group |  |  | section | Cable Feeds
checkpoint-status |  |  | checkpoint | Have all cable supports been connected to the first device
checkpoint-status |  |  | checkpoint | Have all end of lines been fitted and measured
checkpoint-status |  |  | checkpoint | Have cables feeds been connected at the panel
checkpoint-group |  |  | section | Visual Check
checkpoint-status |  |  | checkpoint | Check that no other services are run with or attached to occupant/emergency warning cables or devices
checkpoint-status |  |  | checkpoint | Check that no cables or devices have been damaged
checkpoint-status |  |  | checkpoint | Check that all final device locations are correct and match up with the “For Construction Drawings” and “Reflected Ceiling Plans”
checkpoint-status |  |  | checkpoint | Have devices and readings been noted on “As Constructed Drawings” for handover
checkpoint-status |  |  | checkpoint | Have all stickers been installed to fire rated walls and smoke walls for penetrations
checkpoint-status |  |  | checkpoint | Has photographic evidence been taken and recorded for all penetrations
checkpoint-group |  |  | section | Completion
checkpoint-status |  |  | checkpoint | Sign Off below - pass once complete
holdpoint |  |  | signoff | Sign-Off - click to Add signature(s)
checklist-sectioned |  |  | checklist | LM-FOR-50-ITR-303.2 Ewis Installation |  |  |  |  | Yes | LM-FOR-50-ITR-303.2 Ewis Installation | 1649e9d2-7c70-4539-ae95-e49360961ddf
checkpoint-group |  |  | section | Cabling
checkpoint-status |  |  | checkpoint | Have all cable supports been installed in the correct position with no obstructions
checkpoint-status |  |  | checkpoint | Have all cables been cable tied to soffit / catenary wire with no sagging or obstructions
checkpoint-status |  |  | checkpoint | Have all cables been installed for speakers and horns
checkpoint-status |  |  | checkpoint | Have all cables been installed for warden intercom points
checkpoint-status |  |  | checkpoint | Have all cables been installed for emergency call points
checkpoint-status |  |  | checkpoint | Have all cables been installed for strobes
checkpoint-status |  |  | checkpoint | Have all cables been installed for background music inputs
checkpoint-status |  |  | checkpoint | Have all cables been installed for microphone inputs
checkpoint-status |  |  | checkpoint | Have the ELV and LV segregation rules been applied as per AS/CAS 009 (including 90 degrees crossovers)
checkpoint-status |  |  | checkpoint | Have all cables been installed in the correct position for devices
checkpoint-status |  |  | checkpoint | Have all cables been joined through for testing purposes or fitted with end of line devices
checkpoint-group |  |  | section | Cable Feeds
checkpoint-status |  |  | checkpoint | Have all cable supports been installed in the correct position with no obstructions
checkpoint-status |  |  | checkpoint | Have all cable feeds been installed in the correct position
checkpoint-status |  |  | checkpoint | Have all cables been tied to cable tray with steel ties with no sagging or obstructions
checkpoint-status |  |  | checkpoint | Have all cable trays been installed correctly and secured including joiners and bends
checkpoint-status |  |  | checkpoint | Have the modified cable trays been re-galvanized
checkpoint-group |  |  | section | Visual Check
checkpoint-status |  |  | checkpoint | Check that no other services are run with or attached to occupant/emergency warning cables
checkpoint-status |  |  | checkpoint | Check that no cables have been damaged
checkpoint-status |  |  | checkpoint | Check that all final cable locations are correct and match up with the “For Construction Drawings” and “Reflected Ceiling Plans”
checkpoint-status |  |  | checkpoint | Have all cable runs, cable trays and penetrations been mark on “As Constructed Drawings” for handover
checkpoint-status |  |  | checkpoint | Have all stickers been installed to fire rated walls and smoke walls for penetrations
checkpoint-status |  |  | checkpoint | Has photographic evidence been taken and recorded for all penetrations
checkpoint-group |  |  | section | Completion
checkpoint-status |  |  | checkpoint | Sign Off below - pass once complete
holdpoint |  |  | signoff | Sign-Off - click to Add signature(s)
checklist-sectioned |  |  | checklist | LM-FOR-33-ITR-401 Sprinkler & Hydrant hydrostatic test |  |  |  |  | Yes | LM-FOR-33-ITR-401 Sprinkler & Hydrant hydrostatic test | 1977f70e-428b-4f2f-9fb2-4c125c461856
checkpoint-group |  |  | section | Guidelines
checkpoint-status |  |  | checkpoint | Guidelines understood - Pass once read
label | 96bd7276-beef-523e-98b9-9da245a63cb3 |  | note | Guidelines: Fire Sprinkler Systems – 1600 kPa or 400 kPa above the maximum static pressure for a duration of 2 hours (Check notes on Construction Drawing for nominated test pressure)
label | a98cfa63-41fa-5983-8382-39c2359f5260 |  | note | Fire Hydrant Systems (Low Rise) – 1700 kPa or 1.5 times the design pressure for a duration of 2 hours (Check notes on Construction Drawing for nominated test pressure)
label | 8d48a861-b638-5b8e-8f82-f87018fd8cf9 |  | note | Playhouse Theatre – 1200 kPa or 1.5 times the design pressure for a duration of 2 hours. (Check notes on Construction Drawing for nominated test pressure)
checkpoint-group |  |  | section | Rough In Only OR Rough In & Fit Off Together
checkpoint-status |  |  | checkpoint | First Sighting - Pass once entered - attach photo of pressure gauge and builder sign off if required
checkpoint-status |  |  | checkpoint | Second Sighting - Pass once entered - attach photo of pressure gauge and builder sign off if required
checkpoint-group |  |  | section | Fit Off (if required ie if not covered by the above section)
checkpoint-status |  |  | checkpoint | Subsequent Sighting - Pass once entered - attach photo of pressure gauge and builder sign off if required
checklist-sectioned |  |  | checklist | LM-FOR-40-ITR-302.5 Booster Assembly |  |  |  |  | Yes | LM-FOR-40-ITR-302.5 Booster Assembly | 20b34693-9112-40d5-86a8-d8b614c93b12
checkpoint-group |  |  | section | Installation
checkpoint-status |  |  | checkpoint | All pipework are installed in the correct position and alignment in accordance with the approved drawing/plan
checkpoint-status |  |  | checkpoint | All pipework have been pressure tested and accepted in accordance to approved pressure testing procedure
checkpoint-status |  |  | checkpoint | Fire Brigade Booster is located within sight of the main entrance to the building
checkpoint-status |  |  | checkpoint | Concrete plinth provided for the booster location and hard stand for fire brigade pumping appliance
checkpoint-status |  |  | checkpoint | Feed Hydrant is located within 8 metres from fire brigade appliance hard stand
checkpoint-status |  |  | checkpoint | Fire water storage tank suction point (Storz) is located within 4 metres from fire brigade appliance hard stand
checkpoint-status |  |  | checkpoint | Fire water storage tank suction point (Storz) is located within 10 metres from fire brigade booster inlet connection
checkpoint-status |  |  | checkpoint | Centre distance between feed hydrant and booster inlet connection is 450 mm minimum and 5 m maximum
checkpoint-status |  |  | checkpoint | The height of Feed Hydrant Outlet and Booster Inlet Connection is minimum 750 mm and maximum 1200 mm from FFL
checkpoint-status |  |  | checkpoint | Valves face minimum 150-mm from door and valve handles are 100-mm from cabinet sides
checkpoint-status |  |  | checkpoint | The number of feed hydrant outlet installed is equal to number of fire brigade booster assembly inlets
checkpoint-status |  |  | checkpoint | The required number of fire brigade booster inlets installed is suitable for the system requirement or minimum of 2 inlets
checkpoint-status |  |  | checkpoint | Full flow non-return valve of correct size is installed in the proper location
checkpoint-status |  |  | checkpoint | Approved type of cabinet enclosure is installed as required
checkpoint-group |  |  | section | Completion
checkpoint-status |  |  | checkpoint | Sign Off below - pass once complete
holdpoint |  |  | signoff | Sign-Off - click to Add signature(s)
checklist-sectioned |  |  | checklist | LM-FOR-40-ITR-302.3 Hose Reel Installation |  |  |  |  | Yes | LM-FOR-40-ITR-302.3 Hose Reel Installation | 34164c1b-03f6-4185-827b-ed5378ae9bce
checkpoint-group |  |  | section | Installation
checkpoint-status |  |  | checkpoint | Hose Reel supply pipe works completely installed of correct size, position, elevation, alignment and adequately supported in accordance with approved drawing/plans
text | 511db77d-b2b5-5249-8f94-2df74e6d963b |  | textbox | Hose Reel No.
checkpoint-status |  |  | checkpoint | Hydrostatic pressure testing of installed pipe works completed and accepted
checkpoint-status |  |  | checkpoint | Hose Reel and associated valves, pipes and fitting used are in accordance with the approved specifications and applicable codes/standards
checkpoint-status |  |  | checkpoint | Hose Reel located along normal path of travel to nearest exit and readily accessible
checkpoint-status |  |  | checkpoint | Verify and confirm hose length to be 36-metres or 40-meters
checkpoint-status |  |  | checkpoint | Hose reel spindle is 1400 mm minimum to 2400 mm maximum above floor level. Stop valve is 1000 + 100 mm above floor level
checkpoint-status |  |  | checkpoint | Minimum radial clearance of 100 mm between the reel rim and cabinet/cavity to the sides, above and below
checkpoint-status |  |  | checkpoint | Minimum 100 mm clearance around the stop valve handwheel/handle
checkpoint-status |  |  | checkpoint | Any defects found on the hose reel assembly have been corrected
checkpoint-group |  |  | section | Completion
checkpoint-status |  |  | checkpoint | Sign Off below - pass once complete
holdpoint |  |  | signoff | Sign-Off - click to Add signature(s)
checklist-sectioned |  |  | checklist | LM-FOR-50-ITR-303.1 Fire Panel Installation |  |  |  |  | Yes | LM-FOR-50-ITR-303.1 Fire Panel Installation | 38a33e10-8d9a-4cd5-92c7-d1c19499c0d2
checkpoint-group |  |  | section | Fire Indicator Panel
checkpoint-status |  |  | checkpoint | Are visual indicators and controls not less than 750 mm from the floor
checkpoint-status |  |  | checkpoint | Are visual indicators and controls not more than 1850 mm from the floor
checkpoint-status |  |  | checkpoint | Connected to Brigade - Is the fire indicator panel clearly visible and readily accessible within the designated building entry point or the fire control room
checkpoint-status |  |  | checkpoint | Not Connected to Brigade - Is the fire indicator panel in a secure location and clearly visible and readily accessible to authorized personnel
checkpoint-group |  |  | section | Accessibility
checkpoint-status |  |  | checkpoint | Is the fire indicator panel obscured by a door (if No, continue to CLEARANCE)
checkpoint-status |  |  | checkpoint | Is the door marked in a contrasting colour to the general colour scheme with the words “FIRE PANEL” in letters not less than 50mm high
checkpoint-status |  |  | checkpoint | Is the door absent of locks
checkpoint-status |  |  | checkpoint | Where the door reduces the CIE sounder sound level below the CIE requirement, means are provided to give the required sound level outside the covering door
checkpoint-status |  |  | checkpoint | A minimum clearance is maintained from the enclosure as shown
checkpoint-group |  |  | section | Power sources
checkpoint-status |  |  | checkpoint | Is the battery enclosure located such that the batteries are readily accessible for inspection
checkpoint-status |  |  | checkpoint | Are the connecting leads to the battery clearly labelled to reduce the possibility of reverse connections to the battery
checkpoint-status |  |  | checkpoint | The battery is not be tapped for intermediate voltages
checkpoint-status |  |  | checkpoint | All connections are made using suitable connectors
checkpoint-group |  |  | section | Sub-Indicator Panels
checkpoint-status |  |  | checkpoint | The SIP shall only serve areas on one level of a building unless - Pass once below considered
button | e4010e88-c2e9-5fad-be1b-4f67cfa508c9 |  | button | (a) The SIP serves the entire building | Yes,No
button | 03258cea-bfcc-5e49-883d-44b59af25323 |  | button | (b) All zones connected to the SIP are readily accessible without leaving the area served by the SIP; or | Yes,No
button | 9e43733d-3b3c-5306-9f8c-feb5ebb2e6d0 |  | button | (c) The location of each zone in alarm at the SIP can be identified at the designated building entry point | Yes,No
button | 9843990c-3551-5ea8-9ccd-359768eb2cee |  | button | Where the SIP serves the entire building, it shall be installed in accordance with the requirements for an FIP | Yes,No
button | 466b5f32-a6c8-5aa0-8ecc-1d497f99f5e4 |  | button | If the SIP serves a specific area, is it located at the main point of entry into that area | Yes,No
checkpoint-group |  |  | section | Wiring
checkpoint-status |  |  | checkpoint | The extra low voltage wiring of the fire detection and alarm system is be kept separate and distinct from all other systems
checkpoint-status |  |  | checkpoint | The extra low voltage wiring of the fire detection and alarm system is installed in accordance with the requirements of AS/ACIF S009
checkpoint-status |  |  | checkpoint | Other wiring is installed in accordance with the electrical safety requirements of AS/NZS
checkpoint-status |  |  | checkpoint | Externally energized circuits at voltages in excess of extra low voltage, except the power source for CIE, do not enter any CIE enclosure
checkpoint-group |  |  | section | Completion
checkpoint-status |  |  | checkpoint | Sign Off below - pass once complete
holdpoint |  |  | signoff | Sign-Off - click to Add signature(s)
checklist-sectioned |  |  | checklist | LM-FOR-30-ITR-301.2 Alarm Control Valve |  |  |  |  | Yes | LM-FOR-30-ITR-301.2 Alarm Control Valve | 478fa878-2813-45b5-ba19-f83ed4057806
checkpoint-group |  |  | section | Installation
checkpoint-status |  |  | checkpoint | Supply and Installation pipe works are installed in the correct position and alignment in accordance with the approved drawing/plan
checkpoint-status |  |  | checkpoint | All supports are completely installed, spaced and bolted down
checkpoint-status |  |  | checkpoint | All roll grooved couplings / flanges are properly tightened
checkpoint-status |  |  | checkpoint | Correct size and specification of Alarm Valve is installed in accordance with the approved drawing/plan
checkpoint-status |  |  | checkpoint | Approved type of Monitored Main Stop Valve is fitted and operational
checkpoint-status |  |  | checkpoint | Correct size of alarm line is installed, adequately supported and alarm gong is properly piped to drain
checkpoint-status |  |  | checkpoint | Correct size of orifice is fitted and piped to drain when system is with retard chamber
checkpoint-status |  |  | checkpoint | Main waste & test valve is fitted and piped to drain
checkpoint-status |  |  | checkpoint | Correct type and model of Direct Brigade Alarm device is fitted
checkpoint-status |  |  | checkpoint | Correct model and range of Pressure Switch is fitted
checkpoint-status |  |  | checkpoint | Correct size and range of supply and installation pressure gauges with shut-off cocks are fitted
checkpoint-status |  |  | checkpoint | All signalling devices (Monitored Stop Valve, DBA, Low Pressure Switch), are wired back to FIP
checkpoint-status |  |  | checkpoint | Control Valve associated pipe works paint touch-up repair is completed
checkpoint-group |  |  | section | Completion
checkpoint-status |  |  | checkpoint | Sign Off below - pass once complete
holdpoint |  |  | signoff | Sign-Off - click to Add signature(s)
checklist-flat |  |  | checklist | Additional Tasks - add as required |  |  |  |  | Yes | Additional Tasks - add as required | 65c274c6-82bf-42ee-a49c-a20b3adacd02
checkpoint-status |  |  | checkpoint | Details of additional tasks - comment below
checklist-sectioned |  |  | checklist | LM-FOR-30-ITR-301.1 Sprinkler Control Valve |  |  |  |  | Yes | LM-FOR-30-ITR-301.1 Sprinkler Control Valve | 8e426a1f-26f9-4161-9046-e413466017b2
checkpoint-group |  |  | section | Installation
checkpoint-status |  |  | checkpoint | Supply and Installation pipe works are installed in the correct position and alignment in accordance with the approved drawing/plan
checkpoint-status |  |  | checkpoint | All supports are completely installed, spaced and bolted down box / assembly secured
checkpoint-status |  |  | checkpoint | All roll grooved couplings / flanges are properly tightened
checkpoint-status |  |  | checkpoint | Valve station drain is properly connected to risers drain and building hydraulic drainage
checkpoint-status |  |  | checkpoint | Approved type of Monitored Main Stop Valve is fitted and operational
checkpoint-status |  |  | checkpoint | All specific signage is installed lock shut / lock open including FSV number of M/V’s
checkpoint-status |  |  | checkpoint | Correct size and range of supply and installation pressure gauges with shut-off cocks are fitted
checkpoint-status |  |  | checkpoint | Correct type solenoid, flow switch, couplings etc installed
checkpoint-status |  |  | checkpoint | Correct size and range of supply and installation pressure gauges with shut-off cocks are fitted
checkpoint-status |  |  | checkpoint | Confirm GFA on solenoid activation/ flow switch/ MV activation
checkpoint-status |  |  | checkpoint | Control Valve is positioned between 1150mm to 1800mm
checkpoint-group |  |  | section | Completion
checkpoint-status |  |  | checkpoint | Sign Off below - pass once complete
holdpoint |  |  | signoff | Sign-Off - click to Add signature(s)
checklist-sectioned |  |  | checklist | LM-FOR-30-ITR-301 Sprinkler Installation/Fitoff |  |  |  |  | Yes | LM-FOR-30-ITR-301 Sprinkler Installation/Fitoff | 95ec5577-17e2-499d-9424-0b0e29580f0c
checkpoint-group |  |  | section | Sprinkler Rough-In
checkpoint-status |  |  | checkpoint | Supports spacing & fixing as per AS2118
checkpoint-status |  |  | checkpoint | Pipework installed as per drawings
checkpoint-status |  |  | checkpoint | Concealed space sprinklers installed
checkpoint-status |  |  | checkpoint | All ends blanked off/plugged for testing
checkpoint-status |  |  | checkpoint | Pipes left out
label | ad9438ba-2212-5d6a-ad70-7419cd3f140c |  | note | Fail=Missing, Pass=Complete
button | 6cca11af-854e-546a-bfe9-da47a2c281e9 |  | button | Pipes left out - installed | Yes,No
checkpoint-group |  |  | section | Sprinkler Fit-Off
checkpoint-status |  |  | checkpoint | Ceiling grid levelled
checkpoint-status |  |  | checkpoint | Sprinklers installed as per drawings
checkpoint-status |  |  | checkpoint | Sprinkler Type & temperature as per drawings
checkpoint-status |  |  | checkpoint | All escutcheon plates installed
checkpoint-status |  |  | checkpoint | Areas not fitted-off
label | cff97852-a9f5-577b-8db3-37d32c1e92a2 |  | note | Fail=Missing, Pass=Complete
button | c7c2d708-c7db-59c6-95a4-fceae40eb858 |  | button | Areas not fitted-off - completed | Yes,No
checkpoint-status |  |  | checkpoint | Client Sign Off Sheets Complete
checkpoint-status |  |  | checkpoint | Painting carried out
checkpoint-status |  |  | checkpoint | Pressure Tested (refer ITR 401) - Completed
checkpoint-group |  |  | section | Completion
checkpoint-status |  |  | checkpoint | Sign Off below - pass once complete
holdpoint |  |  | signoff | Sign-Off - click to Add signature(s)
checklist-sectioned |  |  | checklist | LM-FOR-50-ITR-303.4 Fire Detection Installation |  |  |  |  | Yes | LM-FOR-50-ITR-303.4 Fire Detection Installation | c89538b2-f461-445a-8dec-e6a0862aa9ec
checkpoint-group |  |  | section | Cabling
checkpoint-status |  |  | checkpoint | Have all cable supports been installed in the correct position with no obstructions
checkpoint-status |  |  | checkpoint | Have all cables been cable tied to soffit / catenary wire with no sagging or obstructions
checkpoint-status |  |  | checkpoint | Have all cables been installed for detectors
checkpoint-status |  |  | checkpoint | Have all cables been installed for sprinkler valve sets
checkpoint-status |  |  | checkpoint | Have all cables been installed for magnetic door holders
checkpoint-status |  |  | checkpoint | Have all cables been installed for security fire trips
checkpoint-status |  |  | checkpoint | Have all cables been installed for mechanical fire trips
checkpoint-status |  |  | checkpoint | Have all cables been installed for AS 1668 Fan Controls
checkpoint-status |  |  | checkpoint | Have the ELV and LV segregation rules been applied as per AS/CAS 009 (including 90 degrees crossovers)
checkpoint-status |  |  | checkpoint | Have all cables been installed in the correct position for devices
checkpoint-status |  |  | checkpoint | Have all cables been joined through for testing purposes
checkpoint-group |  |  | section | Cable Feeds
checkpoint-status |  |  | checkpoint | Have all cable supports been installed in the correct position with no obstructions
checkpoint-status |  |  | checkpoint | Have all cable feeds been installed in the correct position
checkpoint-status |  |  | checkpoint | Have all cables been tied to cable tray with steel ties with no sagging or obstructions
checkpoint-status |  |  | checkpoint | Have all cable trays been installed correctly and secured including joiners and bends
checkpoint-status |  |  | checkpoint | Have the modified cable trays been re-galvanized
checkpoint-group |  |  | section | Visual Check
checkpoint-status |  |  | checkpoint | Check that no other services are run with or attached to fire detection cables
checkpoint-status |  |  | checkpoint | Check that no cables have been damaged
checkpoint-status |  |  | checkpoint | Check that all final cable locations are correct and match up with the “For Construction Drawings” and “Reflected Ceiling Plans”
checkpoint-status |  |  | checkpoint | Have all cable runs, cable trays and penetrations been mark on “As Constructed Drawings” for handover
checkpoint-status |  |  | checkpoint | Have all stickers been installed to fire rated walls and smoke walls for penetrations
checkpoint-status |  |  | checkpoint | Has photographic evidence been taken and recorded for all penetrations?
checkpoint-group |  |  | section | Completion
checkpoint-status |  |  | checkpoint | Sign Off below - pass once complete
holdpoint |  |  | signoff | Sign-Off - click to Add signature(s)
checklist-sectioned |  |  | checklist | LM-FOR-40-ITR-302.1 Fire Pump Installation |  |  |  |  | Yes | LM-FOR-40-ITR-302.1 Fire Pump Installation | cec32d64-0a54-45c9-b416-3ceda74933b0
checkpoint-group |  |  | section | Installation
checkpoint-status |  |  | checkpoint | Pump installation arrangement including suction and discharge pipe works are in accordance with the approved drawing/plan
checkpoint-status |  |  | checkpoint | Pump clearance is 1000 mm on all four sides and 600 mm between pumps
checkpoint-status |  |  | checkpoint | Concrete plinth/foundation height is minimum 150 mm from FFL and 150 mm wider on all four sides of pump base
checkpoint-status |  |  | checkpoint | Pump base is sitting squarely and bolted down Vibration mounts are properly anchored on plinth or inertia plinth
checkpoint-status |  |  | checkpoint | Pump suction and discharge pipework are completely installed and connected Supports are adequately provided
checkpoint-status |  |  | checkpoint | Control panels installed and bolted down, MFB have clear access around pump controller 1000mm Arc
checkpoint-status |  |  | checkpoint | Suction isolation valve installed is OS & Y type
checkpoint-status |  |  | checkpoint | Non-return valve is installed and located upstream of the isolation valve in pump discharge line
checkpoint-status |  |  | checkpoint | Pump circulation-relief valve for electric driven pump is installed and piped to drain or tank return line
checkpoint-status |  |  | checkpoint | Heat exchanger cooling water harness for diesel driven pump is installed and piped to drain or tank return line
checkpoint-status |  |  | checkpoint | Pressure gauge with gauge cock is installed min 2Ø downstream of discharge flange or reducer
checkpoint-status |  |  | checkpoint | Pressure reductions installed on manifold x2 for each stage with M/V’s and Annubar for each stage
checkpoint-status |  |  | checkpoint | Exhaust connected to pump and installed to approved discharge location
checkpoint-status |  |  | checkpoint | Full tanks have been filled with Diesel; Electric Pumps AND Controls ready for energisation
checkpoint-group |  |  | section | Completion
checkpoint-status |  |  | checkpoint | Sign Off below - pass once complete
holdpoint |  |  | signoff | Sign-Off - click to Add signature(s)
checklist-flat |  |  | checklist | Document Attachment ITP (V.220421) |  |  |  |  | Yes | Document Attachment ITP (V.220421) | e69b2999-c406-4161-975e-cb1bd7ea3174
checkpoint-status |  |  | checkpoint | Documents/Drawings attached for reference - Pass once attached
checklist-sectioned |  |  | checklist | LM-FOR-40-ITR-302.2 Hydrant Installation |  |  |  |  | Yes | LM-FOR-40-ITR-302.2 Hydrant Installation | e82b240b-54f2-4a01-8b73-2dcbfb4644be
checkpoint-group |  |  | section | Installation
checkpoint-status |  |  | checkpoint | Hydrant supply pipe works completely installed of correct size, position, elevation, alignment and adequately supported in accordance with approved drawing/plan
text | dab84813-a3c5-52ec-8105-8d1f12a93eb4 |  | textbox | Hydrant No.
checkpoint-status |  |  | checkpoint | Hydrostatic pressure testing of installed supply pipe works completed and accepted
checkpoint-status |  |  | checkpoint | Hydrant valves and associated pipes and fittings used are in accordance with the approved specifications and applicable codes/standards
checkpoint-status |  |  | checkpoint | Fire Hydrant and associated fire water main isolation valves locations are in accordance with the approved drawing/plan
checkpoint-status |  |  | checkpoint | Hydrants stand pipe is adequately supported and bolted down. Concrete surround block provided for external hydrant
checkpoint-status |  |  | checkpoint | Hydrant valve is between 750 to 1200 mm from finish floor/grade level
checkpoint-status |  |  | checkpoint | Valve outlet is facing away from the wall and not more than 35O below its horizontal axis. Minimum 300 mm clearance around the valve outlet
checkpoint-status |  |  | checkpoint | Minimum 1000 mm clear space in front of valve outlet is provided
checkpoint-status |  |  | checkpoint | Valve handwheel clearance is minimum 100 mm clear of any obstruction at fully open
checkpoint-group |  |  | section | Completion
checkpoint-status |  |  | checkpoint | Sign Off below - pass once complete
holdpoint |  |  | signoff | Sign-Off - click to Add signature(s)
checklist-flat |  |  | checklist | Pre-start checklist (V.090322) |  |  |  |  | Yes | Pre-start checklist (V.090322) | ec31b851-c7a0-458b-9b42-4ed777aa9e5e
checkpoint-status |  |  | checkpoint | Latest consented drawings checked & referenced
text | aa0103bb-34f4-516f-a903-7dcf41ff1936 |  | textbox | Drawing & Revision #
checkpoint-status |  |  | checkpoint | Area clear, tidy and accessible
label | 198f9f9d-94a9-5f32-a9da-dce066dbd57e |  | note | Attach Photos/Comments below if any issues & send report to Builder
checklist-sectioned |  |  | checklist | LM-FOR-50-ITR- 303.5 Fire Detection Fit Off (V160421) |  |  |  |  | Yes | LM-FOR-50-ITR- 303.5 Fire Detection Fit Off (V160421) | ef13a269-c386-49f8-a794-5c0758b8f00a
checkpoint-group |  |  | section | Fit-Off
checkpoint-status |  |  | checkpoint | Have all devices been installed in the correct position with no obstructions
checkpoint-status |  |  | checkpoint | Have all detectors been installed in the correct position and addressed
checkpoint-status |  |  | checkpoint | Have all input/output modules been installed in the correct position and addressed, with all enclosures sealed
checkpoint-status |  |  | checkpoint | Have all magnetic door holders been installed correctly
checkpoint-status |  |  | checkpoint | Have all input/output devices been installed and addressed for security fire trips
checkpoint-status |  |  | checkpoint | Have all input/output devices been installed and addressed for mechanical fire trips
checkpoint-status |  |  | checkpoint | Have all input/output devices been installed and addressed for AS 1668 Fan Controls
checkpoint-status |  |  | checkpoint | Have the ELV and LV segregation rules been applied as per AS/CAS 009 (including 90 degrees crossovers) – Double check to make sure no other trades have been in after fire works
checkpoint-status |  |  | checkpoint | Have all cables and conduits been installed in the correct position for devices
checkpoint-status |  |  | checkpoint | Have all devices been terminated for testing purposes
checkpoint-group |  |  | section | Cable Feeds
checkpoint-status |  |  | checkpoint | Have all cable feeds been connected to the first device
checkpoint-status |  |  | checkpoint | Have all cable feeds been connected to the last device
checkpoint-status |  |  | checkpoint | Have cable feeds been connected at the panel
checkpoint-group |  |  | section | Visual Check
checkpoint-status |  |  | checkpoint | Check that no other services are run with or attached to fire detection cables
checkpoint-status |  |  | checkpoint | Check that no cables have been damaged
checkpoint-status |  |  | checkpoint | Check that all final cable locations are correct and match up with the “For Construction Drawings” and “Reflected Ceiling Plans”
checkpoint-status |  |  | checkpoint | Check that all address tags and labels are clear and readable
checkpoint-status |  |  | checkpoint | Have devices and address been noted on “As Constructed Drawings” for handover
checkpoint-status |  |  | checkpoint | Have all stickers been installed to fire rated walls and smoke walls for penetrations
checkpoint-status |  |  | checkpoint | Has photographic evidence been taken and recorded for all penetrations?
checkpoint-group |  |  | section | Completion
checkpoint-status |  |  | checkpoint | Sign Off below - pass once complete
holdpoint |  |  | signoff | Sign-Off - click to Add signature(s)
checklist-sectioned |  |  | checklist | LM-FOR-40-ITR-302.4 Tank Installation |  |  |  |  | Yes | LM-FOR-40-ITR-302.4 Tank Installation | f85d7c88-5e25-4b3a-b986-8bd9a3c3668e
checkpoint-group |  |  | section | Installation
checkpoint-status |  |  | checkpoint | Tank installation/construction is completed including associated pipe works in accordance with the approved drawing/plan
checkpoint-status |  |  | checkpoint | Tank is free from dents, buckling, cracks, and internal is clean and free of any debris and construction materials
checkpoint-status |  |  | checkpoint | Tank internal liner (if provided) is complete and properly bonded to tank wall/shell
checkpoint-status |  |  | checkpoint | Tank quick infill line including associated infill valve and isolation valve installed and adequately supported
checkpoint-status |  |  | checkpoint | Tank suction isolation valve is fitted in the correct position and operational in accordance with the approved drawing/plan
checkpoint-status |  |  | checkpoint | Tank suction vortex inhibitor is fitted in the correct position and elevation in accordance with the approved drawing/plan
checkpoint-status |  |  | checkpoint | Tank overflow is fitted in the correct position, elevation and properly piped to drain Adequate drain available
checkpoint-status |  |  | checkpoint | Tank drain/sludge isolation valve is fitted and blank off
checkpoint-status |  |  | checkpoint | Tank external water level indicator is fitted and operational
checkpoint-status |  |  | checkpoint | Tank internal and external access ladders are fitted & secured
checkpoint-status |  |  | checkpoint | Tank access hatch is fitted and provided with lockable cover
checkpoint-status |  |  | checkpoint | Ball float for infill pilot line is fixed tightly, close to the manhole and away from the discharge path of tank infill
checkpoint-status |  |  | checkpoint | Tank is located with minimum of 600 mm clearance around tank perimeter and roof line
checkpoint-group |  |  | section | Completion
checkpoint-status |  |  | checkpoint | Sign Off below - pass once complete
holdpoint |  |  | signoff | Sign-Off - click to Add signature(s)