## Project Structure
Folder Structure |  |  |  | Checklists
Site QA
In Ground Pressure Services
|  | B2 |  | Ability to Add
|  | R3 |  | Ability to Add
In Ground Drainage Services
|  | B2 |  | Abiltiy to Add
In Ground Pits & Tanks
|  | B2 |  | Abiltiy to Add
Penetrations & Fire Collars
B2
|  | Retail | Abiltiy to Add
|  | Commercial | Abiltiy to Add
|  | Residential | Abiltiy to Add
B1
|  | Retail | Abiltiy to Add
|  | Commercial | Abiltiy to Add
|  | Residential | Abiltiy to Add
R2
|  | Retail | Abiltiy to Add
R3
|  | Retail | Abiltiy to Add
R3 Mez
|  | Retail | Abiltiy to Add
R4
|  | Retail | Abiltiy to Add
R5
|  | Retail | Abiltiy to Add
R6
|  | Retail | Abiltiy to Add
C7
|  | Commercial | Abiltiy to Add
C8
|  | Commercial | Abiltiy to Add
C9
|  | Commercial | Abiltiy to Add
C10
|  | Commercial | Abiltiy to Add
C11
|  | Commercial | Abiltiy to Add
C12
|  | Commercial | Abiltiy to Add
L13
|  | Commercial/Shared | Abiltiy to Add

## Checklists
type | name | values
checklist | ITP 1- In Ground Pressure Services - Polyethylene (Fusion Weld)
section | Survey & Set Out Works
checkpoint | Take dimensions off drawings and record any remarks / deviations
checkpoint | Review Dial Before You Dig information. Ensure not more than 30 days old.
checkpoint | Refer to dimensions on drawings & note any changes. Clearly mark trench line
checkpoint | Inform all personnel of existing services and mark with appropriate coloured paint
checkpoint | Please take a photo of plan title block. Ensure plan number & revision number visible
section | Excavation & Bedding Materials
checkpoint | Dig trenching to required depth as per AS3500 minimum cover requirements
checkpoint | Ensure minimal over excavation (minimum 75mm below pipe invert)
checkpoint | Lay & compact appropriate bedding material to required thickness, providing a consistent level surface
section | Install Pipework
checkpoint | Ensure that the pipe to be fused is the correct size for the electrofusion fitting being used
checkpoint | Ensure correct fitting is being used and leave in packaging until ready to install
checkpoint | Cut the pipe ends as evenly and squarely as possible using made for purpose tools
checkpoint | Clean pipe end with isopropyl alcohol to an area that is at least 2 times the full length of the coupling on each pipe end
checkpoint | Scrape pipe end to an area that is at least 2 times the full length of the coupling using made for purpose scraping tool
checkpoint | Ensure proper insertion depth of pipe end into electrofusion coupling
checkpoint | Use assembly clamping if required
checkpoint | Complete weld as per welder/ manufacturer steps
checkpoint | Ensure proper observation of cooling time
checkpoint | Use trace wire for plastic pipes
checkpoint | Lay pipework on bedding material ensuring no sagging in pipework. Multiple pipes keep 100mm Spacing, 300mm for non potable
section | Test Pipework
checkpoint | Photographic record to be kept of process. Take photos of gauges before and after
checkpoint | Pump test pipework to required kpa and time period as per AS3500 & AS5601.1
checkpoint | For water test pipework to 1500kpa for a period of not less than 30 mins. Ensure no air left in pipelines
checkpoint | For reduced pressure water systems test pipework to manufacturer's specification kpa & time period
checkpoint | For Gas Installations Test pipework to min 7Kpa or 1.5 times the working pressure whichever is greater for min 5min period
checkpoint | For Fire Service Installations Test pipework to min 1700Kpa for 30mins or specified time & pressure
section | Inspect Pipework
checkpoint | Complete all required inspections by third parties (client, authorities etc) Name/Sign
section | Backfill
checkpoint | Backfill pipework with appropriate material (sand/fine grained soil) not less than 75mm above the pipe soffit when compacted
checkpoint | Place layer warning tape that identifies the specific service 300mm above on compacted backfill directly above pipe
checkpoint | Complete backfill in layers with appropriate material to existing ground level ensuring compaction is achieved via mechanical aids
section | Photographic Record
checkpoint | Photographic record to be kept of process.Photos to include pipework belly filled and once overlay material installed
checkpoint | Works verified as conforming (McPherson Plumbing Representative): |  | Name:
signoff | Work verified by McPherson Plumbing
type | name | values
checklist | ITP 1- In Ground Pressure Services - Pressure PVC-U
section | Survey & Set Out Works
checkpoint | Take dimensions off drawings and record any remarks / deviations
checkpoint | Review Dial Before You Dig information. Ensure not more than 30 days old.
checkpoint | Refer to dimensions on drawings & note any changes. Clearly mark trench line
checkpoint | Inform all personnel of existing services and mark with appropriate coloured paint
checkpoint | Please take a photo of plan title block. Ensure plan number & revision number visible
section | Excavation & Bedding Materials
checkpoint | Dig trenching to required depth as per AS3500 minimum cover requirements
checkpoint | Ensure minimal over excavation (minimum 75mm below pipe invert)
checkpoint | Lay & compact appropriate bedding material to required thickness, providing a consistent level surface
section | Install Pipework
checkpoint | Accurately measure length of pipe & cut square. Deburr inside & outside of cut end
checkpoint | Ensure sockets are primed and clean and apply a sufficient amount of Type P solvent cement
checkpoint | Gently insert the pipe and fitting to full depth with a quarter turn & hold for 30 seconds
checkpoint | Do not disturb joint for at least 5 minutes
checkpoint | Wipe away any excess glue and inspect joint for soundness. Allow to cure for 24 hours before pressure testing
checkpoint | Use trace wire for plastic pipes.
checkpoint | Lay pipework on bedding material ensuring no sagging in pipework. Multiple pipes keep 100mm Spacing, 300mm for non potable
section | Test Pipework
checkpoint | Please take a photo of plan title block to be taken. Ensure plan number & revision number visible
checkpoint | Pump test pipework to required kpa and time period as per AS3500 & AS5601.1
checkpoint | For water test pipework to 1500kpa for a period of not less than 30 mins. Ensure no air left in pipelines
checkpoint | For reduced pressure water systems test pipework to manufacturer's specification kpa & time period
checkpoint | For Gas Installations Test pipework to min 7Kpa or 1.5 times the working pressure whichever is greater for min 5min period
checkpoint | For Fire Service Installations Test pipework to min 1700Kpa for 30mins or specified time & pressure
section | Inspect Pipework
checkpoint | Complete all required inspections by third parties (client, authorities etc) Name/Sign
section | Backfill
checkpoint | Backfill pipework with appropriate material (sand/fine grained soil) not less than 75mm above the pipe soffit when compacted
checkpoint | Place layer warning tape that identifies the specific service 300mm above on compacted backfill directly above pipe
checkpoint | Complete backfill in layers with appropriate material to existing ground level ensuring compaction is achieved via mechanical aids
section | Photographic Record
checkpoint | Photographic record to be kept of process.Photos to include pipework belly filled and once overlay material installed
checkpoint | Works verified as conforming (McPherson Plumbing Representative):
signoff | Work verified by McPherson Plumbing
checklist | ITP 2 - In Ground Drainage Services
section | Survey & Set Out Works
checkpoint | Take dimensions off drawings and record any remarks / deviations
checkpoint | Review Dial Before You Dig information. Ensure not more than 30 days old.
checkpoint | Refer to dimensions on drawings & note any changes. Clearly mark trench line
checkpoint | Inform all personnel of existing services and mark with appropriate coloured paint
checkpoint | Please take a photo of plan title block . Ensure plan number & revision number visible
section | Excavation & Bedding Materials
checkpoint | Dig trenching to required depth as per AS3500 minimum cover requirements
checkpoint | Ensure minimal over excavation (minimum 75mm below pipe invert)
checkpoint | Lay & compact appropriate bedding material to required thickness, providing a consistent level surface
section | Install Pipework
checkpoint | Lay pipework to appropriate invert and ensure correct alignment. Document inverts on As-Built
select | Type of pipe | DWV PVC-U, HDPE
checkpoint | Ensure pipe is scrapped with appropriate tool to expose bare pipe
checkpoint | Allow for all required inspection openings at change of direction and not more than 30m intervals
checkpoint | Install turn up points as per grid setout or surveyor markings
checkpoint | Ensure required depth of cover and proximity from other services is achieved
checkpoint | Belly Fill Pipework to keep in a stable position, but still visible for inspection
section | Test Pipework
checkpoint | Photographic record to be kept of process. Take photos of water level before and after
checkpoint | Hydrostatic test of pipework for a period of not less than 15 mins
section | Inspect Pipework
checkpoint | Complete all required inspections by third parties (client, authorities etc) Name/Sign
section | Backfill
checkpoint | Backfill pipework with appropriate material (sand/fine grained soil) not less than 75mm above the pipe soffit when compacted
checkpoint | Place layer warning tape that identifies the specific service 300mm above on compacted backfill directly above pipe
checkpoint | Complete backfill in layers with appropriate material to existing ground level ensuring compaction is achieved via mechanical aids
section | Photographic Record
checkpoint | Photographic record to be kept of process.Photos to include pipework belly filled and once overlay material installed
checkpoint | Works verified as conforming (McPherson Plumbing Representative): |  | Name:
signoff | Work verified by McPherson Plumbing
checklist | ITP 3 - In Ground Pits & Tanks
section | Survey & Set Out Works
checkpoint | Take dimensions off drawings and record any remarks / deviations
checkpoint | Review Dial Before You Dig information. Ensure not more than 30 days old.
checkpoint | Refer to dimensions on drawings & note any changes. Clearly mark pit location
checkpoint | Inform all personnel of existing services and mark with appropriate coloured paint
checkpoint | Please take a photo of plan title block. Ensure plan number & revision number visible
section | Excavation & Bedding Materials
checkpoint | Establish invert's & RL's and excavate to required depth
checkpoint | Ensure minimal over excavation and as per tank/pit specifications
checkpoint | Lay appropriate bedding material to required thickness, providing a consistent level surface
checkpoint | Check bedding level to ensure that it corresponds correctly with pit finish height
checkpoint | Ensure required depth of cover and proximity from other services is achieved
section | Installation of Pit & Risers
checkpoint | Lift in pit to appropriate level and ensure correct alignment as per plan. Document levels on As-Built
checkpoint | Ensure that the pit is level across the top
checkpoint | Seal pit and riser/ lid segments together using a site-approved non-shrink grout or mastic-type product
checkpoint | Leave the segments undisturbed until the period of curing is completed
section | Installation of Pit Connection Pipework
checkpoint | Establish pipe invert levels entering the pit and mark out on the thin knockout section of the pit wall.
checkpoint | For concrete pits break is to be made in the centre of the knockout carefully widening the penetration to suit the pipe size
checkpoint | For fiberglass pits/tanks use hole saw to suit pipe size
checkpoint | Pipe to be placed into the penetration and cut to the required engagement within the pit/tank
checkpoint | Seal outside of pit/tank wall around pipe connection with cement mix or approved sealant
section | Inspection
checkpoint | Complete all required inspections by third parties (client, authorities etc) Name/Sign
section | Backfilling
checkpoint | Backfill around pit sides with the same aggregate/ material that was used for the base of the pit/tank
checkpoint | Complete backfill with appropriate material to existing ground level, ensuring that suitable compaction is achieved
checkpoint | Photos to include backfill material around the pit/tank and the connection point
section | Pit Finishing
checkpoint | Seal inside of pit wall around pipe connection with cement mix or approved sealant to obtain a smooth surface consistent with pit
checkpoint | Installation of step irons or ladders if required
checkpoint | Provide protection of lid/grate gatic lift points or threads during construction period
checkpoint | Top the base of the pit to match the invert level of the pit outlet pipe where required. Record pit invert level on as-built
checkpoint | Photos to include pit finished & clean and free of debris/construction rubbish
section | Photographic Record
checkpoint | Photographic record to be kept of process.Photos to include entire installation process
checkpoint | Works verified as conforming (McPherson Plumbing Representative): |  | Name:
signoff | Work verified by McPherson Plumbing
checklist | ITP 4 - Set Out - Penetrations & Fire Collars
section | Survey & Set Out Works
checkpoint | Take dimensions off drawings and record any remarks / deviations prior to installing
select | Set Out | Survey Plotted, Manual Set Out
checkpoint | Photo of title block to include drawing number & revision
section | Structural Interface
checkpoint | Consult structural drawings to ensure no structural effect with penetration or cast in position
checkpoint | Ensure pipework within set downs and beams are cast in/out of set downs where required and indicated on penetration drawings
checkpoint | Check that penetration does not clash with elements downstairs e.g. Walls, Beams ETC
section | Fire Collar Installation
checkpoint | Ensure that fire collar is installed as per manufacturer's specifications and is spatially acceptable
section | Pipe Insertion to Collars
checkpoint | Ensure pipe is fitted correctly
checkpoint | Ensure pipe is fitted to maximise the efficiency of the next sequence of work e.g. Pipe is easy to knock through
section | Cast in Conduits
checkpoint | Ensure conduit is within wall or carcass range
checkpoint | Use 15/45 degree bends on all changes in direction
section | Cast in Balcony Outlets
checkpoint | Ensure pipe is supported correctly without affecting balcony soffit
checkpoint | Ensure pipes are not damaged after top steel and set downs are installed.
section | Safewaste or Puddle Flange Installation
checkpoint | Ensure safewaste or puddle flange is installed to all required outlets
checkpoint | Ensure safewaste or puddle flange is installed to the correct height
checkpoint | Spray all floor wastes to identify falls
section | All Pipes & Casting Capped & Supported
checkpoint | Ensure no open ends by installing dust cap or ductape on risers
section | Pipe Sleeves
checkpoint | Ensure all sleeves installed in in situ walls at the correct height
section | Castin Downpipes
checkpoint | Ensure pipes are clear of any obstructions prior to extending riser
checkpoint | Ensure pipe is fitted correctly where agreed by structural engineer
checkpoint | Ensure pipes are wrapped where required
checkpoint | Ensure downpipes capped and taped to riser
checkpoint | Ensure pipe is filled with water for concrete pour where required
section | Inspect Pipework
checkpoint | Complete all required inspections by third parties (client, authorities, builder, etc)
section | Photos
checkpoint | Ensure photos are taken of entire installation inc fire collars and casting prior to concrete pour
checkpoint | Works verified as conforming (McPherson Plumbing Representative) Name:

## Notes
B2
Retail
Commercial
Residential
B1
Retail
Commercial
Residential
R2
Retail
R3
Retail
R3 Mez
Retail
R4
Retail
R5
Retail
R6
Retail
C7
Commercial
C8
Commercial
C9
Commercial
C10
Commercial
C11
Commercial
C12
Commercial
L13
Commercial/Shared