## Resources
Rich Type | Id | Warnings | type | name | values | prefix | postfix | Usage Count | User Addable | Template Name | Template Id
checklist-sectioned |  |  | checklist | ITP 3 - In Ground Pits & Tanks |  |  |  |  | Yes | ITP 3 - In Ground Pits & Tanks | 2f76c893-1286-4e5e-b279-b3bf5c0b4dea
checkpoint-group |  |  | section | Survey & Set Out Works
checkpoint-status |  |  | checkpoint | Take dimensions off drawings and record any remarks / deviations
checkpoint-status |  |  | checkpoint | Review Dial Before You Dig information. Ensure not more than 30 days old.
checkpoint-status |  |  | checkpoint | Refer to dimensions on drawings & note any changes. Clearly mark pit location
checkpoint-status |  |  | checkpoint | Inform all personnel of existing services and mark with appropriate coloured paint
checkpoint-status |  |  | checkpoint | Please take a photo of plan title block. Ensure plan number & revision number visible
checkpoint-group |  |  | section | Excavation & Bedding Materials
checkpoint-status |  |  | checkpoint | Establish invert's & RL's and excavate to required depth
checkpoint-status |  |  | checkpoint | Ensure minimal over excavation and as per tank/pit specifications
checkpoint-status |  |  | checkpoint | Lay appropriate bedding material to required thickness, providing a consistent level surface
checkpoint-status |  |  | checkpoint | Check bedding level to ensure that it corresponds correctly with pit finish height
checkpoint-status |  |  | checkpoint | Ensure required depth of cover and proximity from other services is achieved
checkpoint-group |  |  | section | Installation of Pit & Risers
checkpoint-status |  |  | checkpoint | Lift in pit to appropriate level and ensure correct alignment as per plan. Document levels on As-Built
checkpoint-status |  |  | checkpoint | Ensure that the pit is level across the top
checkpoint-status |  |  | checkpoint | Seal pit and riser/ lid segments together using a site-approved non-shrink grout or mastic-type product
checkpoint-status |  |  | checkpoint | Leave the segments undisturbed until the period of curing is completed
checkpoint-group |  |  | section | Installation of Pit Connection Pipework
checkpoint-status |  |  | checkpoint | Establish pipe invert levels entering the pit and mark out on the thin knockout section of the pit wall.
checkpoint-status |  |  | checkpoint | For concrete pits break is to be made in the centre of the knockout carefully widening the penetration to suit the pipe size
checkpoint-status |  |  | checkpoint | For fiberglass pits/tanks use hole saw to suit pipe size
checkpoint-status |  |  | checkpoint | Pipe to be placed into the penetration and cut to the required engagement within the pit/tank
checkpoint-status |  |  | checkpoint | Seal outside of pit/tank wall around pipe connection with cement mix or approved sealant
checkpoint-group |  |  | section | Inspection
checkpoint-status |  |  | checkpoint | Complete all required inspections by third parties (client, authorities etc) Name/Sign
checkpoint-group |  |  | section | Backfilling
checkpoint-status |  |  | checkpoint | Backfill around pit sides with the same aggregate/ material that was used for the base of the pit/tank
checkpoint-status |  |  | checkpoint | Complete backfill with appropriate material to existing ground level, ensuring that suitable compaction is achieved
checkpoint-status |  |  | checkpoint | Photos to include backfill material around the pit/tank and the connection point
checkpoint-group |  |  | section | Pit Finishing
checkpoint-status |  |  | checkpoint | Seal inside of pit wall around pipe connection with cement mix or approved sealant to obtain a smooth surface consistent with pit
checkpoint-status |  |  | checkpoint | Installation of step irons or ladders if required
checkpoint-status |  |  | checkpoint | Provide protection of lid/grate gatic lift points or threads during construction period
checkpoint-status |  |  | checkpoint | Top the base of the pit to match the invert level of the pit outlet pipe where required. Record pit invert level on as-built
checkpoint-status |  |  | checkpoint | Photos to include pit finished & clean and free of debris/construction rubbish
checkpoint-group |  |  | section | Photographic Record
checkpoint-status |  |  | checkpoint | Photographic record to be kept of process.Photos to include entire installation process
checkpoint-status |  |  | checkpoint | Works verified as conforming (McPherson Plumbing Representative):
text | ba3510a9-2fa3-5686-ae36-b944229f4665 |  | textbox | Name:
holdpoint |  |  | signoff | Work verified by McPherson Plumbing
checklist-sectioned |  |  | checklist | ITP 2 - In Ground Drainage Services |  |  |  |  | Yes | ITP 2 - In Ground Drainage Services | 84602fb7-325f-4473-b97a-d2d86f1addb4
checkpoint-group |  |  | section | Survey & Set Out Works
checkpoint-status |  |  | checkpoint | Take dimensions off drawings and record any remarks / deviations
checkpoint-status |  |  | checkpoint | Review Dial Before You Dig information. Ensure not more than 30 days old.
checkpoint-status |  |  | checkpoint | Refer to dimensions on drawings & note any changes. Clearly mark trench line
checkpoint-status |  |  | checkpoint | Inform all personnel of existing services and mark with appropriate coloured paint
checkpoint-status |  |  | checkpoint | Please take a photo of plan title block . Ensure plan number & revision number visible
checkpoint-group |  |  | section | Excavation & Bedding Materials
checkpoint-status |  |  | checkpoint | Dig trenching to required depth as per AS3500 minimum cover requirements
checkpoint-status |  |  | checkpoint | Ensure minimal over excavation (minimum 75mm below pipe invert)
checkpoint-status |  |  | checkpoint | Lay & compact appropriate bedding material to required thickness, providing a consistent level surface
checkpoint-group |  |  | section | Install Pipework
checkpoint-status |  |  | checkpoint | Lay pipework to appropriate invert and ensure correct alignment. Document inverts on As-Built
select | 919cf17a-95ee-5acb-a26f-6eab80d40114 |  | dropdown | Type of pipe | DWV PVC-U, HDPE
checkpoint-status |  |  | checkpoint | Ensure pipe is scrapped with appropriate tool to expose bare pipe
checkpoint-status |  |  | checkpoint | Allow for all required inspection openings at change of direction and not more than 30m intervals
checkpoint-status |  |  | checkpoint | Install turn up points as per grid setout or surveyor markings
checkpoint-status |  |  | checkpoint | Ensure required depth of cover and proximity from other services is achieved
checkpoint-status |  |  | checkpoint | Belly Fill Pipework to keep in a stable position, but still visible for inspection
checkpoint-group |  |  | section | Test Pipework
checkpoint-status |  |  | checkpoint | Photographic record to be kept of process. Take photos of water level before and after
checkpoint-status |  |  | checkpoint | Hydrostatic test of pipework for a period of not less than 15 mins
checkpoint-group |  |  | section | Inspect Pipework
checkpoint-status |  |  | checkpoint | Complete all required inspections by third parties (client, authorities etc) Name/Sign
checkpoint-group |  |  | section | Backfill
checkpoint-status |  |  | checkpoint | Backfill pipework with appropriate material (sand/fine grained soil) not less than 75mm above the pipe soffit when compacted
checkpoint-status |  |  | checkpoint | Place layer warning tape that identifies the specific service 300mm above on compacted backfill directly above pipe
checkpoint-status |  |  | checkpoint | Complete backfill in layers with appropriate material to existing ground level ensuring compaction is achieved via mechanical aids
checkpoint-group |  |  | section | Photographic Record
checkpoint-status |  |  | checkpoint | Photographic record to be kept of process.Photos to include pipework belly filled and once overlay material installed
checkpoint-status |  |  | checkpoint | Works verified as conforming (McPherson Plumbing Representative):
text | ba2df53e-fc68-529f-a42e-ff33ad012642 |  | textbox | Name:
holdpoint |  |  | signoff | Work verified by McPherson Plumbing
checklist-sectioned |  |  | checklist | ITP 1- In Ground Pressure Services - Polyethylene (Fusion Weld) |  |  |  |  | Yes | ITP 1- In Ground Pressure Services - Polyethylene (Fusion Weld) | 8e90cd14-6b39-4930-a07c-9295671245f1
checkpoint-group |  |  | section | Survey & Set Out Works
checkpoint-status |  |  | checkpoint | Take dimensions off drawings and record any remarks / deviations
checkpoint-status |  |  | checkpoint | Review Dial Before You Dig information. Ensure not more than 30 days old.
checkpoint-status |  |  | checkpoint | Refer to dimensions on drawings & note any changes. Clearly mark trench line
checkpoint-status |  |  | checkpoint | Inform all personnel of existing services and mark with appropriate coloured paint
checkpoint-status |  |  | checkpoint | Please take a photo of plan title block. Ensure plan number & revision number visible
checkpoint-group |  |  | section | Excavation & Bedding Materials
checkpoint-status |  |  | checkpoint | Dig trenching to required depth as per AS3500 minimum cover requirements
checkpoint-status |  |  | checkpoint | Ensure minimal over excavation (minimum 75mm below pipe invert)
checkpoint-status |  |  | checkpoint | Lay & compact appropriate bedding material to required thickness, providing a consistent level surface
checkpoint-group |  |  | section | Install Pipework
checkpoint-status |  |  | checkpoint | Ensure that the pipe to be fused is the correct size for the electrofusion fitting being used
checkpoint-status |  |  | checkpoint | Ensure correct fitting is being used and leave in packaging until ready to install
checkpoint-status |  |  | checkpoint | Cut the pipe ends as evenly and squarely as possible using made for purpose tools
checkpoint-status |  |  | checkpoint | Clean pipe end with isopropyl alcohol to an area that is at least 2 times the full length of the coupling on each pipe end
checkpoint-status |  |  | checkpoint | Scrape pipe end to an area that is at least 2 times the full length of the coupling using made for purpose scraping tool
checkpoint-status |  |  | checkpoint | Ensure proper insertion depth of pipe end into electrofusion coupling
checkpoint-status |  |  | checkpoint | Use assembly clamping if required
checkpoint-status |  |  | checkpoint | Complete weld as per welder/ manufacturer steps
checkpoint-status |  |  | checkpoint | Ensure proper observation of cooling time
checkpoint-status |  |  | checkpoint | Use trace wire for plastic pipes
checkpoint-status |  |  | checkpoint | Lay pipework on bedding material ensuring no sagging in pipework. Multiple pipes keep 100mm Spacing, 300mm for non potable
checkpoint-group |  |  | section | Test Pipework
checkpoint-status |  |  | checkpoint | Photographic record to be kept of process. Take photos of gauges before and after
checkpoint-status |  |  | checkpoint | Pump test pipework to required kpa and time period as per AS3500 & AS5601.1
checkpoint-status |  |  | checkpoint | For water test pipework to 1500kpa for a period of not less than 30 mins. Ensure no air left in pipelines
checkpoint-status |  |  | checkpoint | For reduced pressure water systems test pipework to manufacturer's specification kpa & time period
checkpoint-status |  |  | checkpoint | For Gas Installations Test pipework to min 7Kpa or 1.5 times the working pressure whichever is greater for min 5min period
checkpoint-status |  |  | checkpoint | For Fire Service Installations Test pipework to min 1700Kpa for 30mins or specified time & pressure
checkpoint-group |  |  | section | Inspect Pipework
checkpoint-status |  |  | checkpoint | Complete all required inspections by third parties (client, authorities etc) Name/Sign
checkpoint-group |  |  | section | Backfill
checkpoint-status |  |  | checkpoint | Backfill pipework with appropriate material (sand/fine grained soil) not less than 75mm above the pipe soffit when compacted
checkpoint-status |  |  | checkpoint | Place layer warning tape that identifies the specific service 300mm above on compacted backfill directly above pipe
checkpoint-status |  |  | checkpoint | Complete backfill in layers with appropriate material to existing ground level ensuring compaction is achieved via mechanical aids
checkpoint-group |  |  | section | Photographic Record
checkpoint-status |  |  | checkpoint | Photographic record to be kept of process.Photos to include pipework belly filled and once overlay material installed
checkpoint-status |  |  | checkpoint | Works verified as conforming (McPherson Plumbing Representative):
text | 4e937f53-855d-5f61-8bd8-447144864e7c |  | textbox | Name:
holdpoint |  |  | signoff | Work verified by McPherson Plumbing
checklist-sectioned |  |  | checklist | ITP 1- In Ground Pressure Services - Pressure PVC-U |  |  |  |  | Yes | ITP 1- In Ground Pressure Services - Pressure PVC-U | aa808b6a-dc91-44ab-9c5d-5c176e335373
checkpoint-group |  |  | section | Survey & Set Out Works
checkpoint-status |  |  | checkpoint | Take dimensions off drawings and record any remarks / deviations
checkpoint-status |  |  | checkpoint | Review Dial Before You Dig information. Ensure not more than 30 days old.
checkpoint-status |  |  | checkpoint | Refer to dimensions on drawings & note any changes. Clearly mark trench line
checkpoint-status |  |  | checkpoint | Inform all personnel of existing services and mark with appropriate coloured paint
checkpoint-status |  |  | checkpoint | Please take a photo of plan title block. Ensure plan number & revision number visible
checkpoint-group |  |  | section | Excavation & Bedding Materials
checkpoint-status |  |  | checkpoint | Dig trenching to required depth as per AS3500 minimum cover requirements
checkpoint-status |  |  | checkpoint | Ensure minimal over excavation (minimum 75mm below pipe invert)
checkpoint-status |  |  | checkpoint | Lay & compact appropriate bedding material to required thickness, providing a consistent level surface
checkpoint-group |  |  | section | Install Pipework
checkpoint-status |  |  | checkpoint | Accurately measure length of pipe & cut square. Deburr inside & outside of cut end
checkpoint-status |  |  | checkpoint | Ensure sockets are primed and clean and apply a sufficient amount of Type P solvent cement
checkpoint-status |  |  | checkpoint | Gently insert the pipe and fitting to full depth with a quarter turn & hold for 30 seconds
checkpoint-status |  |  | checkpoint | Do not disturb joint for at least 5 minutes
checkpoint-status |  |  | checkpoint | Wipe away any excess glue and inspect joint for soundness. Allow to cure for 24 hours before pressure testing
checkpoint-status |  |  | checkpoint | Use trace wire for plastic pipes.
checkpoint-status |  |  | checkpoint | Lay pipework on bedding material ensuring no sagging in pipework. Multiple pipes keep 100mm Spacing, 300mm for non potable
checkpoint-group |  |  | section | Test Pipework
checkpoint-status |  |  | checkpoint | Please take a photo of plan title block to be taken. Ensure plan number & revision number visible
checkpoint-status |  |  | checkpoint | Pump test pipework to required kpa and time period as per AS3500 & AS5601.1
checkpoint-status |  |  | checkpoint | For water test pipework to 1500kpa for a period of not less than 30 mins. Ensure no air left in pipelines
checkpoint-status |  |  | checkpoint | For reduced pressure water systems test pipework to manufacturer's specification kpa & time period
checkpoint-status |  |  | checkpoint | For Gas Installations Test pipework to min 7Kpa or 1.5 times the working pressure whichever is greater for min 5min period
checkpoint-status |  |  | checkpoint | For Fire Service Installations Test pipework to min 1700Kpa for 30mins or specified time & pressure
checkpoint-group |  |  | section | Inspect Pipework
checkpoint-status |  |  | checkpoint | Complete all required inspections by third parties (client, authorities etc) Name/Sign
checkpoint-group |  |  | section | Backfill
checkpoint-status |  |  | checkpoint | Backfill pipework with appropriate material (sand/fine grained soil) not less than 75mm above the pipe soffit when compacted
checkpoint-status |  |  | checkpoint | Place layer warning tape that identifies the specific service 300mm above on compacted backfill directly above pipe
checkpoint-status |  |  | checkpoint | Complete backfill in layers with appropriate material to existing ground level ensuring compaction is achieved via mechanical aids
checkpoint-group |  |  | section | Photographic Record
checkpoint-status |  |  | checkpoint | Photographic record to be kept of process.Photos to include pipework belly filled and once overlay material installed
checkpoint-status |  |  | checkpoint | Works verified as conforming (McPherson Plumbing Representative):
holdpoint |  |  | signoff | Work verified by McPherson Plumbing
checklist-sectioned |  |  | checklist | ITP 4 - Set Out - Penetrations & Fire Collars |  |  |  |  | Yes | ITP 4 - Set Out - Penetrations & Fire Collars | bc95480f-96ae-464f-90c9-8d3bc262da6f
checkpoint-group |  |  | section | Survey & Set Out Works
checkpoint-status |  |  | checkpoint | Take dimensions off drawings and record any remarks / deviations prior to installing
select | 65a7e090-1e16-521e-96f5-e25ef296aa49 |  | dropdown | Set Out | Survey Plotted, Manual Set Out
checkpoint-status |  |  | checkpoint | Photo of title block to include drawing number & revision
checkpoint-group |  |  | section | Structural Interface
checkpoint-status |  |  | checkpoint | Consult structural drawings to ensure no structural effect with penetration or cast in position
checkpoint-status |  |  | checkpoint | Ensure pipework within set downs and beams are cast in/out of set downs where required and indicated on penetration drawings
checkpoint-status |  |  | checkpoint | Check that penetration does not clash with elements downstairs e.g. Walls, Beams ETC
checkpoint-group |  |  | section | Fire Collar Installation
checkpoint-status |  |  | checkpoint | Ensure that fire collar is installed as per manufacturer's specifications and is spatially acceptable
checkpoint-group |  |  | section | Pipe Insertion to Collars
checkpoint-status |  |  | checkpoint | Ensure pipe is fitted correctly
checkpoint-status |  |  | checkpoint | Ensure pipe is fitted to maximise the efficiency of the next sequence of work e.g. Pipe is easy to knock through
checkpoint-group |  |  | section | Cast in Conduits
checkpoint-status |  |  | checkpoint | Ensure conduit is within wall or carcass range
checkpoint-status |  |  | checkpoint | Use 15/45 degree bends on all changes in direction
checkpoint-group |  |  | section | Cast in Balcony Outlets
checkpoint-status |  |  | checkpoint | Ensure pipe is supported correctly without affecting balcony soffit
checkpoint-status |  |  | checkpoint | Ensure pipes are not damaged after top steel and set downs are installed.
checkpoint-group |  |  | section | Safewaste or Puddle Flange Installation
checkpoint-status |  |  | checkpoint | Ensure safewaste or puddle flange is installed to all required outlets
checkpoint-status |  |  | checkpoint | Ensure safewaste or puddle flange is installed to the correct height
checkpoint-status |  |  | checkpoint | Spray all floor wastes to identify falls
checkpoint-group |  |  | section | All Pipes & Casting Capped & Supported
checkpoint-status |  |  | checkpoint | Ensure no open ends by installing dust cap or ductape on risers
checkpoint-group |  |  | section | Pipe Sleeves
checkpoint-status |  |  | checkpoint | Ensure all sleeves installed in in situ walls at the correct height
checkpoint-group |  |  | section | Castin Downpipes
checkpoint-status |  |  | checkpoint | Ensure pipes are clear of any obstructions prior to extending riser
checkpoint-status |  |  | checkpoint | Ensure pipe is fitted correctly where agreed by structural engineer
checkpoint-status |  |  | checkpoint | Ensure pipes are wrapped where required
checkpoint-status |  |  | checkpoint | Ensure downpipes capped and taped to riser
checkpoint-status |  |  | checkpoint | Ensure pipe is filled with water for concrete pour where required
checkpoint-group |  |  | section | Inspect Pipework
checkpoint-status |  |  | checkpoint | Complete all required inspections by third parties (client, authorities, builder, etc)
checkpoint-group |  |  | section | Photos
checkpoint-status |  |  | checkpoint | Ensure photos are taken of entire installation inc fire collars and casting prior to concrete pour
checkpoint-status |  |  | checkpoint | Works verified as conforming (McPherson Plumbing Representative) Name: