## Resources
Rich Type | Id | Warnings | type | name | values | prefix | postfix | Usage Count | User Addable | Template Name | Template Id
checklist-sectioned | 4caedcea-d411-4b6e-9534-72b913616140 |  | checklist | ITP 1- In Ground Pressure Services - Polyethylene (Fusion Weld) |  |  |  |  | Yes | SYS - ITP 1- In Ground Pressure Services - Polyethylene (Fusion Weld) | 00a5c32d-1511-4080-81cf-b32218a66a75
checkpoint-group | a343a979-3f48-44e7-89a5-cb1bb3650807 |  | section | Survey & Set Out Works
checkpoint-status | 26147e8f-dfa9-4a5e-928a-b46d75c01880 |  | checkpoint | Take dimensions off drawings and record any remarks / deviations
checkpoint-status | 70854f3d-4115-46e2-b2a0-a77bfc5fc1b2 |  | checkpoint | Review Dial Before You Dig information. Ensure not more than 30 days old.
checkpoint-status | 60943d1d-6cba-4eb1-9993-517b66ac9d08 |  | checkpoint | Refer to dimensions on drawings & note any changes. Clearly mark trench line
checkpoint-status | 29ed4138-3a33-4f6c-a511-32a5436b3e2b |  | checkpoint | Inform all personnel of existing services and mark with appropriate coloured paint
checkpoint-status | f966cfed-872e-411d-9220-8a1028be38cc |  | checkpoint | Please take a photo of plan title block. Ensure plan number & revision number visible
checkpoint-group | 2c95c383-9642-4e83-a256-6c348d54ff5d |  | section | Excavation & Bedding Materials
checkpoint-status | e3878b7f-2862-439e-96c6-abe88c53ec58 |  | checkpoint | Dig trenching to required depth as per AS3500 minimum cover requirements
checkpoint-status | ec9616b4-911b-44a9-9ff7-265801a2f31f |  | checkpoint | Ensure minimal over excavation (minimum 75mm below pipe invert)
checkpoint-status | ddddeaef-7ce3-48dd-b7da-4ac97fb7be37 |  | checkpoint | Lay & compact appropriate bedding material to required thickness, providing a consistent level surface
checkpoint-group | d4e9f622-459e-4dff-8258-c2b54698d63a |  | section | Install Pipework
checkpoint-status | 0a324cfd-6fd7-42df-9023-97df8c206618 |  | checkpoint | Ensure that the pipe to be fused is the correct size for the electrofusion fitting being used
checkpoint-status | d531b84c-aee2-4891-94bd-1ce8bae11458 |  | checkpoint | Ensure correct fitting is being used and leave in packaging until ready to install
checkpoint-status | 0acfe6cb-210a-4d06-96c6-4fcb8da38724 |  | checkpoint | Cut the pipe ends as evenly and squarely as possible using made for purpose tools
checkpoint-status | 26f6a51e-1aff-4c1b-a98e-b4ff96c5bad6 |  | checkpoint | Clean pipe end with isopropyl alcohol to an area that is at least 2 times the full length of the coupling on each pipe end
checkpoint-status | a3fffd11-88ff-4e5a-bf9a-78c3c2a6be62 |  | checkpoint | Scrape pipe end to an area that is at least 2 times the full length of the coupling using made for purpose scraping tool
checkpoint-status | 3e1390f0-3745-4d40-996a-b2d4ae36f6ba |  | checkpoint | Ensure proper insertion depth of pipe end into electrofusion coupling
checkpoint-status | 56ca4fd9-f473-421d-8c2b-5853ccd0de82 |  | checkpoint | Use assembly clamping if required
checkpoint-status | aee85cfe-ab3d-4c09-81dc-b6395df3bb4b |  | checkpoint | Complete weld as per welder/ manufacturer steps
checkpoint-status | 7c45b0c8-03cd-456e-9ef7-747dacd52c44 |  | checkpoint | Ensure proper observation of cooling time
checkpoint-status | 46710ea9-c0da-43aa-924f-845b2d82c79a |  | checkpoint | Use trace wire for plastic pipes
checkpoint-status | a6a787ba-9bd4-481e-a31f-ad18902b642c |  | checkpoint | Lay pipework on bedding material ensuring no sagging in pipework. Multiple pipes keep 100mm Spacing, 300mm for non potable
checkpoint-group | 7ee37f55-9260-4eac-a3eb-279d35aa8a48 |  | section | Test Pipework
checkpoint-status | 79ab7936-e29e-443f-b6a0-8342d9a2c4c9 |  | checkpoint | Photographic record to be kept of process. Take photos of gauges before and after
checkpoint-status | ad6b4963-ab44-4d91-9428-5a8b386085b2 |  | checkpoint | Pump test pipework to required kpa and time period as per AS3500 & AS5601.1
checkpoint-status | 880ba05e-a165-4665-998d-465fe10daa44 |  | checkpoint | For water test pipework to 1500kpa for a period of not less than 30 mins. Ensure no air left in pipelines
checkpoint-status | cfb2cfe2-27bd-4d64-9da9-765bbf326a94 |  | checkpoint | For reduced pressure water systems test pipework to manufacturer's specification kpa & time period
checkpoint-status | 6a07ff8b-b309-4a46-9c4c-8ee26c3b4b4b |  | checkpoint | For Gas Installations Test pipework to min 7Kpa or 1.5 times the working pressure whichever is greater for min 5min period
checkpoint-status | 8811c59c-bb7f-414b-943e-84f79b98b460 |  | checkpoint | For Fire Service Installations Test pipework to min 1700Kpa for 30mins or specified time & pressure
checkpoint-group | e2b2b2d4-5b46-47b9-9957-37078d26a9c5 |  | section | Inspect Pipework
checkpoint-status | 1e4d7fce-409b-4c1e-8a96-c747821f8fdd |  | checkpoint | Complete all required inspections by third parties (client, authorities etc) Name/Sign
checkpoint-group | 2d627426-cdc3-4917-bfca-1021be77e0a4 |  | section | Backfill
checkpoint-status | c626f1d2-643f-4ec9-9b3a-e5b774c81d6d |  | checkpoint | Backfill pipework with appropriate material (sand/fine grained soil) not less than 75mm above the pipe soffit when compacted
checkpoint-status | 81f62b20-11e7-4386-9441-0dd4d30ffccd |  | checkpoint | Place layer warning tape that identifies the specific service 300mm above on compacted backfill directly above pipe
checkpoint-status | 7b18f090-5ebe-4914-9c00-0abc572c21c5 |  | checkpoint | Complete backfill in layers with appropriate material to existing ground level ensuring compaction is achieved via mechanical aids
checkpoint-group | b7bb0d95-f227-4874-bf95-cdb3dada0121 |  | section | Photographic Record
checkpoint-status | b399abb0-0271-4b6b-b5ff-f8f2c5b26a35 |  | checkpoint | Photographic record to be kept of process.Photos to include pipework belly filled and once overlay material installed
checkpoint-status | 5212e14c-dd18-406e-ab01-04effd8cca91 |  | checkpoint | Works verified as conforming (McPherson Plumbing Representative):
text | e8f8c331-20bf-5edb-a014-1cac5c9bc5d8 |  | textbox | Name:
holdpoint | 2cc357e8-fbbb-4964-aa62-2124a94ab564 |  | signoff | Work verified by McPherson Plumbing
checklist-sectioned | 3935cac1-582c-4662-836c-006a791be069 |  | checklist | ITP 1- In Ground Pressure Services - Pressure PVC-U |  |  |  |  | Yes | ITP 1- In Ground Pressure Services - Pressure PVC-U | 35706e92-8a44-4542-b428-a9e6bf5831c1
checkpoint-group | 13eefff4-24e9-43bd-9ee5-1ab437516a9d |  | section | Survey & Set Out Works
checkpoint-status | 07f95701-071a-4e3e-b783-2f525f4cfb33 |  | checkpoint | Take dimensions off drawings and record any remarks / deviations
checkpoint-status | 397fa292-fbd7-4726-8c79-a7e63e872f4f |  | checkpoint | Review Dial Before You Dig information. Ensure not more than 30 days old.
checkpoint-status | 70fd2a13-4d52-41cf-8af8-c42ae0b7972b |  | checkpoint | Refer to dimensions on drawings & note any changes. Clearly mark trench line
checkpoint-status | 69080448-9809-49ea-8e08-81da403ddb2d |  | checkpoint | Inform all personnel of existing services and mark with appropriate coloured paint
checkpoint-status | 86e6a76a-2dff-479f-a56d-6bd343eabb10 |  | checkpoint | Please take a photo of plan title block. Ensure plan number & revision number visible
checkpoint-group | eb942bde-f36e-4fb7-8e9b-5d8753cca281 |  | section | Excavation & Bedding Materials
checkpoint-status | bc44fcf0-a701-46a2-956b-e262909ab3de |  | checkpoint | Dig trenching to required depth as per AS3500 minimum cover requirements
checkpoint-status | 58b14d1f-47b3-4a3a-b7cf-f7b9a0607087 |  | checkpoint | Ensure minimal over excavation (minimum 75mm below pipe invert)
checkpoint-status | 957305c3-e675-4066-b526-c84584d105fe |  | checkpoint | Lay & compact appropriate bedding material to required thickness, providing a consistent level surface
checkpoint-group | bc048cf4-c96c-470b-bcfa-753cd84e2e62 |  | section | Install Pipework
checkpoint-status | caad80d6-c281-4449-9159-ddcf30a15953 |  | checkpoint | Accurately measure length of pipe & cut square. Deburr inside & outside of cut end
checkpoint-status | 36dbd34d-b342-492f-b524-12d6a7d1ccdd |  | checkpoint | Ensure sockets are primed and clean and apply a sufficient amount of Type P solvent cement
checkpoint-status | ef6b75b6-3fb2-4a9b-b9a1-9113d91087ea |  | checkpoint | Gently insert the pipe and fitting to full depth with a quarter turn & hold for 30 seconds
checkpoint-status | b5244bb6-6978-4482-987f-0a92a06dc703 |  | checkpoint | Do not disturb joint for at least 5 minutes
checkpoint-status | 2cebb7b3-d43f-4c4d-b941-639f7e31fd1b |  | checkpoint | Wipe away any excess glue and inspect joint for soundness. Allow to cure for 24 hours before pressure testing
checkpoint-status | f70291e7-f857-4d33-a3f3-2908ad63aa3a |  | checkpoint | Use trace wire for plastic pipes.
checkpoint-status | 59227be5-4c22-4de1-b47b-1c500589f592 |  | checkpoint | Lay pipework on bedding material ensuring no sagging in pipework. Multiple pipes keep 100mm Spacing, 300mm for non potable
checkpoint-group | 4a72b72c-d1c8-4b03-a48e-3a64af910eeb |  | section | Test Pipework
checkpoint-status | a21e1138-71b1-42fb-9406-9163ea52cf6a |  | checkpoint | Please take a photo of plan title block to be taken. Ensure plan number & revision number visible
checkpoint-status | 90bd26de-0153-4054-b0cc-78019625bee7 |  | checkpoint | Pump test pipework to required kpa and time period as per AS3500 & AS5601.1
checkpoint-status | e8973c86-a07b-4d3c-bfab-e2f8238cbd6a |  | checkpoint | For water test pipework to 1500kpa for a period of not less than 30 mins. Ensure no air left in pipelines
checkpoint-status | b75ef691-7402-4d5f-9f19-0f1f9abb80e7 |  | checkpoint | For reduced pressure water systems test pipework to manufacturer's specification kpa & time period
checkpoint-status | 884494b8-e991-43f4-a79f-69d0f42ef3f2 |  | checkpoint | For Gas Installations Test pipework to min 7Kpa or 1.5 times the working pressure whichever is greater for min 5min period
checkpoint-status | b85384f6-577b-4591-8b23-e50b8172cef9 |  | checkpoint | For Fire Service Installations Test pipework to min 1700Kpa for 30mins or specified time & pressure
checkpoint-group | bbe0d959-877a-490b-ba26-0d3f043a9b7e |  | section | Inspect Pipework
checkpoint-status | 463d2581-aba1-4744-89ce-89652fd89661 |  | checkpoint | Complete all required inspections by third parties (client, authorities etc) Name/Sign
checkpoint-group | 9c628404-288a-4579-b7ee-e69f2182f89e |  | section | Backfill
checkpoint-status | f54c36d7-a89e-46d4-acd1-c71a6effcb68 |  | checkpoint | Backfill pipework with appropriate material (sand/fine grained soil) not less than 75mm above the pipe soffit when compacted
checkpoint-status | 28297cd7-5928-4825-bec7-da4070562f63 |  | checkpoint | Place layer warning tape that identifies the specific service 300mm above on compacted backfill directly above pipe
checkpoint-status | c4e37fd1-7c57-499b-8826-e1ac6fe62d09 |  | checkpoint | Complete backfill in layers with appropriate material to existing ground level ensuring compaction is achieved via mechanical aids
checkpoint-group | b565f32e-ba3a-4b9e-a097-d8322b7afb53 |  | section | Photographic Record
checkpoint-status | a4d95c04-ffb5-44bd-8b0d-257ba959a998 |  | checkpoint | Photographic record to be kept of process.Photos to include pipework belly filled and once overlay material installed
checkpoint-status | 057c49c5-1756-4f64-b47a-d83afa4bfd8a |  | checkpoint | Works verified as conforming (McPherson Plumbing Representative):
holdpoint | 7539a159-9610-45aa-89c1-487c0466821b |  | signoff | Work verified by McPherson Plumbing
checklist-sectioned | 4f2712a3-9d6b-457a-ba9f-2c023a02953a |  | checklist | ITP 4 - Set Out - Penetrations & Fire Collars |  |  |  |  | Yes | ITP 4 - Set Out - Penetrations & Fire Collars | aec732c3-62d1-4b0f-9deb-59e663ae37d2
checkpoint-group | 6923512b-332f-4fff-bc85-ec6a7124255e |  | section | Survey & Set Out Works
checkpoint-status | 74de7769-a363-449e-90ba-2c291726820e |  | checkpoint | Take dimensions off drawings and record any remarks / deviations prior to installing
select | a32f10b3-b719-5c1e-8e1f-1acd978043d0 |  | dropdown | Set Out | Survey Plotted, Manual Set Out
checkpoint-status | 45ed0648-af0d-491a-8428-0f97e681842b |  | checkpoint | Photo of title block to include drawing number & revision
checkpoint-group | 501d4ae6-e87c-44e3-910b-b957a3596b14 |  | section | Structural Interface
checkpoint-status | 63805669-8f48-4476-81ec-f5c8efd1f8f4 |  | checkpoint | Consult structural drawings to ensure no structural effect with penetration or cast in position
checkpoint-status | 388c4a0c-ad3e-442a-b05f-db8579213c1c |  | checkpoint | Ensure pipework within set downs and beams are cast in/out of set downs where required and indicated on penetration drawings
checkpoint-status | 40ce841b-cc08-4b8d-a172-6ea0470977b2 |  | checkpoint | Check that penetration does not clash with elements downstairs e.g. Walls, Beams ETC
checkpoint-group | 9e3aac3e-196e-4310-8968-0e8e880d5601 |  | section | Fire Collar Installation
checkpoint-status | d94e65b8-eec4-48e2-9576-b2fe595a984d |  | checkpoint | Ensure that fire collar is installed as per manufacturer's specifications and is spatially acceptable
checkpoint-group | 6a360604-3df3-423a-ac91-5c0e6146441c |  | section | Pipe Insertion to Collars
checkpoint-status | ca228e1b-0b64-4f3c-a19b-350b0b75bea9 |  | checkpoint | Ensure pipe is fitted correctly
checkpoint-status | b2442262-c9a9-49a3-9039-da4e20a585e5 |  | checkpoint | Ensure pipe is fitted to maximise the efficiency of the next sequence of work e.g. Pipe is easy to knock through
checkpoint-group | 804e767b-f55d-4b83-923c-db1ad5e19821 |  | section | Cast in Conduits
checkpoint-status | 32f1fbce-3ba0-408f-8373-2c65361dda39 |  | checkpoint | Ensure conduit is within wall or carcass range
checkpoint-status | 37ba6cbd-6693-4e90-9376-09f963569aa9 |  | checkpoint | Use 15/45 degree bends on all changes in direction
checkpoint-group | 01d41636-ece2-40c7-8256-be543e5a5ac2 |  | section | Cast in Balcony Outlets
checkpoint-status | 40e93711-3bd6-4a0d-93de-bb7b7473f0af |  | checkpoint | Ensure pipe is supported correctly without affecting balcony soffit
checkpoint-status | 55ebf411-28f4-4e28-af7f-71e8347c4148 |  | checkpoint | Ensure pipes are not damaged after top steel and set downs are installed.
checkpoint-group | 75804774-a808-4a9d-a4e7-28e842e1595b |  | section | Safewaste or Puddle Flange Installation
checkpoint-status | 2806e961-4993-40c1-8db3-6e939553d31b |  | checkpoint | Ensure safewaste or puddle flange is installed to all required outlets
checkpoint-status | d45b5320-2501-42b6-86b4-4371a0879714 |  | checkpoint | Ensure safewaste or puddle flange is installed to the correct height
checkpoint-status | f4306e14-baa0-47fb-a1c2-fa78ff4dc89d |  | checkpoint | Spray all floor wastes to identify falls
checkpoint-group | f4272ceb-3f0d-4aa1-b1b3-654fa305a7b8 |  | section | All Pipes & Casting Capped & Supported
checkpoint-status | c153491e-987a-4995-b75f-bb6bdd9bb85a |  | checkpoint | Ensure no open ends by installing dust cap or ductape on risers
checkpoint-group | b9b2fa60-db70-4e9c-8099-d9fcb2e587a5 |  | section | Pipe Sleeves
checkpoint-status | 39ad947f-0eb5-4a2e-a87c-ea73ae8903c8 |  | checkpoint | Ensure all sleeves installed in in situ walls at the correct height
checkpoint-group | fe45f4b7-e131-43b7-8e08-6fa10f65c23a |  | section | Castin Downpipes
checkpoint-status | b84655cd-b3ba-4f76-9616-63cfa66aaa73 |  | checkpoint | Ensure pipes are clear of any obstructions prior to extending riser
checkpoint-status | 0ecdd856-6558-4e1e-bfa6-d1d15f5f58a4 |  | checkpoint | Ensure pipe is fitted correctly where agreed by structural engineer
checkpoint-status | 0141ecaf-52f7-45af-9935-7ac82d4fc856 |  | checkpoint | Ensure pipes are wrapped where required
checkpoint-status | 86b5a832-e95a-4ccf-9222-607703e5bc15 |  | checkpoint | Ensure downpipes capped and taped to riser
checkpoint-status | f0166b20-92cc-4a78-a615-bcd7a9828280 |  | checkpoint | Ensure pipe is filled with water for concrete pour where required
checkpoint-group | a8e428db-14e7-434f-81ff-8b3d062f5849 |  | section | Inspect Pipework
checkpoint-status | 3792f71a-5e80-473c-96b7-e27bf92c3534 |  | checkpoint | Complete all required inspections by third parties (client, authorities, builder, etc)
checkpoint-group | 90994b04-0d90-4173-b4b7-bf971f578a8e |  | section | Photos
checkpoint-status | 718f34fa-7c05-4cc4-9982-9a60bc1fb41f |  | checkpoint | Ensure photos are taken of entire installation inc fire collars and casting prior to concrete pour
checkpoint-status | 41c4b53c-9b5d-44e2-a90f-cbe5fc249928 |  | checkpoint | Works verified as conforming (McPherson Plumbing Representative) Name:
checklist-sectioned | 54283796-f511-4d2b-a082-3a5b4436c2db |  | checklist | ITP 2 - In Ground Drainage Services |  |  |  |  | Yes | ITP 2 - In Ground Drainage Services | cf8bce81-f1b7-410b-9c49-d412346b05ef
checkpoint-group | 81310cd5-2288-47cd-8b86-503a80de0c5e |  | section | Survey & Set Out Works
checkpoint-status | f60e42c8-af65-4c38-921b-1add7577da17 |  | checkpoint | Take dimensions off drawings and record any remarks / deviations
checkpoint-status | 802527a1-7c45-49c9-be4d-bcbbbb524315 |  | checkpoint | Review Dial Before You Dig information. Ensure not more than 30 days old.
checkpoint-status | c056d5d7-7511-48a2-9f5a-9e7084d5338b |  | checkpoint | Refer to dimensions on drawings & note any changes. Clearly mark trench line
checkpoint-status | f9d2466a-c162-4e38-aec6-04ab22dbf675 |  | checkpoint | Inform all personnel of existing services and mark with appropriate coloured paint
checkpoint-status | 5f49ce39-1fdb-4bd0-bf87-717b23844929 |  | checkpoint | Please take a photo of plan title block . Ensure plan number & revision number visible
checkpoint-group | 75f015a7-7c3b-4423-83db-67deda29fc12 |  | section | Excavation & Bedding Materials
checkpoint-status | c20c7bfb-3353-4b6c-8254-91b9eda41f8e |  | checkpoint | Dig trenching to required depth as per AS3500 minimum cover requirements
checkpoint-status | 1323f55e-6dc7-4e47-88da-5f0cfc39e388 |  | checkpoint | Ensure minimal over excavation (minimum 75mm below pipe invert)
checkpoint-status | 24bde96c-1aaf-4be8-a684-04c0bca9556c |  | checkpoint | Lay & compact appropriate bedding material to required thickness, providing a consistent level surface
checkpoint-group | ae5ed5d8-ac24-4473-a5a1-dec652926b26 |  | section | Install Pipework
checkpoint-status | 755eee8e-07a6-4ae5-b929-7f85dbf67213 |  | checkpoint | Lay pipework to appropriate invert and ensure correct alignment. Document inverts on As-Built
select | 63a72541-0557-5c94-aff1-7dae15d6e244 |  | dropdown | Type of pipe | DWV PVC-U, HDPE
checkpoint-status | 643a5da8-5d20-4f0b-a3a9-97455ccf1b2e |  | checkpoint | Ensure pipe is scrapped with appropriate tool to expose bare pipe
checkpoint-status | 466042d9-7688-4c0c-b943-dfe0bfb765d7 |  | checkpoint | Allow for all required inspection openings at change of direction and not more than 30m intervals
checkpoint-status | a54157ac-ac48-4dfb-84a4-603577092e7c |  | checkpoint | Install turn up points as per grid setout or surveyor markings
checkpoint-status | 75376586-3be4-4747-9992-d232b293a6d3 |  | checkpoint | Ensure required depth of cover and proximity from other services is achieved
checkpoint-status | a40223f4-769c-4835-96be-b4b64af5f2fd |  | checkpoint | Belly Fill Pipework to keep in a stable position, but still visible for inspection
checkpoint-group | 903f75e2-9d30-4edb-85e7-3cdd44513821 |  | section | Test Pipework
checkpoint-status | 1390ec56-7e50-4475-8c8f-cb056c00d1c4 |  | checkpoint | Photographic record to be kept of process. Take photos of water level before and after
checkpoint-status | d63072fe-d346-4269-9f93-717ac0659176 |  | checkpoint | Hydrostatic test of pipework for a period of not less than 15 mins
checkpoint-group | b07a0d71-ba88-4d57-a823-bda00fbbd001 |  | section | Inspect Pipework
checkpoint-status | 20dbcbdf-d15f-48e2-b96d-5c5459c4b8f9 |  | checkpoint | Complete all required inspections by third parties (client, authorities etc) Name/Sign
checkpoint-group | bec3360f-f29a-4096-a1a6-50c4dda8042d |  | section | Backfill
checkpoint-status | 5a1c3a4e-8611-458c-baa8-df1859daa703 |  | checkpoint | Backfill pipework with appropriate material (sand/fine grained soil) not less than 75mm above the pipe soffit when compacted
checkpoint-status | e8326d99-7bab-4086-a89f-09d75f28e790 |  | checkpoint | Place layer warning tape that identifies the specific service 300mm above on compacted backfill directly above pipe
checkpoint-status | ccdc2422-4077-4306-bfed-be5e9dd7838f |  | checkpoint | Complete backfill in layers with appropriate material to existing ground level ensuring compaction is achieved via mechanical aids
checkpoint-group | 5a16ec79-c34f-4d5d-b8b0-8c7542584cb8 |  | section | Photographic Record
checkpoint-status | 2895b762-3f1c-42be-ade8-e0f225464e19 |  | checkpoint | Photographic record to be kept of process.Photos to include pipework belly filled and once overlay material installed
checkpoint-status | dba7f7a9-7cd1-4c12-acbe-6231ff416bff |  | checkpoint | Works verified as conforming (McPherson Plumbing Representative):
text | 0bd81c24-6d17-505f-b772-99d4d220de21 |  | textbox | Name:
holdpoint | 6e3e8751-a04b-4317-aa2e-3235edee53ef |  | signoff | Work verified by McPherson Plumbing
checklist-sectioned | bb19533a-3644-44f9-a6d4-30bcf412eeff |  | checklist | ITP 3 - In Ground Pits & Tanks |  |  |  |  | Yes | ITP 3 - In Ground Pits & Tanks | d1c242b9-e347-4909-8cb9-ae9b3dc0ebc7
checkpoint-group | 28091590-a5e5-4fc4-bd07-b7355323294d |  | section | Survey & Set Out Works
checkpoint-status | 57987e81-7d81-4912-8a05-04d33a1f579f |  | checkpoint | Take dimensions off drawings and record any remarks / deviations
checkpoint-status | 74eccdc2-e09e-4eb4-834b-0d4fdbca83e7 |  | checkpoint | Review Dial Before You Dig information. Ensure not more than 30 days old.
checkpoint-status | 283f4956-3509-4b5c-9539-548fa583bc72 |  | checkpoint | Refer to dimensions on drawings & note any changes. Clearly mark pit location
checkpoint-status | 5dfaa30b-aa55-4895-aaa5-39eef8b8c3d9 |  | checkpoint | Inform all personnel of existing services and mark with appropriate coloured paint
checkpoint-status | 7c268b75-a6df-4f20-958e-2e8c08bc5c77 |  | checkpoint | Please take a photo of plan title block. Ensure plan number & revision number visible
checkpoint-group | 9da296bd-7114-4359-ae78-0e5a5414966a |  | section | Excavation & Bedding Materials
checkpoint-status | 0d2973be-1413-40a7-913a-775f9da4a995 |  | checkpoint | Establish invert's & RL's and excavate to required depth
checkpoint-status | 2f209b1a-2326-4f8e-812d-5a2c5083fd02 |  | checkpoint | Ensure minimal over excavation and as per tank/pit specifications
checkpoint-status | 34a28e30-a785-4609-9add-b3d3de28f2dc |  | checkpoint | Lay appropriate bedding material to required thickness, providing a consistent level surface
checkpoint-status | 2e5784a5-4eda-47af-aa2d-d9f5deae761b |  | checkpoint | Check bedding level to ensure that it corresponds correctly with pit finish height
checkpoint-status | b00c9454-1991-44e0-8b13-f5addbda1f00 |  | checkpoint | Ensure required depth of cover and proximity from other services is achieved
checkpoint-group | 6ba4a6fc-4728-4a87-a4e2-48745ffb43cb |  | section | Installation of Pit & Risers
checkpoint-status | e4f2bcd1-00a5-4629-ace5-657384532c99 |  | checkpoint | Lift in pit to appropriate level and ensure correct alignment as per plan. Document levels on As-Built
checkpoint-status | 6c78c708-bd8c-4999-b33e-f458522ba449 |  | checkpoint | Ensure that the pit is level across the top
checkpoint-status | d9219313-caf2-4a0d-adcc-1500cc34369c |  | checkpoint | Seal pit and riser/ lid segments together using a site-approved non-shrink grout or mastic-type product
checkpoint-status | 53a8b958-a085-48fc-8f7a-183ebdf9717d |  | checkpoint | Leave the segments undisturbed until the period of curing is completed
checkpoint-group | 8ea0c124-b57e-43e7-86c3-49ed132595ec |  | section | Installation of Pit Connection Pipework
checkpoint-status | ac9130d1-49f0-4272-83c1-0165249d4d1e |  | checkpoint | Establish pipe invert levels entering the pit and mark out on the thin knockout section of the pit wall.
checkpoint-status | d6881157-886e-4278-aac8-b48030897cb8 |  | checkpoint | For concrete pits break is to be made in the centre of the knockout carefully widening the penetration to suit the pipe size
checkpoint-status | 36fc2994-0082-4f04-b8ee-85a806cd7fee |  | checkpoint | For fiberglass pits/tanks use hole saw to suit pipe size
checkpoint-status | a0a11e24-f517-47cc-8a6e-56ebaab1981f |  | checkpoint | Pipe to be placed into the penetration and cut to the required engagement within the pit/tank
checkpoint-status | 67225577-964e-4893-a2bb-82e3f01f5bb4 |  | checkpoint | Seal outside of pit/tank wall around pipe connection with cement mix or approved sealant
checkpoint-group | 2fc81a0e-4d37-4418-9dc4-413bc607b863 |  | section | Inspection
checkpoint-status | c3a07a2d-2202-4361-b112-6ea0d3f98e22 |  | checkpoint | Complete all required inspections by third parties (client, authorities etc) Name/Sign
checkpoint-group | 3de59393-5975-47bc-aade-27654eedae92 |  | section | Backfilling
checkpoint-status | 151ac253-52aa-48cd-ae1c-88f35ba72025 |  | checkpoint | Backfill around pit sides with the same aggregate/ material that was used for the base of the pit/tank
checkpoint-status | c7d75d1c-432c-47e3-a51b-410bc7f068dd |  | checkpoint | Complete backfill with appropriate material to existing ground level, ensuring that suitable compaction is achieved
checkpoint-status | 95cbd58c-7a47-4f82-8290-934fb5a13cbc |  | checkpoint | Photos to include backfill material around the pit/tank and the connection point
checkpoint-group | 82a70726-7bf4-4aea-aea5-92285f8298fd |  | section | Pit Finishing
checkpoint-status | 63aba385-2ad9-435f-8961-068bab2eb7f0 |  | checkpoint | Seal inside of pit wall around pipe connection with cement mix or approved sealant to obtain a smooth surface consistent with pit
checkpoint-status | 5edb8178-01b3-46a4-b037-3dedc4bcbeca |  | checkpoint | Installation of step irons or ladders if required
checkpoint-status | fc2db073-ee5a-45ad-a063-1057c034dcef |  | checkpoint | Provide protection of lid/grate gatic lift points or threads during construction period
checkpoint-status | b8bb8b59-b755-44c3-af8d-f28bd49018e4 |  | checkpoint | Top the base of the pit to match the invert level of the pit outlet pipe where required. Record pit invert level on as-built
checkpoint-status | 6cdb8969-39bf-46d3-a5ed-016d723bb430 |  | checkpoint | Photos to include pit finished & clean and free of debris/construction rubbish
checkpoint-group | d8f6ea4a-44ac-4c53-9c12-aaef2dbc8b09 |  | section | Photographic Record
checkpoint-status | c0aa64fc-a825-4e28-bb6e-d0bb07b91f90 |  | checkpoint | Photographic record to be kept of process.Photos to include entire installation process
checkpoint-status | 65c65113-0337-4020-9a1f-772e2ce19ee6 |  | checkpoint | Works verified as conforming (McPherson Plumbing Representative):
text | 058314b7-0384-5e55-9f95-942228733021 |  | textbox | Name:
holdpoint | 9bcb3dcc-7dc9-45f8-ac50-b99a52f7f2fd |  | signoff | Work verified by McPherson Plumbing