## Sheet1
ConQA Team Notes: | [10 empty] | Comments/Queries:
Document Title: |  | ITP-Rail CAMMS-Conduit and Pits-Temporary
ITP Description: |  | CAMMS-Conduit and Pits-Temporary
Discipline (e.g. CIV/STR/RAIL: |  | Rail
Revision Number: |  | 0
Revision Date: |  | 2020-08-30
ITP created by: |  | Isaac El Zayat
ITP approved for use by: |  | Victor Mira
Special Notes to ConQA Team : |  | Camms Road
Inspection & Test Plan - Pit and Conduit - Rail (Supply and Install)
[9 empty] | Revision: | 0
[9 empty] | Date: | 2020-08-30
Legend: HP: Hold Point, HP* Internal Hold Point, WP: Witness Point, IP: Inspection Point, SP: Surveillance Point
Item | Task/Activity Description | Reference | Acceptance Criteria | Inspection / Test |  |  | Responsibility | Verifying Documents | Date Completed | Sign-off
|  |  |  | Method | Frequency | Category
1 | Referenced Documentation
1.1 | Non Dependent | IFC Drawings L1-CHE-STD-043 (VRIOGS 012.2.1) Australian Standards | N/A | N/A | N/A | N/A | N/A | N/A | NA | N/A
2 | Preliminaries-Materials
2.1 | Conduits | Comms Conduit: AS/ACIF S008:2006 LV Conduit: AS/ NZS 3000 - 2000. L1-CHE-STD-043 | Comms Conduits: 100Ø (114mm OD), PVC White comms conduit 4.6mm wall thickness LV & Signalling: 100Ø (114mm OD), orange electrical heavy duty 5.9mm wall thickness Inspect materials upon delivery and attached delivery dockets. | Document Review | Each Material Type, Each Delivery | IP | SE/PE | Attach Material Conformnace Certs, include TB Approval No. Attach delivery dockets
2.2 | Pits and Pit Lids | IFC Drawings L1-CHE-STD-043 | Pits: Concrete Pits to be made as per AS 3600 Pit Lids: Pit Covers shall comply with AS3996-2006 Pit lids in trafficable areas to be Class D, non-trafficable areas to be Class C. LV, Comms Cover: pit covers shall be labelled with the words “RAILWAYS SIGNALS & COMMUNICATIONS” (L1-CHE-STD-043 14.6) Inspect materials upon delivery and attached delivery dockets. | Document Review | Each Material Type, Each Delivery | IP | SE/PE | Attach Material Conformnace Certs, include TB Approval No. Attach delivery dockets Attach Precast Birth Cert
2.3 | Warning/Marker Tape | IFC Drawings L1-CHE-STD-043 6.4 | Warning/Marker Tape: Above LV: 150mm minimum wide orange coloured PVC ‘DANGER RAILWAY SIGNALLING CONDUITS’ Above Comms: 75mm minimum wide white coloured PVC ‘WARNING COMMUNICATIONS CABLES’ with an embedded stainless steel trace wire Inspect materials upon delivery and attached delivery dockets. | Document Review | Each Material Type, Each Delivery | IP | SE/PE | Attach Material Conformnace Certs, include TB Approval No. Attach delivery dockets
2.4 | Protection Barriers | IFC Drawings L1-CHE-STD-070 | Approved plastic protective orange strip (Vinidex or type approved equivalent) Inspect materials upon delivery and attached delivery dockets. | Document Review | Each Material Type, Each Delivery | IP | SE/PE | Attach Material Conformnace Certs, include TB Approval No. Attach delivery dockets
2.5 | Backfill Material | IFC Drawings L1-CHE-STD-043 Section 2 Table 1 | Material free of rocks that will not pass a 30mm sieve. The material shall be free or organic matter or anything that could dmanage the conduits. Inspect backfill material. Attached delivery dockets (if applicable). | Document Review | Each Material Type, Each Delivery | IP | SE/PE | Attach Material Conformnace Certs, include TB Approval No. Attach delivery dockets (if applicable)
2.6 | Bedding Sand | IFC Drawings L1-CHE-SPE-313 | Recycled Glass Sand shall be free of any perishable matter Bedding material and embedment material shall comply with the following grading requirements: 4.75mm passing 100% 2.36mm passing 75-100% 0.075mm passing 0-5% | Document Review | Each Material Type, Each Delivery | IP | SE/PE | Attach Material Conformnace Certs, include TB Approval No. Attach delivery dockets
2.7 | Draw String | IFC Drawings L1-CHE-STD-043 | 6 mm diameter polypropylene blue/yellow | Document Review | Each Material Type, Each Delivery | IP | SE/PE | Attach Material Conformnace Certs, include TB Approval No. Attach delivery dockets
2.8 | Markers and Marker Posts | L1-CHE-STD-043 13.2 AS 4799 | Markers and Marker Posts are to be manufactured in accordance with AS4799. | Document Review | Each Material Type, Each Delivery | IP | SE/PE | Attach Material Conformnace Certs, include TB Approval No. Attach delivery dockets
3 | Preliminaries-Procedures
4 | Pre-construction
4.1 | Survey Set-out | IFC Drawings | Survey to set out trench alignment and pits, and establish construction control (alignment and level). | Measure Visual | Each element | IP | Surveyor SE/Site Supervisor | This ITP
5 | Construction
5.1 | Trench Excavation | IFC Drawings L1-CHE-STD-043 | Trench profile and depth as per IFC drawings. The width of the trench shall be not less than 200 mm (chain or bucket excavation) or 300 mm (backhoe and other). The floor of the trench shall be level and free from all loose sharp objects; such as stones or rock of any type, or size, or rail ballast. | Measure, Visual | Each lot |  | SE/Site Supervisor | Sign ITP
5.2 | Trench Stability | L1-CHE-SPE-070 L1-CHE-STD-043 L1-CHE-STD-070 IFC Drawings MRPA standards | Trench stability check: - Shoring, - benching - geotech signoff | Visual, Document Review | Each lot | IP | SE/Site Supervisor | Sign ITP
5.3 | Conduit-Bedding Sand | IFC Drawings L1-CHE-STD-043 | 50mm bedding sand to be placed at base of trench in accordance with IFC drawings In areas where rock is encountered, the cables shall be laid on a clean bed of sand 100 mm thick | Measure, Visual | Each lot | IP | SE/Site Supervisor | Sign ITP
5.4 | Conduit-Configuration | IFC Drawings L1-CHE-STD-043 | Conduits are configured in accordance with IFC drawings and meet cable separation requirements. Min Cover - Natural Ground: 800mm - Under Road: 1200mm | Measure, Visual | Each lot | IP | SE/Site Supervisor | Sign ITP
5.5 | Conduit-Separation of Services | IFC Drawings TS-SP-013 L1-CHE-STD-043 | Separation of services - HV: Min. seperation distance between HV conduits at least 50mm - VicTrack: 100mm from HV - Utility: 300mm to utilities | Measure, Visual | Each lot | IP | SE/Site Supervisor | Sign ITP
5.6 | Conduit-Joints | L1-CHE-SPE-070 L1-CHE-STD-043 L1-CHE-STD-070 IFC Drawings | All conduit joints shall be made by utilising the spigot and socket ends. Ends to be joined shall be thoroughly cleaned using a solvent approved by the conduit manufacturer. The joint shall be impervious to water and shall be glued with an adhesive approved by the conduit manufacturer. Socket ends to be placed firmly into the spigots then hit with a mallet to ensure a sound connection | Visual | Each Joint in each trench | IP | SE/Site Supervisor | Sign ITP
5.7 | Conduit-As Built Pick Up | IFC Drawings L1-CHE-STD-043 | GPS co-ordinates to an accuracy of ± 0.5 m shall be recorded every ten metres for the entire length of the cable route / trench, and at all changes of direction. This method shall also be utilised to capture all; i. Cable joint locations. ii. Cable pit locations. iii. Under line crossings iv. Under road crossings v. Other significant points of the cable route | Measure | Every 10m | WP | SE/Site Supervisor | Sign ITP
5.8 | Conduit-Bedding Sand Installation | IFC Drawings L1-CHE-STD-043 | Bedding sand extends 50mm past edge of conduits. Bedding sand extends 100mm above conduits. | Visual | Each lot | IP | SE/Site Supervisor | Sign ITP Attach Delivery Dockets
5.9 | Conduit-Protective Cover | IFC Drawings L1-CHE-STD-043 | The cover strip shall be placed on top of the cables and overlap the cables by not less than 50 mm on each side The protective cover shall be no closer than 75 mm above the cable/s | Visual | Each lot | IP | SE/Site Supervisor | Sign ITP
5.10 | Conduit-Marker Tape | IFC Drawings L1-CHE-STD-043 | 150mm wide orange coloured PVC "DANGER RAILWAY SIGNALLING CABLES" marker tape shall be installed in all trenches 300 mm below ground level | Visual | Each lot | IP | SE/Site Supervisor | Sign ITP
5.11 | Conduit-Backfill Installation | IFC Drawings L1-CHE-STD-043 clauses 6.15 and 6.16 | Backfill per trench profile - 150mm layers Backfill material to pass through 30mm sieve and be free of material that could damage conduit. The trench shall be finished with a slight mound, height equal to approximately 25% of trench width, to provide for further settlement. Trenches under road pavement - backfill to be same material as the road formation material. | Visual | Each lot | IP | SE/Site Supervisor/NA/VicTrack Rep | Sign ITP Attached Delivery Dockets
5.12 | Conduit-Compaction Testing | L1-CHE-STD-043 clauses 6.16 | Compaction to achieve 95% Standard Compaction. The tests shall be taken on a frequency of one (1) test per 200 linear metres per layer or one (1) test per area per layer where any area of excavation is less than 200 metres long. | Document Review, Visual | Each Layer & Every 200m OR Per Area | IP | SE/PE | Sign ITP Attached Test Report
5.13 | Pit-Bedding | IFC Drawings L1-CHE-STD-043 | All pits and chambers shall have a prepared foundation of “A” grade 20 mm crushed rock not less than 150 mm thick Gravel drainage sumps shall consist of 20 mm aggregate with a minimum depth of 300 mm | Viual | Each Pit | IP | SE/Site Supervisor | Sign ITP Attach Delivery Dockets
5.14 | Pit-Orientation | IFC Drawings | Pit to be parallel to track and parallel to conduit route. | Viual | Each Pit | IP | SE/Site Supervisor | Sign ITP
5.15 | Fit off-Conduit Entry | IFC Drawings L1-CHE-STD-043 | Entry holes shall be 100 mm minimum from the base of the pit or chamber. The end of conduits shall not protrude more than 50 mm into the pit space | Visual | Each Pit | IP | SE/Site Supervisor | Sign ITP
5.16 | Fit off-Spigots | IFC Drawings L1-CHE-STD-043 | Spigot bush to be installed on conduits being cabled | Visual | Each Pit | IP | SE/Site Supervisor | Sign ITP
5.17 | Fit off-Draw Ropes | IFC Drawings L1-CHE-STD-043 | The draw wire shall be continuous for the complete length of the conduit run. The draw wire shall have a minim of 2 metres of slack within each and every pit along the conduit run, and shall be suitably anchored at each end of the conduit run and then sealed with proprietary end caps | Visual | Each Pit | IP | SE/Site Supervisor | Sign ITP
5.18 | Fit off-Step Irons | IFC Drawings L1-CHE-STD-043 | Unless otherwise noted on IFC drawings, the below is required: All other Pits: Step irons/rungs to be installed if pit is greater than 1.2m in depth (including lid thickness) | Visual | Each Pit | IP | SE/Site Supervisor | Sign ITP
5.19 | Fit off-Spare Conduits | IFC Drawings L1-CHE-STD-043 | Spare conduits to be capped and to be included on survey report. | Visual | Each Pit | IP | SE/Site Supervisor | Sign ITP
5.20 | Fit off-Pit Lables | IFC Drawings L1-CHE-STD-043 | Pit labels Brass Label (30mm x 150mm) - Signalling: Railway Signals & Comms | Visual | Each Pit Lid | IP | SE/Site Supervisor | Sign ITP
5.21 | Protectipon and Labeling-Non Trafficable Pits | L1-CHE-SPE-070 L1-CHE-STD-043 L1-CHE-STD-070 IFC Drawings | Non trafficable pit lids to be 50mm above FSL and to have 2 x white bollardes installed at the corners of the pit. | Visual | Each Pit | IP | SE/Site Supervisor | Sign ITP
5.22 | Protectipon and Labeling-Cable Route Markers | IFC Drawings L1-CHE-STD-043 | Cable Route Markers - points entering & leaving the rail corridor - no greater than 100m spacing - Change of direction (more than 5 degrees) - White posts with marker plates for conduit runs | Visual | Per Cable Route | IP | SE/Site Supervisor | Sign ITP
6 | Post Construction
6.1 | As-built Survey file | L1-CHE-SPE-070 Section 13.1 | Survey report to include but not limited to: - Cable joint locations. - Cable pit locations (Corners) - Pit dimensions & pit lid type - Under line crossings - Under road crossings - Changes of direction - Spare Conduits - Conduits labelled as per trench profile - every 10m - Other significant points of the cable route | Document Review | Each Design Pack | IP | SE/PE | Sign ITP Attached Survey Report
6.2 | Engineering Redline mark-up | IFC Drawings | As constructed cable plans shall be provided for the entire cable installation and in accordance with AS 4799 and the PTV Infrastructure Drafting Standard. | Document Review | Each Design Pack | IP | SE/PE | Sign ITP Attached RLMU
Final Inspection
On behalf of Metropolitan Roads Program Alliance, it is hereby certified that the Works represented by the item of work listed have been tested in accordance with the Project Quality Plan and conform in all respects with the requirements of the Contract.
Print Name: Position: Signature: Date: / /