## res_ITP-CIV Delineation Fence R
type | name | values | prefix | postfix | usage count | user addable | template name
checklist | ITP-RAIL-CAMMS-MTM-Conduit and Pit-Temporary Rev 0 | itp |  |  |  |  | ITP-RAIL-CAMMS-MTM-Conduit and Pit-Temporary Rev 0
section | Referenced Documentation
checkpoint | Referenced Documentation
note | Document Title: ITP-RAIL-CAMMS-MTM-Conduit and Pit-Temporary
note | ITP Description: Conduit and Pits-Temporary
note | Document Number (in Teambinder): MRP-0000-MRPA-ALT-ITP-00XX
note | Discipline (e.g. CIV/STR/RAIL): RAIL
note | Revision Number: 0
note | Revision Date: 30/08/2020
note | ITP created by: Isaac El Zayat
note | ITP approved for use by: Victor Mira
note | 1.1 - Non Dependent
note | Reference Documents:
note | IFC Drawings
note | L1-CHE-STD-043 (VRIOGS 012.2.1)
note | Australian Standards
section | Preliminaries-Materials
checkpoint | 2.1 Conduits
note | REFERENCE:
note | Comms Conduit: AS/ACIF S008:2006
note | LV Conduit: AS/NZS 3000 - 2000.
note | L1-CHE-STD-043
note | ---------------------------------
note | ACCEPTANCE CRITERIA:
note | Comms Conduits: 100Ø (114mm OD), PVC White comms conduit 4.6mm wall thickness
note | LV & Signalling: 100Ø (114mm OD), orange electrical heavy duty 5.9mm wall thickness
note | Inspect materials upon delivery and attached delivery dockets.
note | ---------------------------------
note | METHOD: Document Review
note | ---------------------------------
note | FREQUENCY: Each Material Type, Each Delivery
note | ---------------------------------
note | CATEGORY: IP
note | ---------------------------------
note | RESPONSIBILITY: SE/PE
note | ---------------------------------
note | VERIFYING DOCUMENTS:
note | Attach Material Conformnace Certs, include TB Approval No.
note | Attach delivery dockets
textbox | Date Completed:
checkpoint | 2.2 Pits and Pit Lids
note | REFERENCE:
note | IFC Drawings
note | L1-CHE-STD-043
note | ---------------------------------
note | ACCEPTANCE CRITERIA:
note | • Pits: Concrete Pits to be made as per AS 3600
note | • Pit Lids: Pit Covers shall comply with AS3996-2006
note | Pit lids in trafficable areas to be Class D, non-trafficable areas to be Class C.
note | LV, Comms Cover: pit covers shall be labelled with the words “RAILWAYS SIGNALS & COMMUNICATIONS” (L1-CHE-STD-043 14.6)
note | Inspect materials upon delivery and attached delivery dockets.
note | ---------------------------------
note | METHOD: Document Review
note | ---------------------------------
note | FREQUENCY: Each Material Type, Each Delivery
note | ---------------------------------
note | CATEGORY: IP
note | ---------------------------------
note | RESPONSIBILITY: SE/PE
note | ---------------------------------
note | VERIFYING DOCUMENTS:
note | Attach Material Conformnace Certs, include TB Approval No.
note | Attach delivery dockets
note | Attach Precast Birth Cert
textbox | Date Completed:
checkpoint | 2.3 Warning/Marker Tape
note | REFERENCE:
note | IFC Drawings
note | L1-CHE-STD-043 6.4
note | ---------------------------------
note | ACCEPTANCE CRITERIA:
note | • Warning/Marker Tape:
note | • Above LV:
note | 150mm minimum wide orange coloured PVC
note | ‘DANGER RAILWAY SIGNALLING CONDUITS’
note | • Above Comms:
note | 75mm minimum wide white coloured PVC
note | ‘WARNING COMMUNICATIONS CABLES’ with an embedded stainless steel trace wire
note | Inspect materials upon delivery and attached delivery dockets.
note | ---------------------------------
note | METHOD: Document Review
note | ---------------------------------
note | FREQUENCY: Each Material Type, Each Delivery
note | ---------------------------------
note | CATEGORY: IP
note | ---------------------------------
note | RESPONSIBILITY: SE/PE
note | ---------------------------------
note | VERIFYING DOCUMENTS:
note | Attach Material Conformnace Certs, include TB Approval No.
note | Attach delivery dockets
textbox | Date Completed:
checkpoint | 2.4 Protection Barriers
note | REFERENCE:
note | IFC Drawings
note | L1-CHE-STD-070
note | ---------------------------------
note | ACCEPTANCE CRITERIA:
note | Approved plastic protective orange strip (Vinidex or type approved equivalent)
note | Inspect materials upon delivery and attached delivery dockets.
note | ---------------------------------
note | METHOD: Document Review
note | ---------------------------------
note | FREQUENCY: Each Material Type, Each Delivery
note | ---------------------------------
note | CATEGORY: IP
note | ---------------------------------
note | RESPONSIBILITY: SE/PE
note | ---------------------------------
note | VERIFYING DOCUMENTS:
note | Attach Material Conformnace Certs, include TB Approval No.
note | Attach delivery dockets
textbox | Date Completed:
checkpoint | 2.5 Backfill Material
note | REFERENCE:
note | IFC Drawings
note | L1-CHE-STD-043 Section 2 Table 1
note | ---------------------------------
note | ACCEPTANCE CRITERIA:
note | Material free of rocks that will not pass a 30mm sieve. The material shall be free or organic matter or anything that could dmanage the conduits.
note | Inspect backfill material.
note | Attached delivery dockets (if applicable).
note | ---------------------------------
note | METHOD: Document Review
note | ---------------------------------
note | FREQUENCY: Each Material Type, Each Delivery
note | ---------------------------------
note | CATEGORY: IP
note | ---------------------------------
note | RESPONSIBILITY: SE/PE
note | ---------------------------------
note | VERIFYING DOCUMENTS:
note | Attach Material Conformnace Certs, include TB Approval No.
note | Attach delivery dockets (if applicable)
textbox | Date Completed:
checkpoint | 2.6 Bedding Sand
note | REFERENCE:
note | IFC Drawings
note | L1-CHE-SPE-313
note | ---------------------------------
note | ACCEPTANCE CRITERIA:
note | • Recycled Glass Sand shall be free of any perishable matter
note | • Bedding material and embedment material shall comply with the following grading requirements:
note | 4.75mm passing 100%
note | 2.36mm passing 75-100%
note | 0.075mm passing 0-5%
note | ---------------------------------
note | METHOD: Document Review
note | ---------------------------------
note | FREQUENCY: Each Material Type, Each Delivery
note | ---------------------------------
note | CATEGORY: IP
note | ---------------------------------
note | RESPONSIBILITY: SE/PE
note | ---------------------------------
note | VERIFYING DOCUMENTS:
note | Attach Material Conformnace Certs, include TB Approval No.
note | Attach delivery dockets
textbox | Date Completed:
checkpoint | 2.7 Draw String
note | REFERENCE:
note | IFC Drawings
note | L1-CHE-STD-043
note | ---------------------------------
note | ACCEPTANCE CRITERIA: 6 mm diameter polypropylene blue/yellow
note | ---------------------------------
note | METHOD: Document Review
note | ---------------------------------
note | FREQUENCY: Each Material Type, Each Delivery
note | ---------------------------------
note | CATEGORY: IP
note | ---------------------------------
note | RESPONSIBILITY: SE/PE
note | ---------------------------------
note | VERIFYING DOCUMENTS:
note | Attach Material Conformnace Certs, include TB Approval No.
note | Attach delivery dockets
textbox | Date Completed:
checkpoint | 2.8 Markers and Marker Posts
note | REFERENCE:
note | L1-CHE-STD-043 13.2
note | AS 4799
note | ---------------------------------
note | ACCEPTANCE CRITERIA: Markers and Marker Posts are to be manufactured in accordance with AS4799.
note | ---------------------------------
note | METHOD: Document Review
note | ---------------------------------
note | FREQUENCY: Each Material Type, Each Delivery
note | ---------------------------------
note | CATEGORY: IP
note | ---------------------------------
note | RESPONSIBILITY: SE/PE
note | ---------------------------------
note | VERIFYING DOCUMENTS:
note | Attach Material Conformnace Certs, include TB Approval No.
note | Attach delivery dockets
textbox | Date Completed:
section | Preliminaries-Procedures
section | Pre-construction
checkpoint | 4.1 Survey Set-out
note | REFERENCE: IFC Drawings
note | ---------------------------------
note | ACCEPTANCE CRITERIA: Survey to set out trench alignment and pits, and establish construction control (alignment and level).
note | ---------------------------------
note | METHOD: Measure, Visual
note | ---------------------------------
note | FREQUENCY: Each element
note | ---------------------------------
note | CATEGORY: IP
note | ---------------------------------
note | RESPONSIBILITY: Surveyor, SE/Site Supervisor
note | ---------------------------------
note | VERIFYING DOCUMENTS: This ITP
textbox | Date Completed:
section | Construction
checkpoint | 5.1 Trench Excavation
note | REFERENCE:
note | IFC Drawings
note | L1-CHE-STD-043
note | ---------------------------------
note | ACCEPTANCE CRITERIA:
note | Trench profile and depth as per IFC drawings.
note | The width of the trench shall be not less than 200 mm (chain or bucket excavation) or 300 mm (backhoe and other).
note | The floor of the trench shall be level and free from all loose sharp objects; such as stones or rock of any type, or size, or rail ballast.
note | ---------------------------------
note | METHOD: Measure, Visual
note | ---------------------------------
note | FREQUENCY: Each lot
note | ---------------------------------
note | RESPONSIBILITY: SE/Site Supervisor
note | ---------------------------------
note | VERIFYING DOCUMENTS: Sign ITP
textbox | Date Completed:
checkpoint | 5.2 Trench Stability
note | REFERENCE:
note | L1-CHE-SPE-070
note | L1-CHE-STD-043
note | L1-CHE-STD-070
note | IFC Drawings
note | MRPA standards
note | ---------------------------------
note | ACCEPTANCE CRITERIA:
note | Trench stability check:
note | – Shoring,
note | – benching
note | – geotech signoff
note | ---------------------------------
note | METHOD: Visual, Document Review
note | ---------------------------------
note | FREQUENCY: Each lot
note | ---------------------------------
note | CATEGORY: IP
note | ---------------------------------
note | RESPONSIBILITY: SE/Site Supervisor
note | ---------------------------------
note | VERIFYING DOCUMENTS: Sign ITP
textbox | Date Completed:
checkpoint | 5.3 Conduit-Bedding Sand
note | REFERENCE:
note | IFC Drawings
note | L1-CHE-STD-043
note | ---------------------------------
note | ACCEPTANCE CRITERIA:
note | 50mm bedding sand to be placed at base of trench in accordance with IFC drawings
note | In areas where rock is encountered, the cables shall be laid on a clean bed of sand 100 mm thick
note | ---------------------------------
note | METHOD: Measure, Visual
note | ---------------------------------
note | FREQUENCY: Each lot
note | ---------------------------------
note | CATEGORY: IP
note | ---------------------------------
note | RESPONSIBILITY: SE/Site Supervisor
note | ---------------------------------
note | VERIFYING DOCUMENTS: Sign ITP
textbox | Date Completed:
checkpoint | 5.4 Conduit-Configuration
note | REFERENCE:
note | IFC Drawings
note | L1-CHE-STD-043
note | ---------------------------------
note | ACCEPTANCE CRITERIA:
note | Conduits are configured in accordance with IFC drawings and meet cable separation requirements.
note | Min Cover
note | – Natural Ground: 800mm
note | – Under Road: 1200mm
note | ---------------------------------
note | METHOD: Measure, Visual
note | ---------------------------------
note | FREQUENCY: Each lot
note | ---------------------------------
note | CATEGORY: IP
note | ---------------------------------
note | RESPONSIBILITY: SE/Site Supervisor
note | ---------------------------------
note | VERIFYING DOCUMENTS: Sign ITP
textbox | Date Completed:
checkpoint | 5.5 Conduit-Separation of Services
note | REFERENCE:
note | IFC Drawings
note | TS-SP-013
note | L1-CHE-STD-043
note | ---------------------------------
note | ACCEPTANCE CRITERIA:
note | Separation of services
note | – HV: Min. seperation distance between HV conduits at least 50mm
note | – VicTrack: 100mm from HV
note | – Utility: 300mm to utilities
note | ---------------------------------
note | METHOD: Measure, Visual
note | ---------------------------------
note | FREQUENCY: Each lot
note | ---------------------------------
note | CATEGORY: IP
note | ---------------------------------
note | RESPONSIBILITY: SE/Site Supervisor
note | ---------------------------------
note | VERIFYING DOCUMENTS: Sign ITP
textbox | Date Completed:
checkpoint | 5.6 Conduit-Joints
note | REFERENCE:
note | L1-CHE-SPE-070
note | L1-CHE-STD-043
note | L1-CHE-STD-070
note | IFC Drawings
note | ---------------------------------
note | ACCEPTANCE CRITERIA:
note | All conduit joints shall be made by utilising the spigot and socket ends.
note | Ends to be joined shall be thoroughly cleaned using a solvent approved by the conduit manufacturer.
note | The joint shall be impervious to water and shall be glued with an adhesive approved by the conduit manufacturer.
note | Socket ends to be placed firmly into the spigots then hit with a mallet to ensure a sound connection
note | ---------------------------------
note | METHOD: Visual
note | ---------------------------------
note | FREQUENCY: Each Joint in each trench
note | ---------------------------------
note | CATEGORY: IP
note | ---------------------------------
note | RESPONSIBILITY: SE/Site Supervisor
note | ---------------------------------
note | VERIFYING DOCUMENTS: Sign ITP
textbox | Date Completed:
checkpoint | 5.7 Conduit-As Built Pick Up
note | REFERENCE:
note | IFC Drawings
note | L1-CHE-STD-043
note | ---------------------------------
note | ACCEPTANCE CRITERIA:
note | GPS co-ordinates to an accuracy of ± 0.5 m shall be recorded every ten metres for the entire length of the cable route / trench, and at all changes of direction.
note | This method shall also be utilised to capture all;
note | i. Cable joint locations.
note | ii. Cable pit locations.
note | iii. Under line crossings
note | iv. Under road crossings
note | v. Other significant points of the cable route
note | ---------------------------------
note | METHOD: Measure
note | ---------------------------------
note | FREQUENCY: Every 10m
note | ---------------------------------
note | CATEGORY: WP
note | ---------------------------------
note | RESPONSIBILITY: SE/Site Supervisor
note | ---------------------------------
note | VERIFYING DOCUMENTS: Sign ITP
textbox | Date Completed:
checkpoint | 5.8 Conduit-Bedding Sand Installation
note | REFERENCE:
note | IFC Drawings
note | L1-CHE-STD-043
note | ---------------------------------
note | ACCEPTANCE CRITERIA:
note | Bedding sand extends 50mm past edge of conduits.
note | Bedding sand extends 100mm above conduits.
note | ---------------------------------
note | METHOD: Visual
note | ---------------------------------
note | FREQUENCY: Each lot
note | ---------------------------------
note | CATEGORY: IP
note | ---------------------------------
note | RESPONSIBILITY: SE/Site Supervisor
note | ---------------------------------
note | VERIFYING DOCUMENTS:
note | Sign ITP
note | Attach Delivery Dockets
textbox | Date Completed:
checkpoint | 5.9 Conduit-Protective Cover
note | REFERENCE:
note | IFC Drawings
note | L1-CHE-STD-043
note | ---------------------------------
note | ACCEPTANCE CRITERIA:
note | The cover strip shall be placed on top of the cables and overlap the cables by not less than 50 mm on each side
note | The protective cover shall be no closer than 75 mm above the cable/s
note | ---------------------------------
note | METHOD: Visual
note | ---------------------------------
note | FREQUENCY: Each lot
note | ---------------------------------
note | CATEGORY: IP
note | ---------------------------------
note | RESPONSIBILITY: SE/Site Supervisor
note | ---------------------------------
note | VERIFYING DOCUMENTS: Sign ITP
textbox | Date Completed:
checkpoint | 5.10 Conduit-Marker Tape
note | REFERENCE:
note | IFC Drawings
note | L1-CHE-STD-043
note | ---------------------------------
note | ACCEPTANCE CRITERIA: 150mm wide orange coloured PVC "DANGER RAILWAY SIGNALLING CABLES" marker tape shall be installed in all trenches 300 mm below ground level
note | ---------------------------------
note | METHOD: Visual
note | ---------------------------------
note | FREQUENCY: Each lot
note | ---------------------------------
note | CATEGORY: IP
note | ---------------------------------
note | RESPONSIBILITY: SE/Site Supervisor
note | ---------------------------------
note | VERIFYING DOCUMENTS: Sign ITP
textbox | Date Completed:
checkpoint | 5.11 Conduit-Backfill Installation
note | REFERENCE:
note | IFC Drawings
note | L1-CHE-STD-043 clauses 6.15 and 6.16
note | ---------------------------------
note | ACCEPTANCE CRITERIA:
note | Backfill per trench profile
note | – 150mm layers
note | Backfill material to pass through 30mm sieve and be free of material that could damage conduit.
note | The trench shall be finished with a slight mound, height equal to approximately 25% of trench width, to provide for further settlement.
note | Trenches under road pavement - backfill to be same material as the road formation material.
note | ---------------------------------
note | METHOD: Visual
note | ---------------------------------
note | FREQUENCY: Each lot
note | ---------------------------------
note | CATEGORY: IP
note | ---------------------------------
note | RESPONSIBILITY: SE/Site Supervisor/NA/VicTrack Rep
note | ---------------------------------
note | VERIFYING DOCUMENTS:
note | Sign ITP
note | Attached Delivery Dockets
textbox | Date Completed:
checkpoint | 5.12 Conduit-Compaction Testing
note | REFERENCE: L1-CHE-STD-043 clauses 6.16
note | ---------------------------------
note | ACCEPTANCE CRITERIA:
note | Compaction to achieve 95% Standard Compaction.
note | The tests shall be taken on a frequency of one (1) test per 200 linear metres per layer or one (1) test per area per layer where any area of excavation is less than 200 metres long.
note | ---------------------------------
note | METHOD: Document Review, Visual
note | ---------------------------------
note | FREQUENCY: Each Layer & Every 200m OR Per Area
note | ---------------------------------
note | CATEGORY: IP
note | ---------------------------------
note | RESPONSIBILITY: SE/PE
note | ---------------------------------
note | VERIFYING DOCUMENTS:
note | Sign ITP
note | Attached Test Report
textbox | Date Completed:
checkpoint | 5.13 Pit-Bedding
note | REFERENCE:
note | IFC Drawings
note | L1-CHE-STD-043
note | ---------------------------------
note | ACCEPTANCE CRITERIA:
note | All pits and chambers shall have a prepared foundation of “A” grade 20 mm crushed rock not less than 150 mm thick
note | Gravel drainage sumps shall consist of 20 mm aggregate with a minimum depth of 300 mm
note | ---------------------------------
note | METHOD: Visual
note | ---------------------------------
note | FREQUENCY: Each Pit
note | ---------------------------------
note | CATEGORY: IP
note | ---------------------------------
note | RESPONSIBILITY: SE/Site Supervisor
note | ---------------------------------
note | VERIFYING DOCUMENTS:
note | Sign ITP
note | Attach Delivery Dockets
textbox | Date Completed:
checkpoint | 5.14 Pit-Orientation
note | REFERENCE: IFC Drawings
note | ---------------------------------
note | ACCEPTANCE CRITERIA: Pit to be parallel to track and parallel to conduit route.
note | ---------------------------------
note | METHOD: Visual
note | ---------------------------------
note | FREQUENCY: Each Pit
note | ---------------------------------
note | CATEGORY: IP
note | ---------------------------------
note | RESPONSIBILITY: SE/Site Supervisor
note | ---------------------------------
note | VERIFYING DOCUMENTS: Sign ITP
textbox | Date Completed:
checkpoint | 5.15 Fit off-Conduit Entry
note | REFERENCE:
note | IFC Drawings
note | L1-CHE-STD-043
note | ---------------------------------
note | ACCEPTANCE CRITERIA:
note | Entry holes shall be 100 mm minimum from the base of the pit or chamber.
note | The end of conduits shall not protrude more than 50 mm into the pit space
note | ---------------------------------
note | METHOD: Visual
note | ---------------------------------
note | FREQUENCY: Each Pit
note | ---------------------------------
note | CATEGORY: IP
note | ---------------------------------
note | RESPONSIBILITY: SE/Site Supervisor
note | ---------------------------------
note | VERIFYING DOCUMENTS: Sign ITP
textbox | Date Completed:
checkpoint | 5.16 Fit off-Spigots
note | REFERENCE:
note | IFC Drawings
note | L1-CHE-STD-043
note | ---------------------------------
note | ACCEPTANCE CRITERIA: Spigot bush to be installed on conduits being cabled
note | ---------------------------------
note | METHOD: Visual
note | ---------------------------------
note | FREQUENCY: Each Pit
note | ---------------------------------
note | CATEGORY: IP
note | ---------------------------------
note | RESPONSIBILITY: SE/Site Supervisor
note | ---------------------------------
note | VERIFYING DOCUMENTS: Sign ITP
textbox | Date Completed:
checkpoint | 5.17 Fit off-Draw Ropes
note | REFERENCE:
note | IFC Drawings
note | L1-CHE-STD-043
note | ---------------------------------
note | ACCEPTANCE CRITERIA:
The draw wire shall be continuous for the complete length of the conduit run.
The draw wire shall have a minim of 2 metres of slack within each and every pit along the conduit run, and shall be suitably anchored at each end of the conduit run and then sealed with proprietary end caps
note | ---------------------------------
note | METHOD: Visual
note | ---------------------------------
note | FREQUENCY: Each Pit
note | ---------------------------------
note | CATEGORY: IP
note | ---------------------------------
note | RESPONSIBILITY: SE/Site Supervisor
note | ---------------------------------
note | VERIFYING DOCUMENTS: Sign ITP
textbox | Date Completed:
checkpoint | 5.18 Fit off-Step Irons
note | REFERENCE:
note | IFC Drawings
note | L1-CHE-STD-043
note | ---------------------------------
note | ACCEPTANCE CRITERIA:
note | Unless otherwise noted on IFC drawings, the below is required:
note | All other Pits: Step irons/rungs to be installed if pit is greater than 1.2m in depth (including lid thickness)
note | ---------------------------------
note | METHOD: Visual
note | ---------------------------------
note | FREQUENCY: Each Pit
note | ---------------------------------
note | CATEGORY: IP
note | ---------------------------------
note | RESPONSIBILITY: SE/Site Supervisor
note | ---------------------------------
note | VERIFYING DOCUMENTS: Sign ITP
textbox | Date Completed:
checkpoint | 5.19 Fit off-Spare Conduits
note | REFERENCE:
note | IFC Drawings
note | L1-CHE-STD-043
note | ---------------------------------
note | ACCEPTANCE CRITERIA: Spare conduits to be capped and to be included on survey report.
note | ---------------------------------
note | METHOD: Visual
note | ---------------------------------
note | FREQUENCY: Each Pit
note | ---------------------------------
note | CATEGORY: IP
note | ---------------------------------
note | RESPONSIBILITY: SE/Site Supervisor
note | ---------------------------------
note | VERIFYING DOCUMENTS: Sign ITP
textbox | Date Completed:
checkpoint | 5.20 Fit off-Pit Lables
note | REFERENCE:
note | IFC Drawings
note | L1-CHE-STD-043
note | ---------------------------------
note | ACCEPTANCE CRITERIA:
note | Pit labels Brass Label (30mm x 150mm)
note | – Signalling: Railway Signals & Comms
note | ---------------------------------
note | METHOD: Visual
note | ---------------------------------
note | FREQUENCY: Each Pit Lid
note | ---------------------------------
note | CATEGORY: IP
note | ---------------------------------
note | RESPONSIBILITY: SE/Site Supervisor
note | ---------------------------------
note | VERIFYING DOCUMENTS: Sign ITP
textbox | Date Completed:
checkpoint | 5.21 Protection and Labeling-Non Trafficable Pits
note | REFERENCE:
note | L1-CHE-SPE-070
note | L1-CHE-STD-043
note | L1-CHE-STD-070
note | IFC Drawings
note | ---------------------------------
note | ACCEPTANCE CRITERIA: Non trafficable pit lids to be 50mm above FSL and to have 2 x white bollardes installed at the corners of the pit.
note | ---------------------------------
note | METHOD: Visual
note | ---------------------------------
note | FREQUENCY: Each Pit
note | ---------------------------------
note | CATEGORY: IP
note | ---------------------------------
note | RESPONSIBILITY: SE/Site Supervisor
note | ---------------------------------
note | VERIFYING DOCUMENTS: Sign ITP
textbox | Date Completed:
checkpoint | 5.22 Protectipon and Labeling-Cable Route Markers
note | REFERENCE:
note | IFC Drawings
note | L1-CHE-STD-043
note | ---------------------------------
note | ACCEPTANCE CRITERIA:
note | Cable Route Markers
note | – points entering & leaving the rail corridor
note | – no greater than 100m spacing
note | – Change of direction (more than 5 degrees)
note | – White posts with marker plates for conduit runs
note | ---------------------------------
note | METHOD: Visual
note | ---------------------------------
note | FREQUENCY: Per Cable Route
note | ---------------------------------
note | CATEGORY: IP
note | ---------------------------------
note | RESPONSIBILITY: SE/Site Supervisor
note | ---------------------------------
note | VERIFYING DOCUMENTS: Sign ITP
textbox | Date Completed:
section | Post Construction
checkpoint | 6.1 As-built Survey file
note | REFERENCE: L1-CHE-SPE-070 Section 13.1
note | ---------------------------------
note | ACCEPTANCE CRITERIA:
note | Survey report to include but not limited to:
note | – Cable joint locations.
note | – Cable pit locations (Corners)
note | – Pit dimensions & pit lid type
note | – Under line crossings
note | – Under road crossings
note | – Changes of direction
note | – Spare Conduits
note | – Conduits labelled as per trench profile
note | – every 10m
note | – Other significant points of the cable route
note | ---------------------------------
note | METHOD: Document Review
note | ---------------------------------
note | FREQUENCY: Each Design Pack
note | ---------------------------------
note | CATEGORY: IP
note | ---------------------------------
note | RESPONSIBILITY: SE/PE
note | ---------------------------------
note | VERIFYING DOCUMENTS:
note | Sign ITP
note | Attached Survey Report
textbox | Date Completed:
checkpoint | 6.2 Engineering Redline mark-up
note | REFERENCE: IFC Drawings
note | ---------------------------------
note | ACCEPTANCE CRITERIA: As constructed cable plans shall be provided for the entire cable installation and in accordance with AS 4799 and the PTV Infrastructure Drafting Standard.
note | ---------------------------------
note | METHOD: Document Review
note | ---------------------------------
note | FREQUENCY: Each Design Pack
note | ---------------------------------
note | CATEGORY: IP
note | ---------------------------------
note | RESPONSIBILITY: SE/PE
note | ---------------------------------
note | VERIFYING DOCUMENTS:
note | Sign ITP
note | Attached RLMU
textbox | Date Completed:
checkpoint | Metropolitan Roads Program Alliance Final Inspection
note | On behalf of Metropolitan Roads Program Alliance, it is hereby certified that the Works represented by the item of work listed have been tested in accordance with the Project Quality Plan and conform in all respects with the requirements of the Contract.
textbox | Name:
textbox | Position:
textbox | Date Completed:
signoff | Sign ITP