## TO BUILD - Project Breakdown
Project Breakdown |  |  |  | Checklists
(PROJECT NAME: Morgans Finance - L25 367 Collins st
Site QA
4133-01 Ductwork Layout
Mech Rough in
|  |  | Ductwork | Ductwork Checklist
|  |  | Flex | Flex Checklist
|  |  | Cushion boxes | Cushion Boxes Checklist
|  |  | PAC-25.1 | Equipment Checklist
|  |  | PAC-25.2 | Equipment Checklist
|  |  | ERV-25.1 | Equipment Checklist
Mech Fit off
|  |  | Grilles | Grilles Fit-Off
|  |  | Drains | Drain Fit-Off Testing Checklist
PAC-25.1
|  |  | Filters | Filters Fit-Off Checklist
|  |  | Drains | Drains Checklist
PAC-25.2
|  |  | Filters | Filters Fit-Off Checklist
|  |  | Drains | Drains Checklist
|  | ERV-25.1 |  | Filters Fit-Off Checklist

## ChecklistsITCs
type | name | values | prefix | postfix
checklist | Ductwork Checklist
checkpoint | Ductwork delivered, protected & clean - i.e plastic wrapped
checkpoint | Marked off on latest drawing
button | Installed as per latest drawing | Yes, No
button | Correct height as per drawing | Yes, No
button | Duct flanges firmly bolted & sealed where required | Yes, No
button | Cleats installed as required | Yes, No
button | Insulated as required/ damage free | Yes, No
checkpoint | Supported to requirements
button | Correct hanger spacing | Yes, No
button | Correct rod length | Yes, No
checkpoint | Volume dampers installed as per drawing
checkpoint | Motorised dampers installed as per drawing
button | Dampers open & free moving | Yes, No
checkpoint | Acoustic penetration sealing to requirements
checkpoint | Damage free post-install & Area left clean/tidy (Any Issues comment below)
checklist | Equipment Checklist
checkpoint | Correct unit installed as per latest drawing & schedule
button | Correctly supported with anti vibration as required | Yes, No
checkpoint | Flexible connections installed as required
checkpoint | Access available & access panels marked on drawing
label | Marked up drawing attached below if applicable
button | Correctly labelled as per latest drawing | Yes, No
checkpoint | Installation completed to drawings/specification & Area left clean/tidy (Any Issues comment below)
checklist | Refrigeration Pipe Checklist
checkpoint | Correct IDU & ODU installed as per latest drawing & schedule
checkpoint | Installed as per latest drawings
checkpoint | No other services suspended from pipe work (Attach Photos below)
checkpoint | Installation damage free (Any Issues comment/attach Photos below)
button | correct hanger spacing | Yes, No
checkpoint | Pipe labelled after insulation
bool | Photo of Label attached
checkpoint | Pipe Mains Installation completed to drawings/specification & Area left clean/tidy (Any Issues comment below)
checkpoint | Pipework system pressure tested
checklist | Drains Checklist
checkpoint | Drains installed with fall to tundish
button | Pipes insulated as required | Yes, No
button | Tundish installed | Yes, No
checkpoint | Drain has been tested (Test results attached if applicable)
checkpoint | Drain(s) Installation completed to drawings/specification & Area left clean/tidy (Any Issues comment below)
checkpoint | Drain has had final test, traps are full
checklist | Flex Checklist
checkpoint | Supported with duct saddle only, not from other trades materials
button | Not sagging on ceiling | Yes, No
button | Dampers fully open | Yes, No
checkpoint | Correct as per latest drawing
checkpoint | Flex Installation completed to drawings/specification & Area left clean/tidy (Any Issues comment below)
checklist | Cushion Boxes Checklist
checkpoint | Correct size as per latest schedule
checkpoint | Secured & sealed
button | Flexible duct connected neat & secure | Yes, No
checkpoint | Cushion box damper installed & open
checkpoint | Diffuser cut out marked on ceiling (Attach Photos if applicable)
checkpoint | Cushion Box Installation completed to drawings/specification & Area left clean/tidy (Any Issues comment below)
checklist | As Builts Checklist
checkpoint | Update As-Built's of any know changes (Attach if applicable)
checklist | Access Panel Markup Checklist
checkpoint | Marked up completed & attached
button | Submitted to draftsman | Yes, No
checklist | Testing Checklist
checkpoint | Test passed with air/water
checkpoint | Test sighted by builder & signed off (Click to Add Signature below - If applicable)
button | Air bled from system | Yes, No
checklist | Fit-Off Checklist (Full)
section | Drain Fit-Off Testing
checkpoint | Drain has been terminated into tundish
checkpoint | Drain has had final test, traps are full
section | Grilles Fit-Off
checkpoint | Grilles, Registers, Diffusers fit off as per latest drawing/ schedule
button | Free of any damage | Yes, No
button | Grilles installed flush to ceiling | Yes, No
button | Boxes sealed to grill | Yes, No
button | Grille finish/colour as per latest spec | Yes, No
checkpoint | Grilles Fit-Off completed to drawings/specification & Area left clean/tidy (Any Issues comment below)
section | Filters Fit-Off
checkpoint | Plenums clean of dirt & debris
checkpoint | Filters installed correctly as per schedule (Any Issues Comment below)
checklist | Drain Fit-Off Testing Checklist
checkpoint | Drain has been terminated into tundish
checkpoint | Drain has had final test, traps are full
checklist | Grilles Fit-Off Checklist
checkpoint | Grilles, Registers, Diffusers fit off as per latest drawing/ schedule
button | Free of any damage | Yes, No
button | Grilles installed flush to ceiling | Yes, No
button | Boxes sealed to grill | Yes, No
button | Grille finish/colour as per latest spec | Yes, No
checkpoint | Grilles Fit-Off completed to drawings/specification & Area left clean/tidy (Any Issues comment below)
checklist | Filters Fit-Off Checklist
checkpoint | Plenums clean of dirt & debris
checkpoint | Filters installed correctly as per schedule (Any Issues Comment below)
checklist | Commissioning Checklist
checkpoint | Commissioning completed (Pass once below completed)
button | Any issues during commissioning | Yes, No
text | If Yes, please specify
bool | Any commissioning reports/results attached (If applicable)
checklist | Subbie Rough-in Progression Checklist
checkpoint | All work in Zone completed
label | Pass once all work complete
checkpoint | Any Progress Photos/File's attached for reference (Attach below)
checkpoint | Rough-In completed to specification/drawings & Area left clean/tidy
label | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
checklist | Subbie Fit-off Progression Checklist
checkpoint | All work in Zone completed
label | Pass once all work complete
checkpoint | Any Progress Photos/File's attached for reference (Attach below)
checkpoint | Fit-Off completed to specification/drawings & Area left clean/tidy
label | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
checklist | Subbie Testing Progression Checklist
checkpoint | All work in Zone completed
label | Pass once all work complete
checkpoint | Any Progress Photos/File's attached for reference (Attach below)
checkpoint | Testing completed to specification/drawings & Area left clean/tidy
label | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
checklist | Gripple Inspection Upload Checklist
checkpoint | Gripple Seismic inspection completed
label | Attach report as applicable below
button | Gripple inspector signature added below as applicable | Yes, No, N/A
holdpoint | If required - Click to request Gripple sign-off
checklist | Ductwork Checklist
checkpoint | Ductwork delivered, protected & clean - i.e plastic wrapped
checkpoint | Marked off on latest drawing
button | Installed as per latest drawing | Yes, No
button | Correct height as per drawing | Yes, No
button | Duct flanges firmly bolted & sealed where required | Yes, No
button | Cleats installed as required | Yes, No
button | Insulated as required/ damage free | Yes, No
checkpoint | Supported to requirements
button | Correct hanger spacing | Yes, No
button | Correct rod length | Yes, No
checkpoint | Volume dampers installed as per drawing
checkpoint | Smoke dampers installed as per drawing
button | Dampers open & free moving | Yes, No
checkpoint | Damage free post-install & Area left clean/tidy (Any Issues comment below)