## Resources
Rich Type | Id | Warnings | type | name | values | prefix | postfix | Usage Count | User Addable | Template Name | Template Id
checklist-flat |  |  | checklist | FRM-ITR-107 Battery Discharge Test |  |  |  |  | Yes | FRM-ITR-107 Battery Discharge Test | 19c53e49-8d09-46fc-b01f-4a9fa1932e10
checkpoint-status |  |  | checkpoint | Battery Discharge Testing
text | 7e3dc433-3064-5334-a17f-ae9e64b26357 |  | textbox | DB No.
text | ecbb5491-e694-55b1-809e-77678944eb42 |  | textbox | CB No.
text | a7a31db1-a31c-5a88-8e41-e4aa6346f20b |  | textbox | Light Number
text | e849dc43-eb83-5348-acb7-58fd740abe43 |  | textbox | 30 min
text | 1c2d17e1-8fd6-5ddc-afc3-aed0573e113a |  | textbox | 60 min
text | a4416b4d-d64c-5d4b-acf5-35926b04a0ed |  | textbox | 75 min
text | 02cb2174-ca19-5ce4-b29f-2b3346c76658 |  | textbox | 90 min
checklist-flat |  |  | checklist | FRM-ITR-102 Electrical Cable Ladder and Tray - Pre-Commissioning ITR |  |  |  |  | Yes | FRM-ITR-102 Electrical Cable Ladder and Tray - Pre-Commissioning ITR | 4cf8d11b-e08e-45b7-9844-495753aa9e4d
checkpoint-status |  |  | checkpoint | Verify Cable Ladder tagged correctly against drawings and project specifications
checkpoint-status |  |  | checkpoint | Verify general arrangement of installation meets latest drawings and specifications.
checkpoint-status |  |  | checkpoint | Verify there are no sharp edges in ladders and trays (both internally and externally)
checkpoint-status |  |  | checkpoint | Verify Cable Ladder is correctly aligned, levelled, rigid and secured with correct fixings.
checkpoint-status |  |  | checkpoint | Verify Cable Ladder adequately supported against latest drawings and specifications.
checkpoint-status |  |  | checkpoint | Verify earthing and bonding of Cable Ladder against latest drawings
checkpoint-status |  |  | checkpoint | Verify continuity test across joints has been completed and the results recorded. Ensure results are satisfactory as per design criteria. Highest Measured value
text | 3eb51705-9dad-5732-9b68-4df3c82ace85 |  | textbox | Ω
checkpoint-status |  |  | checkpoint | Verify cable segregation in accordance with latest drawings
checkpoint-status |  |  | checkpoint | Verify the capacity of cable tray/ ladder.
checkpoint-status |  |  | checkpoint | Verify that spare capacity is within specification
checkpoint-status |  |  | checkpoint | Verify insulation pads are adapted to stainless steel or aluminium cable tray /ladder.
checkpoint-status |  |  | checkpoint | Verify cable tray/ ladder cleanness.
checkpoint-status |  |  | checkpoint | Verify lid installation (if any) against drawings.
checkpoint-status |  |  | checkpoint | Verify all equipment is undamaged, installed in accordance with manufacturer’s instructions with enough clearance and accessibility for operation and maintenance.
checkpoint-status |  |  | checkpoint | Verify manufacturer/ project documentation and drawings. Ensure any discrepancies between design drawings and installation are clearly recorded as per project procedure.
checkpoint-status |  |  | checkpoint | Verify all equipotential Bonding. Record Results: Highest Measured Value
text | 1fd47ba4-8be8-5ac2-9870-367b2708ac06 |  | textbox | Ω
checkpoint-status |  |  | checkpoint | Ensure all Punch List items are recorded as per project procedure.
checkpoint-status |  |  | checkpoint | Sign Off
text | 78f30b3f-674c-5a37-932a-48c5a006dd65 |  | textbox | Full Name:
text | e87472aa-dc6a-5e0f-a721-5cfb3bb61f06 |  | textbox | Position / Title:
holdpoint |  |  | signoff | Add Signature / Request Sign Off
checklist-flat |  |  | checklist | FRM-ITR-106 ELV & Instrument Cabling Termination & Pre Commissioning |  |  |  |  | Yes | FRM-ITR-106 ELV & Instrument Cabling Termination & Pre Commissioning | 4fe9d9f6-41f6-47bd-91aa-fa3de0a6f664
checkpoint-status |  |  | checkpoint | Perform continuity check of earthing conductor:
text | df1c1bc8-1d95-5ae9-a04a-6fe178c8c97e |  | textbox | Ω
checkpoint-status |  |  | checkpoint | Perform insulation resistance test per core to earth as per AS/NZS 3000:2018 Section 8.3.3.2 (250Vdc) – Record Minimum Value
text | dd9492fa-e8ca-5c9c-a9c3-ea83a810965c |  | textbox | MΩ
checkpoint-status |  |  | checkpoint | Verify manufacturer I project documentation and drawings. Ensure any discrepancies between design drawings and installation are clearly recorded as per project procedure.
checkpoint-status |  |  | checkpoint | Ensure all Punch List items are recorded as per project procedure
checkpoint-status |  |  | checkpoint | Sign Off
text | 78f30b3f-674c-5a37-932a-48c5a006dd65 |  | textbox | Full Name:
text | e87472aa-dc6a-5e0f-a721-5cfb3bb61f06 |  | textbox | Position / Title:
holdpoint |  |  | signoff | Add Signature / Request Sign Off
checklist-flat |  |  | checklist | FRM-ITR-103 LV Cable ITR |  |  |  |  | Yes | FRM-ITR-103 LV Cable ITR | 5ddb9f3a-f4c1-4faa-8dd8-1015015d7da1
checkpoint-status |  |  | checkpoint | Verify equipment is de-energized and safe.
checkpoint-status |  |  | checkpoint | Verify cable type matches Cable Schedule.
checkpoint-status |  |  | checkpoint | Verify cable tagged correctly at both ends as per termination drawings and project requirements (including earthing arrangements and spare cores).
checkpoint-status |  |  | checkpoint | Verify cable is undamaged and installed in accordance with AS/NZS 3000:2018 Section 3.9.
checkpoint-status |  |  | checkpoint | Verify cable routing against drawings (segregation, distance, ties/fixing, etc.).
checkpoint-status |  |  | checkpoint | Verify cable support is as per project specifications.
checkpoint-status |  |  | checkpoint | Verify cable cores are correctly loomed and segregated (where required).
checkpoint-status |  |  | checkpoint | Verify cable and core marking against drawings.
checkpoint-status |  |  | checkpoint | Verify cable gland (or entry method) is suitable for cable type, meeting IP and support requirements.
checkpoint-status |  |  | checkpoint | Verify cable earthing against drawings.
checkpoint-status |  |  | checkpoint | Verify gland plate for single core current-carrying cables is nonferrous and retains suitable IP rating.
checkpoint-status |  |  | checkpoint | Verify bending radius is within the specified limits by standards and manufacturer's data sheets.
checkpoint-status |  |  | checkpoint | Sign Off
text | 78f30b3f-674c-5a37-932a-48c5a006dd65 |  | textbox | Full Name:
text | e87472aa-dc6a-5e0f-a721-5cfb3bb61f06 |  | textbox | Position / Title:
holdpoint |  |  | signoff | Add Signature / Request Sign Off
checklist-flat |  |  | checklist | FRM - ITR - 100 In-Ground Works |  |  |  |  | Yes | FRM - ITR - 100 In-Ground Works | 5e1ce297-a0ae-438a-a4c5-ad517e969af1
checkpoint-status |  |  | checkpoint | Survey and set out was correct at time of survey Surveyor to complete (& reference set out info)
checkpoint-status |  |  | checkpoint | Permit to dig
checkpoint-status |  |  | checkpoint | Alignment correct width / depth suitability of base
checkpoint-status |  |  | checkpoint | Ensure ITR 101 - Conduits has been completed
checkpoint-status |  |  | checkpoint | Conduit Installation, correct spacers used
checkpoint-status |  |  | checkpoint | Confirm adequate trench tape is installed
checkpoint-status |  |  | checkpoint | Ensure correct trench depth is as per specifications
checkpoint-status |  |  | checkpoint | Ensure conduit works has adequate bracing as per site specifications
checkpoint-status |  |  | checkpoint | Ensure adequate spare conduits are installed as per site specifications
checkpoint-status |  |  | checkpoint | Photograph, Trench Detail & Depth
checkpoint-status |  |  | checkpoint | GFIS detail for as build data base - Surveyor to complete
checkpoint-status |  |  | checkpoint | Suitability of proposed backfill
checkpoint-status |  |  | checkpoint | Confirm backfill is suitable - Check compaction & frequency requirements
checkpoint-status |  |  | checkpoint | Sign Off
text | 78f30b3f-674c-5a37-932a-48c5a006dd65 |  | textbox | Full Name:
text | e87472aa-dc6a-5e0f-a721-5cfb3bb61f06 |  | textbox | Position / Title:
holdpoint |  |  | signoff | Add Signature / Request Sign Off
checklist-flat |  |  | checklist | FRM-ITR-105 ELV & Instrumentation Cabling ITR |  |  |  |  | Yes | FRM-ITR-105 ELV & Instrumentation Cabling ITR | 6b790960-f486-41f3-b52f-6062b40d0e05
checkpoint-status |  |  | checkpoint | Verify equipment is de-energized and safe.
checkpoint-status |  |  | checkpoint | Verify cable type matches Cable Schedule.
checkpoint-status |  |  | checkpoint | Verify cable terminated and tagged correctly at both ends against IFC drawings (including earthing arrangements and spare cores).
checkpoint-status |  |  | checkpoint | Verify cable is undamaged.
checkpoint-status |  |  | checkpoint | Verify cable routing against drawings (segregation, distance, ties/fixing).
checkpoint-status |  |  | checkpoint | Verify cable support is as per project specifications.
checkpoint-status |  |  | checkpoint | Verify cable cores are correctly loomed and segregated.
checkpoint-status |  |  | checkpoint | Verify cable and core marking against drawings.
checkpoint-status |  |  | checkpoint | Verify all cable glands for correct type against cable type/schedule and project specification.
checkpoint-status |  |  | checkpoint | Verify bending radius is within the specified limits
checkpoint-status |  |  | checkpoint | Verify continuity of all cores, screen and armour.
checkpoint-status |  |  | checkpoint | Sign Off
text | 78f30b3f-674c-5a37-932a-48c5a006dd65 |  | textbox | Full Name:
text | e87472aa-dc6a-5e0f-a721-5cfb3bb61f06 |  | textbox | Position / Title:
holdpoint |  |  | signoff | Add Signature / Request Sign Off
checklist-flat |  |  | checklist | FRM - ITR - 101 Conduits |  |  |  |  | Yes | FRM - ITR - 101 Conduits | 7520efbd-79a6-41d5-b36a-a4fb0d08be31
checkpoint-status |  |  | checkpoint | Conduit Installation Size / Type / Quantity
checkpoint-status |  |  | checkpoint | Coordination Complete
checkpoint-status |  |  | checkpoint | Setout Checked and Deck / Trench marked
checkpoint-status |  |  | checkpoint | Conduit Installed
checkpoint-status |  |  | checkpoint | Conduit Accessories Installed
checkpoint-status |  |  | checkpoint | Conduit Glued
checkpoint-status |  |  | checkpoint | Draw Wire Installed
checkpoint-status |  |  | checkpoint | Inspected at concrete pour
checkpoint-status |  |  | checkpoint | Fixings and supports installed
checkpoint-status |  |  | checkpoint | Sign Off
text | 78f30b3f-674c-5a37-932a-48c5a006dd65 |  | textbox | Full Name:
text | e87472aa-dc6a-5e0f-a721-5cfb3bb61f06 |  | textbox | Position / Title:
holdpoint |  |  | signoff | Add Signature / Request Sign Off
checklist-flat |  |  | checklist | FRM-ITR 104 LV Cable Termination & Pre Commissioning |  |  |  |  | Yes | FRM-ITR 104 LV Cable Termination & Pre Commissioning | 7c80e611-db2a-4bb7-8ca5-343cc1a10719
checkpoint-status |  |  | checkpoint | Perform continuity check protective earthing conductor as per AS/NZS 3000:2018 Section 8.3.5:
text | 4f08430a-82ca-5923-8041-6bb2170cd677 |  | textbox | Record Results Ω
checkpoint-status |  |  | checkpoint | Perform insulation resistance test (500Vdc) as per AS/NZS 3000:2018 Section 8.3.6 Consumer mains, sub mains and final subcircuits (not socket outlets) shall not be less than 1MΩ Record results in table below -
text | f757d974-fa87-53a5-a876-1363c2815d70 |  | textbox | R-W
text | 26f62d88-0da6-5d00-bc5c-4090118e2ae6 |  | textbox | R-B
text | 77e5ed49-9ddd-5e22-adbe-9340934919a4 |  | textbox | W-B
text | 976befe2-f01d-57a7-89b3-476943a640bf |  | textbox | R-E
text | a5e58a96-94b3-5a43-a40d-2022e39afceb |  | textbox | W-E
text | 726c467d-cd8e-5173-839e-c762fbecb921 |  | textbox | B-E
text | e38ab791-88c6-59d1-be1e-f6e63ce32f01 |  | textbox | R-N
text | 902579dc-4df5-5f17-98a2-a1b0afb50c66 |  | textbox | W-N
text | 1bd220b8-2713-5d30-b3a7-b71dbfe7463c |  | textbox | B-N
text | 79534102-a1a1-5e08-b2a6-60f89fdaac56 |  | textbox | N-E
checkpoint-status |  |  | checkpoint | Perform continuity check / Polarity of each core and each armour (as applicable) as per AS/NZS 3000:2018 Section 8.3.
checkpoint-status |  |  | checkpoint | Verify Correct Circuit Connections as per AS/NZS 3000:2018 Section 8.3.8 and terminations are made as per project specifications, are tight, clean, and coated with approved anti- corrosive where applicable (i.e. earth terminations).
checkpoint-status |  |  | checkpoint | Ensure al Punch List items are recorded as per project procedure
checkpoint-status |  |  | checkpoint | Sign Off
text | 78f30b3f-674c-5a37-932a-48c5a006dd65 |  | textbox | Full Name:
text | e87472aa-dc6a-5e0f-a721-5cfb3bb61f06 |  | textbox | Position / Title:
holdpoint |  |  | signoff | Add Signature / Request Sign Off
checklist-flat |  |  | checklist | FRM - ITR 106 Single & Three Phase Sub-Circuit Test Sheet |  |  |  |  | Yes | FRM - ITR 106 Single & Three Phase Sub-Circuit Test Sheet | cadc79b7-ec96-4549-85f3-fd6d090e8613
checkpoint-status |  |  | checkpoint | De-Energised Tests
text | cff2ff8d-067a-5a36-a106-7d51c6860900 |  | textbox | Distribution Board No.:
text | 29decf64-3826-567e-bb34-ce762dd8fe2a |  | textbox | CB No.
text | 0dcfd79d-4e32-57c7-b942-1f5055ba4983 |  | textbox | Neutral No.
text | 7070972b-b5f6-517a-952a-435f41a13396 |  | textbox | Circruit No.
text | 3f0fb67f-23cd-54c4-a20e-bcba18fcbb69 |  | textbox | Cable Size
text | 0160a150-081e-59ed-bad7-5a802d1e64c2 |  | textbox | Destination
text | e04e42ce-de3c-5e10-9760-addebf4b2ced |  | textbox | No. Pts
boolean | 48d6901a-bf76-5d05-8027-54395b88adcd |  | tickbox | Visual Check
text | 115c8642-a907-501b-97c8-b2c4059f7572 |  | textbox | CB Size (Amps) & Type (A,B,C,D)
text | cf6c5ae6-4b1d-566a-b96a-8632b7bc9e39 |  | textbox | Earth Continuity (Ω)
label | 86f22ae8-1b63-5d27-af31-56d5cde3d217 |  | note | Insulation Resistance (MΩ)
text | c67c2791-296b-597d-9844-79f490d480de |  | textbox | Red to White
text | 68601738-7695-5f2e-89cb-998036e1969d |  | textbox | White to Blue
text | bd4ccf15-2626-5c7a-9042-9874ca91cfb9 |  | textbox | Blue to Red
text | 72bd9e44-92c0-5c04-8e1b-48f684cbdef6 |  | textbox | A Phase to Neutral
text | 24545014-69c0-508f-aaa7-d5898b06696a |  | textbox | B Phase to Neutral
text | d8382fe6-0b51-5d76-be00-f7e250eca94f |  | textbox | C Phase to Neutral
text | 91f2b6ee-3131-59be-ac1c-1f83662af53f |  | textbox | Phases to Earth
text | b93bc147-d2ae-542b-8cf2-cf360ac687c3 |  | textbox | Neutral to Earth
boolean | 8faf718f-1d7a-5253-bbcf-493f54c9f0f9 |  | tickbox | Polarity Pass
boolean | d041fce2-424c-51dd-92bf-e06aab283021 |  | tickbox | Correct circuit connections
checkpoint-status |  |  | checkpoint | Safe to Energise
holdpoint |  |  | signoff | Ensure safe to energise
checkpoint-status |  |  | checkpoint | Energised Tests
text | 1053e2a9-5683-5338-822e-dfddc04d60e1 |  | textbox | Voltage (V)
text | bf21eb4e-696b-550a-8bb7-a9d657e31abb |  | textbox | Phase Sequence
text | 4d0970a2-def9-50e6-84d9-95b4020ba80f |  | textbox | Fault Loop Impedance
label | baf6b7aa-7ba8-5c3f-9f70-75bac89393fa |  | note | RCD Timed Test (mS)
label | ec13d481-346d-5935-9274-fa2ae4fccc4b |  | note | 30mA / 10mA
checkpoint-status |  |  | checkpoint | Sign Off
text | 78f30b3f-674c-5a37-932a-48c5a006dd65 |  | textbox | Full Name:
text | e87472aa-dc6a-5e0f-a721-5cfb3bb61f06 |  | textbox | Position / Title:
holdpoint |  |  | signoff | Add Signature / Request Sign Off