## QA Folder Structure
QA Folder Structure |  |  | Checklists
Site QA
| Initial Inspection |  | Pre-Inspection Checklist
Tower A
|  | 1st to 4th Floor - Facade Subsill | Enviro HP1200+800TC
|  | 4th Floor Perimeter Set Downs | Enviro HP1200+800TC
|  | Roof Plant | Enviro HP1200+800TC
|  | LMR Roof | Enviro HP1200+800TC
|  | 4th Upper Floor - Plant Room | Enviro 700X
|  | 34th Floor - AHU Room | Enviro 700X
|  | 53rd Floor - Plant Room & Relief Air Fan Room | Enviro 700X
|  | 53rd Floor - Domestic Water Tank Floor & Wall | Enviro HP1200
|  | 53rd Floor - Damper Tank Floor & Wall | Enviro HP1200
Tower B
|  | 4th Floor - Facade Subsill | Enviro HP1200+800TC
|  | 4th Floor Perimeter Set Downs | Enviro HP1200+800TC
|  | Roof | Enviro HP1200+800TC
|  | LMR Roof | Enviro HP1200+800TC
|  | 3rd Floor - Plant Room & Cooling Tower | Enviro 700X
|  | 3rd Mezzanine Floor - Pool Plant | Enviro 700X
|  | 25th Floor - Plant Room | Enviro 700X
|  | 25th Floor - Domestic Water Tank Floor & Wall | Enviro HP1200
|  | 25th Floor - To Underneath of Domestic Water Tank | Enviro 700X

## ITPs Checklists
type | name | values
checklist-flat | Delivery Checklist
checkpoint | Check correct materials are received at least 24 hours prior to commencing work on site
text | Batch No.
label | Specification / Standard: AS4654.1-2012; Manufacturer’s Technical Data Sheet
label | Attach Delivery Docket
checklist-flat | Enviro HP1200
checkpoint | Relevant Australian Standards Checked
label | AS4654.2-2012; Manufacturer’s Technical Data Sheet
checkpoint | Check substrate - The surface must be clean, dry and free from all loose particles
checkpoint | Prepare surface to accept primer using scraper (and/or light grind) and vacuum/sweep residual debris. Remove all concrete/mortar projections
label | Attach Photo
checkpoint | Moisture Content Test
label | Attach Photo
checkpoint | Caulking - Apply Enviro Flex FC / PRO to the junction between floor slab and walls
label | Attach Photo
checkpoint | Apply primer using a brush or roller
label | Attach Photo
checkpoint | Mixing
checkpoint | Apply Enviro HP1200 using a spray gun
checkpoint | Curing
checkpoint | Pin Hole Detection Test of area with holiday tester Pull Off Adhesion Testing shall not be less than 1MPa. Thickness shall not be less than 1.5mm
label | Attach Photo
checkpoint | Final Inspection and Sign-off. Visually inspect and ensure adequately cured - DO NOT PASS UNTIL HOLDPOINT COMPLETE BELOW
holdpoint | HOLD POINT - CLICK HERE TO REQUEST BUILDER SIGN OFF
checklist-flat | Enviro HP1200+800TC
checkpoint | Relevant Australian Standards Checked
label | AS4654.2-2012; Manufacturer’s Technical Data Sheet
checkpoint | Check substrate - The surface must be clean, dry and free from all loose particles
checkpoint | Prepare surface to accept primer using scraper (and/or light grind) and vacuum/sweep residual debris. Remove all concrete/mortar projections
label | Attach Photo
checkpoint | Moisture Content Test
label | Attach Photo
checkpoint | Caulking - Apply Enviro Flex FC / PRO to the junction between floor slab and walls
label | Attach Photo
checkpoint | Apply primer using a brush or roller
label | Attach Photo
checkpoint | Mixing
checkpoint | Apply Enviro HP1200 using a spray gun
checkpoint | Curing
checkpoint | Pin Hole Detection Test of area with holiday tester Pull Off Adhesion Testing shall not be less than 1MPa. Thickness shall not be less than 1.5mm
label | Attach Photo
checkpoint | Top Coat - Mix and Apply Enviro 800TC with brush or new roller (spray application optional) Re-apply as required or determined by the Specification
checkpoint | Pin Hole Detection Test of area with holiday tester Pull Off Adhesion Testing shall not be less than 1MPa. Thickness shall not be less than 1.5mm
label | Attach Photo
checkpoint | Final Inspection and Sign-off. Visually inspect and ensure adequately cured - DO NOT PASS UNTIL HOLDPOINT COMPLETE BELOW
holdpoint | HOLD POINT - CLICK HERE TO REQUEST BUILDER SIGN OFF
checklist-flat | Enviro HP1200+850TC
checkpoint | Relevant Australian Standards Checked
label | AS4654.2-2012; Manufacturer’s Technical Data Sheet
checkpoint | Check substrate - The surface must be clean, dry and free from all loose particles
label | Attach Photo
checkpoint | Prepare surface to accept primer using scraper (and/or light grind) and vacuum/sweep residual debris. Remove all concrete/mortar projections
label | Attach Photo
checkpoint | Moisture Content Test
checkpoint | Caulking - Apply Enviro Flex FC / PRO to the junction between floor slab and walls
label | Attach Photo
checkpoint | Apply primer using a brush or roller
label | Attach Photo
checkpoint | Mixing
checkpoint | Apply Enviro HP1200 using a spray gun
checkpoint | Curing
checkpoint | Pin Hole Detection Test of area with holiday tester Pull Off Adhesion Testing shall not be less than 1MPa. Thickness shall not be less than 1.5mm
label | Attach Photo
checkpoint | Top Coat - Mix and Apply Enviro 850TC with brush or new roller (spray application optional) Re-apply as required or determined by the Specification
label | Attach Photo
checkpoint | Pin Hole Detection Test of area with holiday tester Pull Off Adhesion Testing shall not be less than 1MPa. Thickness shall not be less than 1.5mm
label | Attach Photo
checkpoint | Final Inspection and Sign-off. Visually inspect and ensure adequately cured - DO NOT PASS UNTIL HOLDPOINT COMPLETE BELOW
holdpoint | HOLD POINT - CLICK HERE TO REQUEST BUILDER SIGN OFF
checklist-flat | Enviro HP1200+900+850TC
checkpoint | Relevant Australian Standards Checked
label | AS4654.2-2012; Manufacturer’s Technical Data Sheet
checkpoint | Check substrate - The surface must be clean, dry and free from all loose particles
label | Attach Photo
checkpoint | Prepare surface to accept primer using scraper (and/or light grind) and vacuum/sweep residual debris. Remove all concrete/mortar projections
label | Attach Photo
checkpoint | Moisture Content Test
label | Attach Photo
checkpoint | Caulking - Apply Enviro Flex FC / PRO to the junction between floor slab and walls
label | Attach Photo
checkpoint | Apply primer using a brush or roller
label | Attach Photo
checkpoint | Mixing
checkpoint | Apply Enviro HP1200 using a spray gun
checkpoint | Curing
checkpoint | Pin Hole Detection Test of area with holiday tester Pull Off Adhesion Testing shall not be less than 1MPa. Thickness shall not be less than 1.5mm
label | Attach Photo
checkpoint | Wear Coat - Mix and Apply Enviro 900 with brush or new roller (spray application optional) Broadcast aggregate uniformly to the wet Enviro 900 within the timeframes specified
label | Attach Photo
checkpoint | Top Coat Mix and Apply Enviro 850 with brush or new roller (second coat optional pending specification)
label | Attach Photo
checkpoint | Final Inspection and Sign-off. Visually inspect and ensure adequately cured - DO NOT PASS UNTIL HOLDPOINT COMPLETE BELOW
holdpoint | HOLD POINT - CLICK HERE TO REQUEST BUILDER SIGN OFF
checklist-flat | Enviro 700X
checkpoint | Relevant Australian Standards Checked
text | Specification / Standard: AS4654.1-2012; AS3740 - 2010, Manufacturer’s Technical Data Sheet
checkpoint | Check substrate - The surface must be clean, dry and free from all loose particles
label | Attach Photo
checkpoint | Prepare surface to accept primer using scraper (and/or light grind) and vacuum/sweep residual debris. Remove all concrete/mortar projections
label | Attach Photo
checkpoint | Moisture Content Test
label | Attach Photo
checkpoint | Caulking - Apply Enviro Flex FC / PRO to the junction between floor slab and walls
label | Attach Photo
checkpoint | Apply primer using a brush or roller
label | Attach Photo
checkpoint | Membrane Application (1st coat) - Apply Enviro 700X using a brush or roller
checkpoint | Curing - Allow to cure in accordance with Manufacturers Specifications
checkpoint | Membrane Application (2nd coat) - Apply Enviro 700X using a brush or roller
checkpoint | Flood Testing (if required)
label | Attach Photo
checkpoint | Final Inspection and Sign-off. Visually inspect and ensure adequately cured - DO NOT PASS UNTIL HOLDPOINT COMPLETE BELOW
holdpoint | HOLD POINT - CLICK HERE TO REQUEST BUILDER SIGN OFF
checklist-flat | Enviro 200P
checkpoint | Relevant Australian Standards Checked
label | Specification / Standard: AS3740 - 2010, Manufacturer’s Technical Data Sheet
checkpoint | Check Substrate - The surface must be clean, dry and free from all loose particles
checkpoint | Prepare surface to accept primer using scraper (and/or light grind) and vacuum/sweep residual debris. Remove all concrete/mortar projections.
label | Attach Photo
checkpoint | Moisture Content Test
label | Attach Photo
checkpoint | Caulking - Apply Enviro Flex FC / PRO to the junction between floor slab and walls
label | Attach Photo
checkpoint | Apply primer using a brush or roller
label | Attach Photo
checkpoint | Membrane Application (1st coat) - Apply Enviro 200P using a brush or roller
checkpoint | Curing - Allow to cure in accordance with Manufacturers Specifications
checkpoint | Membrane Application (2nd coat) - Apply Enviro 200P using a brush or roller
checkpoint | Flood Testing (if required)
label | Attach Photo
checkpoint | Final Inspection and Sign-off. Visually inspect and ensure adequately cured - DO NOT PASS UNTIL HOLDPOINT COMPLETE BELOW
holdpoint | HOLD POINT - CLICK HERE TO REQUEST BUILDER SIGN OFF
checklist-flat | Enviro Flex 2 Part
checkpoint | Relevant Australian Standards Checked
label | Specification / Standard: AS3740 - 2010, Manufacturer’s Technical Data Sheet
checkpoint | Check Substrate - The surface must be clean, dry and free from all loose particles
checkpoint | Prepare surface to accept primer using scraper (and/or light grind) and vacuum/sweep residual debris. Remove all concrete/mortar projections.
label | Attach Photo
checkpoint | Moisture Content Test
label | Attach Photo
checkpoint | Caulking - Apply Enviro Flex FC / PRO to the junction between floor slab and walls
label | Attach Photo
checkpoint | Apply primer using a brush or roller
label | Attach Photo
checkpoint | Membrane Application (1st coat) - Apply Enviro Flex 2 Part using a brush or roller
checkpoint | Curing - Allow to cure in accordance with Manufacturers Specifications
checkpoint | Membrane Application (2nd coat) - Apply Enviro Flex 2 Part using a brush or roller
checkpoint | Flood Testing (if required)
label | Attach Photo
checkpoint | Final Inspection and Sign-off. Visually inspect and ensure adequately cured - DO NOT PASS UNTIL HOLDPOINT COMPLETE BELOW
holdpoint | HOLD POINT - CLICK HERE TO REQUEST BUILDER SIGN OFF
checklist-flat | Enviro Epoxy RC / Ultra Tuff
checkpoint | Relevant Australian Standards Checked
label | Specification / Standard: AS3740 - 2010, Manufacturer’s Technical Data Sheet
checkpoint | Check Substrate - The surface must be clean, dry and free from all loose particles
checkpoint | Prepare surface to accept primer using scraper (and/or light grind) and vacuum/sweep residual debris. Remove all concrete/mortar projections.
label | Attach Photo
checkpoint | Moisture Content Test
label | Attach Photo
checkpoint | Cutting - Make sure that adjoining ends of intersecting waterstop segments are cut extremely straight
label | Attach Photo
checkpoint | Apply primer using a brush or roller
label | Attach Photo
checkpoint | Epoxy Application (1st coat) - Apply Enviro Epoxy RC / Enviro Ultra Tuff with a brush, roller or spray
label | (If no aggregate is required, 1st coat of epoxy can be dilluted with 10% xylene
label | If aggregate is required, broadcast at correct coverage while 1st coat has been applied and is in it's wet state prior to curing
checkpoint | Epoxy Application (2nd Coat) - Apply Enviro Epoxy RC / Enviro Ultra Tuff with a brush, roller or spray
checkpoint | Final Inspection and Sign-off. Visually inspect and ensure adequately cured.
checkpoint | Final Inspection and Sign-off. Visually inspect and ensure adequately cured - DO NOT PASS UNTIL HOLDPOINT COMPLETE BELOW
holdpoint | HOLD POINT - CLICK HERE TO REQUEST BUILDER SIGN OFF
checklist-flat | Enviro Hydrostatic 1
checkpoint | Relevant Australian Standards Checked
label | Specification / Standard: AS4654.2-2012, Manufacturer’s Technical Data Sheet
checkpoint | Check Substrate - The surface must be clean, dry and free from all loose particles
checkpoint | Prepare surface to accept primer using scraper (and/or light grind) and vacuum/sweep residual debris. Remove all concrete/mortar projections.
label | Attach Photo
checkpoint | Caulking - Apply Enviro Flex FC / PRO to the junction between floor slab and walls
label | Attach Photo
checkpoint | Primer application - Lightly Spray areas to receive Hydrostatic 1
label | Attach Photo
checkpoint | Membrane Application (1st coat) - Mix Enviro Hydrostatic 1 thoroughly using a mechanical mixer. Apply first coat of Enviro Hydrostatic 1 by brush or roller Use Enviro Joint Band in floor-wall junctions and general movement joints
checkpoint | Membrane Application (2nd coat) - Mix Enviro Hydrostatic 1 thoroughly using a mechanical mixer. Apply second coat of Enviro Hydrostatic 1 by brush or roller
checkpoint | Curing - Allow to cure in accordance with Manufacturers Specifications
checkpoint | Final Inspection and Sign-off. Visually inspect and ensure adequately cured - DO NOT PASS UNTIL HOLDPOINT COMPLETE BELOW
holdpoint | HOLD POINT - CLICK HERE TO REQUEST BUILDER SIGN OFF
checklist-flat | Enviro Clad
checkpoint | Relevant Australian Standards Checked
label | Specification / Standard: AS4654.2-2012, Manufacturer’s Technical Data Sheet
checkpoint | Check Substrate - The surface must be clean, dry and free from all loose particles
checkpoint | Prepare surface to accept primer using scraper (and/or light grind) and vacuum/sweep residual debris. Remove all concrete/mortar projections.
label | Attach Photo
checkpoint | Primer Application - Pending Substrate Condition, Apply Enviro Prime WB using a brush or roller
label | Attach Photo
checkpoint | Caulking - Apply Enviro Flex FC / PRO to the junction between floor slab and walls
label | Attach Photo
checkpoint | Membrane Application (1st coat) - Mix and Apply Enviro Clad as a first coat to the thicknesses prescribed by the specifications
checkpoint | Membrane Application (2nd coat) - Mix and Apply Enviro Clad as a second coat to the thicknesses prescribed by the specifications
checkpoint | Curing - Allow to cure in accordance with Manufacturers Specifications
checkpoint | Final Inspection and Sign-off. Visually inspect and ensure adequately cured - DO NOT PASS UNTIL HOLDPOINT COMPLETE BELOW
holdpoint | HOLD POINT - CLICK HERE TO REQUEST BUILDER SIGN OFF
checklist-flat | Enviro 700X + 200P
checkpoint | Relevant Australian Standards Checked
text | Specification / Standard: AS4654.1-2012; AS3740 - 2010, Manufacturer’s Technical Data Sheet
checkpoint | Check Substrate Check for cracks/defect in concrete. Check critical areas (puddle flanges, penetrations, expansion joints, rebates/setdowns).
label | Attach Photo
checkpoint | Prepare Substrate. (moisture test if required) prepare surface to accept primer using a scraper or grinder and vacuum or sweep residual debris.
label | Attach Photo
checkpoint | Apply primer (Enviro Shield/Enviro prime P2 or Enviro Epoxy B-LV) by brush/roller
label | Attach Photo
checkpoint | Caulking. Apply Enviro Flex FC junction fillets (where applicable)
label | Attach Photo
checkpoint | Mixing and Application. Mix Enviro 700X thoroughtly using mechanical mixer. Apply Enviro 700X using brush/roller achieving 1.6mm WFT / 1.5mm DFT.
label | Attach Photo
checkpoint | Testing. Flood test when applicable.
label | Attach Photo
checkpoint | First signoff. Visually inspect and ensure adequately cured. Check for any pinholes and bubbles. Sign-off from builder.
checkpoint | Check Screed (moisture test if required).
checkpoint | Apply primer (Enviro Shield/Enviro Shield or Prime WB by brush/roller
label | Attach Photo
checkpoint | Apply first coat of Enviro 200P Ultra with a brush or roller.
label | Attach Photo
checkpoint | Apply second coat of Enviro 200P Ultra with a brush or roller. Achieve 0.8mm WFT and 1.0mm DFT.
label | Attach Photo
checkpoint | Final signoff. Visually inspect and ensure adequately cured. Sign-off from builder and hand-over
holdpoint | HOLD POINT - CLICK HERE TO REQUEST BUILDER SIGN OFF
checklist-flat | Enviro CSH
checkpoint | Relevant Australian Standards Checked
label | Specification / Standard: Manufacturer’s Technical Data Sheet
checkpoint | Check Substrate. (moisture test if oncrete not fully cured) and prepare surface using a scraper or grinder and vacuum or sweep residual debris.
checkpoint | Check for cracks/defect in concrete.
label | Attach Photo
checkpoint | Perform mechanical profiling / shot blasting to concrete
label | Visual
checkpoint | Spray Enviro CSH concrete surface hardener and moisture barrier, first application
label | Visual
checkpoint | Spray Enviro CSH concrete surface hardener and moisture barrier, second application
label | Visual
checkpoint | Final Inspection and Sign-off. Visually inspect and ensure adequately cured - DO NOT PASS UNTIL HOLDPOINT COMPLETE BELOW
label | Attach Photo.
holdpoint | HOLD POINT - CLICK HERE TO REQUEST BUILDER SIGN OFF
checklist-flat | Enviro 700X + 800TC
checkpoint | Relevant Australian Standards Checked
text | Specification / Standard: AS4654.1-2012; AS3740 - 2010, Manufacturer’s Technical Data Sheet
checkpoint | Check substrate. The surface must be clean, dry and free from all loose particles including dust, laitance, grease, coatings, curing compounds and any other foreign matter. Check critical areas (puddle flanges, penetrations, expansion joints, rebates/setdowns)
label | Attach Photo
checkpoint | Substrate Preparation and Caulking. Prepare surface to accept primer using a scraper or grinder and vacuum or sweep residual debris. Remove all sharp edges including screws, nails and concrete/mortar projections. Apply a suitable and approved joint sealant such as Enviro Flex Pro or Enviro Flex FC to all joints and connecting building parts prior to the application of Enviro 700X.
label | Attach Photo
checkpoint | Priming. Apply primer (Enviro Epoxy B-LV / Enviro Prime P2 / Enviro Shield) using a brush or roller. Allow primer to fully cure before proceeding with the application of Enviro 700X.
label | Attach Photo
checkpoint | Mixing and Application. Enviro 700X should be thoroughly mixed with a mechanical mixer at low speed (less than 400 RPM) prior to application. Apply Enviro 700X using brush/roller achieving 1.6mm WFT / 1.5mm DFT. (2 coats).
label | Attach Photo
checkpoint | Curing. Allow product to cure for 12 hours before recoating. Care should be taken when walking over newly installed Enviro 700X to ensure the membrane is not damaged.
checkpoint | Top Coat. Enviro 800 TC should be thoroughly mixed using a mechanical mixer at low speed prior to application.Add Part B to Part A and mix to a uniform colour and consistency for a minimum of 3 minutes. Allow to react for 10 minutes before application. Allow to react for 15 minutes when thinning with Enviro Thinner No.8 before application. Do not apply in damp or wet conditions. Allow each coat to sufficiently dry before proceeding to the next coat.
label | Attach Photo
checkpoint | Testing. Carry out Spark Testing and adhesion tests. Repair pinholes and imperfections. Areas marked indicate location of Test.
label | Attach Photo
checkpoint | Final signoff and handover. Visually inspect and ensure adequately cured. Check for any pinholes and bubbles. Sign-off from builder and hand-over
holdpoint | HOLD POINT - CLICK HERE TO REQUEST BUILDER SIGN OFF
checklist-flat | Enviro Shield / Prime P2 / Epoxy B-LV
checkpoint | Relevant Australian Standards Checked
text | Specification / Standard: AS4654.1-2012; AS3740 - 2010, Manufacturer’s Technical Data Sheet
checkpoint | Check Screed (moisture test if required, Enviro Shield is moisture tolerant.)
label | Attach Photo
checkpoint | Apply first coat of Enviro Shield with a brush or roller.
label | Visual
checkpoint | Apply second coat of Enviro Shield with a brush or roller.
label | Attach photo
checkpoint | Protection board. Install Elmich Versidrain 8 Geo. Applicable to planters only
label | Attach photo
checkpoint | Final signoff and handover. Visually inspect and ensure adequately cured. Check for any pinholes and bubbles. Sign-off from builder and hand-over
holdpoint | HOLD POINT - CLICK HERE TO REQUEST BUILDER SIGN OFF
checklist-flat | Enviro HP1200+Shield
checkpoint | Relevant Australian Standards Checked
label | AS4654.2-2012; Manufacturer’s Technical Data Sheet
checkpoint | Check Substrate Check for cracks/defect in concrete. Check critical areas (puddle flanges, penetrations, expansion joints, rebates/setdowns).
label | Attach Photo
checkpoint | Prepare Substrate. (moisture test if required) and prepare surface to accept primer using a scraper or grinder and vacuum or sweep residual debris.
label | Attach Photo
checkpoint | Check label on drum(s) to ensure correct material is being used
checkpoint | Apply primer (Enviro prime P2 or Enviro Epoxy B-LV) by brush/roller
label | Attach Photo
checkpoint | Caulking/ Joints. Apply bondbreaker at junctions
label | Attach Photo
checkpoint | Mixing. Mix HP 1200. Mixing by way of 1:1 mix ratio (by volume) in heated plural component spray equipment such as Graco E-10 or EXP-2. Both low and high pressure spray equipment can be used for the application of Enviro HP1200.
label | Attach Photo
checkpoint | Application. Spray on Enviro HP1200. Achieve 1.5mm DFT.
label | Attach Photo
checkpoint | Testing. Carry out Spark Testing and adhesion tests. Repair pinholes and imperfections. Areas marked indicate location of Test.
label | Attach Photo
checkpoint | First signoff. Visually inspect and ensure adequately cured. Check for any pinholes and bubbles. Sign-off from builder and hand-over if applicable.
checkpoint | Check Screed (areas where applicable) moisture test if required, Enviro Shield is moisture tolerant.
checkpoint | Apply first coat of Enviro Shield with a brush or roller.
label | Attach Photo
checkpoint | Apply second coat of Enviro Shield with a brush or roller.
label | label
checkpoint | Final Inspection and Sign-off. Visually inspect and ensure adequately cured - DO NOT PASS UNTIL HOLDPOINT COMPLETE BELOW
holdpoint | HOLD POINT - CLICK HERE TO REQUEST BUILDER SIGN OFF
checklist-flat | Enviro HP1200+900
checkpoint | Relevant Australian Standards Checked
label | AS4654.2-2012; Manufacturer’s Technical Data Sheet
checkpoint | Check substrate - Check for cracks/defect in concrete. Check critical areas (puddle flanges, penetrations, expansion joints, rebates/setdowns).
label | Attach Photo of substrate
checkpoint | Prepare surface to accept primer using scraper (and/or light grind) and vacuum/sweep residual debris. Remove all concrete/mortar projections
label | Attach Photo.
checkpoint | Moisture Content Test.
label | Attach Photo of moiture reading or enter moisture reading in comment section
checkpoint | Check label on drum to ensure correct material is being used
checkpoint | Caulking - Apply Enviro Flex FC / PRO to the junction between floor slab and walls
label | Attach Photo
checkpoint | Apply primer using a brush or roller
label | Visual inspection, ensure adequately cured.
checkpoint | Caulking - Apply Enviro Flex FC / PRO to the junction between floor slab and walls
checkpoint | Mixing. Mix HP 1200. Mixing by way of 1:1 mix ratio (by volume) in heated plural component spray equipment such as Graco E-10 or EXP-2. Both low and high pressure spray equipment can be used for the application of Enviro HP1200.
checkpoint | Apply Enviro HP1200 using a spray gun. Achieve 1.5mm DFT.
label | Attach photo.
checkpoint | Curing
checkpoint | Testing. Carry out Spark Testing and adhesion tests. Repair pinholes and imperfections. Areas marked indicate location of Test.
label | Attach Photo
checkpoint | Wear Coat - Mix and Apply Enviro 900 with brush or new roller (spray application optional) Broadcast aggregate uniformly to the wet Enviro 900 within the timeframes specified
label | Attach Photo
checkpoint | Top Coat Mix and Apply Enviro 850 with brush or new roller (second coat optional pending specification)
label | Attach Photo
checkpoint | DFT Testing
label | Attach Photo. Enter DFT reading on comment section.
checkpoint | Final Inspection and Sign-off. Visually inspect and ensure adequately cured - DO NOT PASS UNTIL HOLDPOINT COMPLETE BELOW
holdpoint | HOLD POINT - CLICK HERE TO REQUEST BUILDER SIGN OFF
checklist-flat | Enviro 200P Secondary
checkpoint | Relevant Australian Standards Checked
label | Specification / Standard: AS3740 - 2010, Manufacturer’s Technical Data Sheet
checkpoint | Check Screed (moisture test if required).
label | Attach Photo
checkpoint | Apply Primer. Enviro Shield or Enviro Prime WB.
label | Visual
checkpoint | Apply first coat of Enviro 200P with a brush or roller.
label | Visual
checkpoint | Apply first coat of Enviro 200P with a brush or roller. Achieve 0.8mm WFT and 1.0mm DFT.
label | Attach Photo of WFT reading. Enter WFT reading on comment section.
checkpoint | Final Inspection and Sign-off. Visually inspect and ensure adequately cured - DO NOT PASS UNTIL HOLDPOINT COMPLETE BELOW
holdpoint | HOLD POINT - CLICK HERE TO REQUEST BUILDER SIGN OFF
checklist-flat | Patching and Handover to Bondek
checkpoint | Relevant Australian Standards Checked
label | AS4654.2-2012; Manufacturer’s Technical Data Sheet
checkpoint | Check membrane - Check for damages to membrane.
label | Attach Photo of damages
checkpoint | Patching. Apply Enviro HP1200 using a spray gun. Achieve 1.5mm DFT. Or Apply Enviro 700X.
label | Attach photo of patching.
checkpoint | Lapping to blockwork prior to bondek being laid. Apply Enviro HP1200 using a spray gun. Achieve 1.5mm DFT. Or Apply Enviro 700X.
label | Attach Photo of lap to blockwork.
checkpoint | Final Inspection and Sign-off. Visually inspect and ensure adequately cured - DO NOT PASS UNTIL HOLDPOINT COMPLETE BELOW
holdpoint | HOLD POINT - CLICK HERE TO REQUEST BUILDER SIGN OFF
checklist-flat | Pre-Inspection Checklist
section | General Area
checkpoint | Has the builder provided a marked up plan on each area to be waterproofed?
label | Marked up plan has to be numbered if more than one area at a time is to be completed
checkpoint | Has the concrete been cured for 28 days, date of pour to be provided?
checkpoint | Has concrete moisture test been carried out and the result was provided for the locations on a marked up plan?
label | The moisture level should be around 7%
checkpoint | Is the concrete finished to an acceptable steel trowel class finish?
checkpoint | Have all tape, steel wire, nails, plywood or formwork, bracing, dyna bolt and/or steel brackets been removed and patched?
checkpoint | Is there any cracking in the substrate? If yes, an engineer’s report will need to be provided or the builder must sign off prior to commencement of works
checkpoint | Has any chemicals been used in the concrete process that may affect the membrane adhesion?
section | Hobbs
checkpoint | Spalling
checkpoint | Laitance
checkpoint | Boney Concrete
checkpoint | Prework was under standard
checkpoint | Form Ply Ridges
section | Wall
checkpoint | Spalling
checkpoint | Laitance
checkpoint | Boney Concrete
checkpoint | Prework was under standard
checkpoint | Form Ply Ridges
section | Floor
checkpoint | Spalling
checkpoint | Laitance
checkpoint | Boney Concrete
checkpoint | Prework was under standard
checkpoint | Form Ply Ridges
section | Access
checkpoint | Puddle flanges used or installed must be recessed flush to the top of the concrete surface
holdpoint | Builder to check correct falls to drains
checkpoint | Patching to be completed 3 days prior to waterproofing proposed start date and/or second inspection required
checkpoint | Adequate spacing to seal around each one for Cast in items (conduit, water pipes etc). No flexible conduits permitted
checkpoint | Would recommend using Enviro mortar 45 for all pin holes, overfilled then stoned back when dry
checklist-flat | Enviro HP1200 + 700X
checkpoint | Relevant Australian Standards Checked
text | Specification / Standard: AS4654.1-2012; AS3740 - 2010, Manufacturer’s Technical Data Sheet
checkpoint | Check substrate. The surface must be clean, dry and free from all loose particles including dust, laitance, grease, coatings, curing compounds and any other foreign matter. Check critical areas (puddle flanges, penetrations, expansion joints, rebates/setdowns)
label | Attach Photo
checkpoint | Substrate Preparation and Caulking. Prepare surface to accept primer using a scraper or grinder and vacuum or sweep residual debris. Remove all sharp edges including screws, nails and concrete/mortar projections. Apply a suitable and approved joint sealant such as Enviro Flex Pro or Enviro Flex FC to all joints and connecting building parts prior to the application of Enviro 700X
label | Attach Photo
checkpoint | Priming. Apply primer (Enviro Epoxy B-LV / Enviro Prime P2 / Enviro Shield) using a brush or roller. Allow primer to fully cure before proceeding with the application of Enviro 700X
label | Attach Photo
checkpoint | Mixing and Application. HP1200 should be thoroughly mixed with a mechanical mixer at low speed (less than 400 RPM) prior to application. Apply Enviro 700X using brush/roller achieving 1.6mm WFT / 1.5mm DFT. (2 coats)
label | Attach Photo
checkpoint | Curing. Allow product to cure for 12 hours before recoating. Care should be taken when walking over newly installed Enviro 700X to ensure the membrane is not damaged
checkpoint | Top Coat. Enviro 700X should be thoroughly mixed using a mechanical mixer at low speed prior to application.Add Part B to Part A and mix to a uniform colour and consistency for a minimum of 3 minutes. Allow to react for 10 minutes before application. Allow to react for 15 minutes when thinning with Enviro Thinner No.8 before application. Do not apply in damp or wet conditions. Allow each coat to sufficiently dry before proceeding to the next coat
label | Attach Photo
checkpoint | Testing. Carry out Spark Testing and adhesion tests. Repair pinholes and imperfections. Areas marked indicate location of Test
label | Attach Photo
checkpoint | Final signoff and handover. Visually inspect and ensure adequately cured. Check for any pinholes and bubbles. Sign-off from builder and hand-over
holdpoint | HOLD POINT - CLICK HERE TO REQUEST BUILDER SIGN OFF
checklist-flat | Enviro P2 + HP1200
checkpoint | Relevant Australian Standards Checked
text | Specification / Standard: AS4654.1-2012; AS3740 - 2010, Manufacturer’s Technical Data Sheet
checkpoint | Check substrate. The surface must be clean, dry and free from all loose particles including dust, laitance, grease, coatings, curing compounds and any other foreign matter. Check critical areas (puddle flanges, penetrations, expansion joints, rebates/setdowns)
label | Attach Photo
checkpoint | Substrate Preparation and Caulking. Prepare surface to accept primer using a scraper or grinder and vacuum or sweep residual debris. Remove all sharp edges including screws, nails and concrete/mortar projections. Apply a suitable and approved joint sealant such as Enviro Flex Pro or Enviro Flex FC to all joints and connecting building parts prior to the application of Enviro 700X
label | Attach Photo
checkpoint | Priming. Apply P2 using a brush or roller. Allow primer to fully cure before proceeding with the application of Enviro 700X
label | Attach Photo
checkpoint | Mixing and Application. HP1200 should be thoroughly mixed with a mechanical mixer at low speed (less than 400 RPM) prior to application
label | Attach Photo
checkpoint | Curing. Allow product to cure for 12 hours before recoating. Care should be taken when walking over newly installed waterproofing system to ensure the membrane is not damaged
checkpoint | Top Coat. should be thoroughly mixed using a mechanical mixer at low speed prior to application.Add Part B to Part A and mix to a uniform colour and consistency for a minimum of 3 minutes. Allow to react for 10 minutes before application. Allow to react for 15 minutes when thinning with Enviro Thinner No.8 before application. Do not apply in damp or wet conditions. Allow each coat to sufficiently dry before proceeding to the next coat
label | Attach Photo
checkpoint | Testing. Carry out Spark Testing and adhesion tests. Repair pinholes and imperfections. Areas marked indicate location of Test
label | Attach Photo
checkpoint | Final signoff and handover. Visually inspect and ensure adequately cured. Check for any pinholes and bubbles. Sign-off from builder and hand-over
holdpoint | HOLD POINT - CLICK HERE TO REQUEST BUILDER SIGN OFF
checklist-flat | Enviro BSM
checkpoint | Relevant Australian Standards Checked
text | Specification / Standard: AS4654.1-2012; AS3740 - 2010, Manufacturer’s Technical Data Sheet
checkpoint | Check substrate. Blinding sound and level, Trowel finished, no voids or leftover formwork or sharp edges. NCR any unacceptable items
label | Attach Photo
checkpoint | Free substrate of Dirt and Debris where required.
label | Attach Photo
checkpoint | Reinspect substrate. Polyseal applicator - Area clean and dry, ready to instal sheet membrane
label | Attach Photo
checkpoint | Lay BSM - Overlap as per manufacturers instructions, stragger cut joins where possible, detail strip to be installed at cut joins.
label | Attach Photo
checkpoint | Apply Hp 1600 to Dwall BEFORE bars ensure lap down onto BSM
label | Attach Photo
checkpoint | Following bar install, bar to be detailed with flex fc, 700x to be applied with a 50mm return on the bar, bars to be epoxied in by others (generous amount of epoxy required)
label | Attach Photo
checkpoint | epoxy incapulation to pipe penos, Pile cap to be incapsulated with epoxy grout 50mm finished height
label | Attach Photo
checkpoint | InspecInspection of Membrane - Pre Reo (Polyseal & Client & Enviro systems )tion of Membrane, All Elements to be reinspected. Corner terminations, overlaps, pile heads
label | Attach Photo
checkpoint | Final signoff and handover. Visually inspect and ensure adequately cured. Check for any pinholes and bubbles. Sign-off from builder and hand-over
holdpoint | HOLD POINT - CLICK HERE TO REQUEST BUILDER SIGN OFF
checklist-flat | Enviro HP1600
checkpoint | Relevant Australian Standards Checked
label | AS4654.2-2012; Manufacturer’s Technical Data Sheet
checkpoint | Check substrate - The surface must be clean, dry and free from all loose particles
checkpoint | Prepare surface to accept primer using scraper (and/or light grind) and vacuum/sweep residual debris. Remove all concrete/mortar projections
label | Attach Photo
checkpoint | Moisture Content Test
label | Attach Photo
checkpoint | Caulking - Apply Enviro Flex FC / PRO to the junction between floor slab and walls
label | Attach Photo
checkpoint | Apply primer using a brush or roller
label | Attach Photo
checkpoint | Mixing
checkpoint | Apply Enviro HP1600 using a spray gun
checkpoint | Curing
checkpoint | Pin Hole Detection Test of area with holiday tester Pull Off Adhesion Testing shall not be less than 1MPa. Thickness shall not be less than 1.5mm
label | Attach Photo
checkpoint | Final Inspection and Sign-off. Visually inspect and ensure adequately cured - DO NOT PASS UNTIL HOLDPOINT COMPLETE BELOW
holdpoint | HOLD POINT - CLICK HERE TO REQUEST BUILDER SIGN OFF
checklist-flat | Enviro BLV + HP1200
checkpoint | Relevant Australian Standards Checked
text | Specification / Standard: AS4654.1-2012; AS3740 - 2010, Manufacturer’s Technical Data Sheet
checkpoint | Check substrate. The surface must be clean, dry and free from all loose particles including dust, laitance, grease, coatings, curing compounds and any other foreign matter. Check critical areas (puddle flanges, penetrations, expansion joints, rebates/setdowns)
label | Attach Photo
checkpoint | Substrate Preparation and Caulking. Prepare surface to accept primer using a scraper or grinder and vacuum or sweep residual debris. Remove all sharp edges including screws, nails and concrete/mortar projections. Apply a suitable and approved joint sealant such as Enviro Flex Pro or Enviro Flex FC to all joints and connecting building parts prior to the application of Enviro 700X
label | Attach Photo
checkpoint | Priming. Apply BLV using a brush or roller. Allow primer to fully cure before proceeding with the application of HP1200
label | Attach Photo
checkpoint | Mixing and Application. HP1200 should be thoroughly mixed with a mechanical mixer at low speed (less than 400 RPM) prior to application
label | Attach Photo
checkpoint | Curing. Allow product to cure for 12 hours before recoating. Care should be taken when walking over newly installed waterproofing system to ensure the membrane is not damaged
checkpoint | Top Coat. should be thoroughly mixed using a mechanical mixer at low speed prior to application.Add Part B to Part A and mix to a uniform colour and consistency for a minimum of 3 minutes. Allow to react for 10 minutes before application. Allow to react for 15 minutes when thinning with Enviro Thinner No.8 before application. Do not apply in damp or wet conditions. Allow each coat to sufficiently dry before proceeding to the next coat
label | Attach Photo
checkpoint | Testing. Carry out Spark Testing and adhesion tests. Repair pinholes and imperfections. Areas marked indicate location of Test
label | Attach Photo
checkpoint | Final signoff and handover. Visually inspect and ensure adequately cured. Check for any pinholes and bubbles. Sign-off from builder and hand-over
holdpoint | HOLD POINT - CLICK HERE TO REQUEST BUILDER SIGN OFF
checklist-flat | Sika Sarnafil
checkpoint | Relevant Australian Standards Checked
text | Specification / Standard: AS4654.1-2012; AS3740 - 2010, Manufacturer’s Technical Data Sheet
checkpoint | Check Substrate Check for cracks/defect in concrete. Check critical areas (puddle flanges, penetrations, expansion joints, rebates/setdowns).
label | Attach Photo
checkpoint | Prepare Substrate. (moisture test if required) prepare surface to accept primer using a scraper or grinder and vacuum or sweep residual debris.
label | Attach Photo
checkpoint | Apply Sarnacol. Record atmospheric & substrate conditions & notate in QA Documents. Humidity <85%, Delta >3⁰, Air Temp 5-40⁰.
label | Attach Photo
checkpoint | Apply Sarnafil. Overlap as per manufacturers instructions,75mm, stagger cut joins where possible, detail strip to be installed at cut joins.
label | Attach Photo
checkpoint | Weld all joins, Ensure PPE, Respirator, fire extuinguisher within vicinity. Weld overlap in one direction to avoid ribbons --Ensure 75mm overlap
label | Attach Photo
checkpoint | Install Pressure Bar, Install as instructed by builder to finish termination height. Install sealant is placed above pressure bar. Every second hole on pressure bar to be drilled. 1 hole overlap on edge of termination bar
label | Attach Photo
checkpoint | Check all welds with spatula/screwdriver for lifts. Use blunt pointed object to ensure all welds correctly sealed. Any lifts, circle to return to weld
label | Attach Photo
checkpoint | First signoff. Visually inspect and ensure adequately cured. Check for any potential defects. Sign-off from builder.
checkpoint | Inspection of welds. All Elements to be inspected. Corner terminations, overlaps, lifts, burns, joins, and pressure seal
checkpoint | Test Welds. All Elements to be reinspected. Corner terminations, overlaps, pile heads. ensure all action items from previous inspection have been resolved.
label | Attach Photo
checkpoint | Final signoff. Visually inspect and ensure adequately cured. Sign-off from builder and hand-over
holdpoint | HOLD POINT - CLICK HERE TO REQUEST BUILDER SIGN OFF
Checklist | Combiflex
checkpoint | Relevant Australian Standards Checked
text | Specification / Standard: AS4654.1-2012; AS3740 - 2010, Manufacturer’s Technical Data Sheet
checkpoint | Check Substrate Check for cracks/defect in concrete. Check critical areas (puddle flanges, penetrations, expansion joints, rebates/setdowns).
label | Attach Photo
checkpoint | Prepare Substrate. (moisture test if required) prepare surface to accept primer using a scraper or grinder and vacuum or sweep residual debris.
label | Attach Photo
checkpoint | Measure and Temporarily fix ElastoFlex or Combiflex
label | Attach Photo
checkpoint | Install ElastoFlex or Combiflex to Movement Joint locations
label | Attach Photo
checkpoint | Remove Push Pins and Patch holes
label | Attach Photo
checkpoint | Inspect Length of Combiflex material
label | Attach Photo
checkpoint | Inspect Length of epoxy anchor
label | Attach Photo
checkpoint | Carry ouf sprinkler testing
label | Attach Photo
checkpoint | Check Substrate & Repair defects
label | Attach Photo
checkpoint | Final signoff. Visually inspect and ensure adequately cured. Sign-off from builder and hand-over
holdpoint | HOLD POINT - CLICK HERE TO REQUEST BUILDER SIGN OFF
checklist-flat | Enviro HP1200+900+800TC
checkpoint | Relevant Australian Standards Checked
label | AS4654.2-2012; Manufacturer’s Technical Data Sheet
checkpoint | Check substrate - The surface must be clean, dry and free from all loose particles
label | Attach Photo
checkpoint | Prepare surface to accept primer using scraper (and/or light grind) and vacuum/sweep residual debris. Remove all concrete/mortar projections
label | Attach Photo
checkpoint | Moisture Content Test
label | Attach Photo
checkpoint | Caulking - Apply Enviro Flex FC / PRO to the junction between floor slab and walls
label | Attach Photo
checkpoint | Apply primer using a brush or roller
label | Attach Photo
checkpoint | Mixing
checkpoint | Apply Enviro HP1200 using a spray gun
checkpoint | Curing
checkpoint | Pin Hole Detection Test of area with holiday tester Pull Off Adhesion Testing shall not be less than 1MPa. Thickness shall not be less than 1.5mm
label | Attach Photo
checkpoint | Wear Coat - Mix and Apply Enviro 900 with brush or new roller (spray application optional) Broadcast aggregate uniformly to the wet Enviro 900 within the timeframes specified
label | Attach Photo
checkpoint | Top Coat Mix and Apply Enviro 850 with brush or new roller (second coat optional pending specification)
label | Attach Photo
checkpoint | Final Inspection and Sign-off. Visually inspect and ensure adequately cured - DO NOT PASS UNTIL HOLDPOINT COMPLETE BELOW
holdpoint | HOLD POINT - CLICK HERE TO REQUEST BUILDER SIGN OFF
checklist-flat | Enviro Shield + 700X
checkpoint | Relevant Australian Standards Checked
text | Specification / Standard: AS4654.1-2012; AS3740 - 2010, Manufacturer’s Technical Data Sheet
checkpoint | Check Substrate/Work Area, Check for cracks/defect in concrete. Check critical areas (puddle flanges, penetrations, expansion joints, rebates/setdowns).
label | Attach Photo
checkpoint | Prepare Substrate. (moisture test if required) Prepare surface to accept primer using a scraper or grinder and vacuum or sweep residual debris.
label | Attach Photo
checkpoint | Apply primer (Enviro Shield/Enviro prime P2 or Enviro Epoxy B-LV) by brush/roller
label | Attach Photo
checkpoint | Caulking. Apply Enviro Flex FC junction fillets (where applicable)
label | Attach Photo
checkpoint | Mixing and Application. Mix Enviro 700X thoroughtly using mechanical mixer. Apply Enviro 700X using brush/roller achieving 1.6mm WFT / 1.5mm DFT.
label | Attach Photo
checkpoint | Carry out Dry Film Thickness test & Holiday Testing & Pull Off Test, Repair any defects found using patch and repair method specified in procedures.
label | Attach Photo
checkpoint | Final Inspection and Sign-off. Visually inspect and ensure adequately cured - DO NOT PASS UNTIL HOLDPOINT COMPLETE BELOW
holdpoint | HOLD POINT - CLICK HERE TO REQUEST BUILDER SIGN OFF