## Sheet1
151021 | X | Type | Name | Values | Prefix | Postfix
TST |  | checklist | TST Testing Storm Water Drainage (Air Test)
TST |  | checkpoint | Tested & Checked off as below
TST |  | label | Pressure reading photo's must be taken at start & finish of test. Comments as applicable
TST |  | button | Installer is a Registered Plumber (VIC) with endorsements for this work | Yes, No, N/A
TST |  | button | Installation complies with current AS/NZS-3500 (2018) | Yes, No, N/A
TST |  | button | Installation complies with current drawings & specifications | Yes, No, N/A
TST |  | button | Installation materials were used in accordance with manufacturer requirements | Yes, No, N/A
TST |  | button | Check internal bore clear of blockages, constrictions or debris | Yes, No, N/A
TST |  | button | Check pipe-work is secure to eliminate movement during test | Yes, No, N/A
TST |  | button | Plug & seal open ends of pipe-work section to be tested | Yes, No, N/A
TST |  | button | Provide a temporary valved test point with union fitting | Yes, No, N/A
TST |  | button | Connect pressure testing device to temporary valve point | Yes, No, N/A
TST |  | button | Commence testing by slowly increasing pressure up to 30 kPa and hold | Yes, No, N/A
TST |  | button | Discontinue pressurization & allow system to stabilization over 3 minutes | Yes, No, N/A
TST |  | button | Testing is deemed successful if pressure drop is ≤ 5kPa over at least 30 minutes | Yes, No, N/A
TST |  | button | If test is successful, slowly release test pressure and return the system back to neutral working conditions | Yes, No, N/A
TST |  | bool | Confirm test photo' s have been taken
TST |  | checkpoint | Supervisor cleared test as successful
TST |  | label | Supervisor to add test type & location to ITP name
TST |  | bool | Test passed sticker applied
Note on B2: X = Make Available in +Add Checklist Folder