## Resources
Rich Type | Id | Warnings | type | name | values | prefix | postfix | Usage Count | User Addable | Template Name | Template Id
checklist-flat |  |  | checklist | TST Testing Potable Water (900 kPa Test 3) - [Island Sink] |  |  |  |  | Yes | TST Testing Potable Water (900 kPa Test 3) - [Island Sink] | 98ec1963-f3ed-4d46-bdf0-92e47973cb1c
checkpoint-status |  |  | checkpoint | This testing procedure conforms with that as set out in AS-3500.1 (2018) &/or AS-3500.4 (2018)
checkpoint-status |  |  | checkpoint | Ensure all valves dedicated to isolating the test zone are securely shut off & tagged
checkpoint-status |  |  | checkpoint | Nominate an air purging valve point
checkpoint-status |  |  | checkpoint | Nominate a pressure testing valve point (if none at meter manifold)
checkpoint-status |  |  | checkpoint | Ensure isolating valves within the test zone are open as required
checkpoint-status |  |  | checkpoint | Ensure all terminal open ends i.e. lugged elbows, etc are securely capped off
checkpoint-status |  |  | checkpoint | Slowly open a feeder valve & fill the test zone with water until completely purged of any air
checkpoint-status |  |  | checkpoint | Connect pressure testing device to the nominated test point
checkpoint-status |  |  | checkpoint | Shut off the water feeder valve
checkpoint-status |  |  | checkpoint | Commence testing by slowly increasing pressure up to 900 kPa and hold for 30 minutes
checkpoint-status |  |  | checkpoint | [For Couta System] Release pressure down to 500 kpa and hold briefly
checkpoint-status |  |  | checkpoint | [For Couta System] Rapidly increase shock pressure back to 900 kPa and hold for test duration
checkpoint-status |  |  | checkpoint | Testing is deemed successful if the water pressure remains unchanged after 30 minutes
checkpoint-status |  |  | checkpoint | If test is successful, slowly release test pressure and return the system back to neutral conditions
checkpoint-status |  |  | checkpoint | Test sticker in visible location
checkpoint-status |  |  | checkpoint | Test result recorded by photo/time/date
checkpoint-status |  |  | checkpoint | Test route/location attached to this Check Point as PDF plan or snap shot with its unique I.D. number.
checkpoint-status |  |  | checkpoint | Failures are to be immediately reported to management for analysis & repatriation
checklist-flat |  |  | checklist | CW Risers (Pumped or Mains Pressure Risers) |  |  |  |  | Yes | CW Risers (Pumped or Mains Pressure Risers) | 99c7faa4-35ff-46b6-9b71-30627d5aa21c
checkpoint-status |  |  | checkpoint | This installation and following checks are to comply with AS-3500
checkpoint-status |  |  | checkpoint | General visual check for pipe damage/leaks, etc
checkpoint-status |  |  | checkpoint | Penetrations are installed
checkpoint-status |  |  | checkpoint | Pipe materials are correct for application
checkpoint-status |  |  | checkpoint | Pipe-work is designed, installed & sized as per current IFC documentation
checkpoint-status |  |  | checkpoint | Check all valves &/or meter assemblies conform with current documentation
checkpoint-status |  |  | checkpoint | Ensure all risers are installed professionally with no abnormalities
checkpoint-status |  |  | checkpoint | Roll Groove joints are torqued down to manufacturers Instructions
checkpoint-status |  |  | checkpoint | Welded pipe joints are completed
checkpoint-status |  |  | checkpoint | CU pressed pipe joints crimped & witness marked as per manufacturers instructions
checkpoint-status |  |  | checkpoint | XLPE pipe joints are correctly crimped & witness marked as per manufacturers instructions
checkpoint-status |  |  | checkpoint | Pipe penetrations are caulked
checkpoint-status |  |  | checkpoint | Anchors are installed as per manufacturer instructions & compliant with AS3500
checkpoint-status |  |  | checkpoint | Clips are solidly fixed & of correct size/type as per manufactures instructions.
checkpoint-status |  |  | checkpoint | Clips & spacing are installed & compliant with AS3500
checkpoint-status |  |  | checkpoint | Expansion device or loop is correctly sized & installed conforming with AS3500
checkpoint-status |  |  | checkpoint | Isolation valves are installed & flow correct
checkpoint-status |  |  | checkpoint | Test by Pneumatic/Hydrostatic method as per AS3500 & RSG procedure
checkpoint-status |  |  | checkpoint | Test sticker to be adhered to pipe 1500mm above floor level facing a corridor or accessible wall
checkpoint-status |  |  | checkpoint | Test result to be recorded by photo/time/date. (Provide comment if required)
checkpoint-status |  |  | checkpoint | Pipe I.D. labels are installed & spaced compliant with AS3500
checkpoint-status |  |  | checkpoint | Isolation valves closed after testing (If Required)
checklist-flat |  |  | checklist | Enter Level/Apartment/Description |  |  |  |  | Yes | Record Hold-Up | 6b94d177-5eb8-424a-8de6-e10d24b9600b
checkpoint-status |  |  | checkpoint | Decription of Hold Up
label | 5e0751f9-320c-4de6-84d9-cea2d37df381 |  | note | (See Photos & Comments Attached Below)
checklist-flat |  |  | checklist | RW Rough-in (Low Level) |  |  |  |  | Yes | RW Rough-in (Low Level) | 6359299e-92fb-440d-89b7-8f99d16b128e
checkpoint-status |  |  | checkpoint | This installation and following checks are to comply with AS-3500
checkpoint-status |  |  | checkpoint | Check general visual check for pipe damage/leaks, etc
checkpoint-status |  |  | checkpoint | Pipe materials are correct for application
checkpoint-status |  |  | checkpoint | Check silicone applied to studs
checkpoint-status |  |  | checkpoint | Check in-wall noggings are installed to correct locations
checkpoint-status |  |  | checkpoint | Check In-wall lugged elbows are installed to correct locations
checkpoint-status |  |  | checkpoint | Check in-wall pan/cistern brackets are installed to correct locations
checkpoint-status |  |  | checkpoint | Check for possible cross connections
checkpoint-status |  |  | checkpoint | Check all crimped joints & witness marks
checkpoint-status |  |  | checkpoint | Check clip spacing are correct at ≤600mm
checkpoint-status |  |  | checkpoint | Test by Pneumatic/Hydrostatic method as per AS3500 & RSG procedure
checkpoint-status |  |  | checkpoint | Test result to be recorded by photo/time/date. (Provide comment if required)
checkpoint-status |  |  | checkpoint | Pipe I.D. labels are installed & spaced compliant with AS3500
checkpoint-status |  |  | checkpoint | Seal or cap off any open ends if required for security
checkpoint-status |  |  | checkpoint | Isolation valves closed after testing (If Required)
checklist-flat |  |  | checklist | CW Rough-in (Low Level) |  |  |  |  | Yes | CW Rough-in (Low Level) | 799accd0-743f-41ef-ad95-7ca019d8dc4f
checkpoint-status |  |  | checkpoint | This installation and following checks are to comply with AS-3500
checkpoint-status |  |  | checkpoint | Check general visual check for pipe damage/leaks, etc
checkpoint-status |  |  | checkpoint | Pipe materials are correct for application
checkpoint-status |  |  | checkpoint | Check silicone applied to studs
checkpoint-status |  |  | checkpoint | Check TCV/TMV in wall box correct location & securely clipped
checkpoint-status |  |  | checkpoint | Check RPZD in wall box correct location & securely clipped
checkpoint-status |  |  | checkpoint | Check in-wall noggings are installed to correct locations
checkpoint-status |  |  | checkpoint | Check In-wall mixer bodies & lugged elbows are installed to correct locations
checkpoint-status |  |  | checkpoint | Check in-wall pan/cistern brackets are installed to correct locations
checkpoint-status |  |  | checkpoint | Check for possible cross connections
checkpoint-status |  |  | checkpoint | Check all crimped joints & witness marks
checkpoint-status |  |  | checkpoint | Check clip spacing are correct at ≤600mm
checkpoint-status |  |  | checkpoint | Test by Pneumatic/Hydrostatic method as per AS3500 & RSG procedure
checkpoint-status |  |  | checkpoint | Test result to be recorded by photo/time/date. (Provide comment if required)
checkpoint-status |  |  | checkpoint | Pipe I.D. labels are installed & spaced compliant with AS3500
checkpoint-status |  |  | checkpoint | Seal or cap off any open ends if required for security
checkpoint-status |  |  | checkpoint | Isolation valves closed after testing (If Required)
checklist-flat |  |  | checklist | NG Rough-in (Low Level) |  |  |  |  | Yes | NG Rough-in (Low Level) | 84f37fec-ecdb-46db-88ef-b08a1c8fd9b2
checkpoint-status |  |  | checkpoint | This installation and following checks are to comply with AS-5601
checkpoint-status |  |  | checkpoint | Check general visual check for pipe damage/leaks, etc
checkpoint-status |  |  | checkpoint | Pipe materials are correct for application
checkpoint-status |  |  | checkpoint | Check silicone applied to studs
checkpoint-status |  |  | checkpoint | Check in-wall noggings are installed to correct locations
checkpoint-status |  |  | checkpoint | Check In-wall lugged elbows are installed to correct locations
checkpoint-status |  |  | checkpoint | Check all crimped joints & witness marks
checkpoint-status |  |  | checkpoint | Check clip spacing are correct at ≤600mm
checkpoint-status |  |  | checkpoint | Test by Pneumatic/Hydrostatic method as per AS3500 & RSG procedure
checkpoint-status |  |  | checkpoint | Test result to be recorded by photo/time/date. (Provide comment if required)
checkpoint-status |  |  | checkpoint | Pipe I.D. labels are installed & spaced compliant with AS3500
checkpoint-status |  |  | checkpoint | Seal or cap off any open ends if required for security
checkpoint-status |  |  | checkpoint | Isolation valves closed after testing (If Required)
checklist-flat |  |  | checklist | PE In-Ground Grease Arresting Tank |  |  |  |  | Yes | PE In-Ground Grease Arresting Tank | 09bbf263-ffb9-4c35-8c48-a3a61d7695f1
checkpoint-status |  |  | checkpoint | The installer is qualified & trained to carry out the task as assigned
checkpoint-status |  |  | checkpoint | Authority applications & start work notices accepted
checkpoint-status |  |  | checkpoint | Plant & Equipment installation conforms with current IFC documentation
checkpoint-status |  |  | checkpoint | General finish & alignment both level & finished height are OK
checkpoint-status |  |  | checkpoint | General visual check for damage, etc
checkpoint-status |  |  | checkpoint | Finished R.L. are correct & verified
checkpoint-status |  |  | checkpoint | Vents are installed if required
checkpoint-status |  |  | checkpoint | Backfill is specified materials & compacted to test OK
checkpoint-status |  |  | checkpoint | Spoil is removed
checkpoint-status |  |  | checkpoint | Inlet drain is installed & connected
checkpoint-status |  |  | checkpoint | Outlet drain is installed & connected
checkpoint-status |  |  | checkpoint | Disconnector trap is installed & connected
checkpoint-status |  |  | checkpoint | Vacuum-line installed & connected
checkpoint-status |  |  | checkpoint | Vacuum-line stortz couplings & caps are installed
checkpoint-status |  |  | checkpoint | Test by Pneumatic/Hydrostatic method as per AS3500 & RSG procedure
checkpoint-status |  |  | checkpoint | Test result to be recorded by photo/time/date. (Provide comment if required)
checklist-flat |  |  | checklist | TST Testing Sewer Drainage (Water Test) |  |  |  |  | Yes | TST Testing Sewer Drainage (Water Test) | 9c35aeb5-672a-469d-8521-6cb658713606
checkpoint-status |  |  | checkpoint | This testing procedure conforms with that as set out in AS-3500.2 (2018)
checkpoint-status |  |  | checkpoint | Ensure bore is completely free of any blockages, constrictions or debris
checkpoint-status |  |  | checkpoint | Ensure pipe-work is securely fixed to eliminate movement during pressure test
checkpoint-status |  |  | checkpoint | Temporarily plug & seal any open ends below the test point (i.e. floor or shower wastes)
checkpoint-status |  |  | checkpoint | Extend a temporary test point riser to a height of 1 metre above the highest overflow point
checkpoint-status |  |  | checkpoint | Slowly fill the test riser with water until full and hold for at least 15 minutes
checkpoint-status |  |  | checkpoint | Testing is deemed successful if the water level remains unchanged after 15 minutes
checkpoint-status |  |  | checkpoint | If test is successful, slowly release test pressure and return the system back to neutral working conditions
checkpoint-status |  |  | checkpoint | Test sticker on pipe 1500mm high facing a corridor or accessible wall
checkpoint-status |  |  | checkpoint | Test result recorded by photo/time/date
checkpoint-status |  |  | checkpoint | Test route/location attached to this Check Point as PDF plan or snap shot with its unique I.D. number.
checkpoint-status |  |  | checkpoint | Failures are to be immediately reported to management for analysis & repatriation
checklist-flat |  |  | checklist | RW Re-Cycled Water Meters |  |  |  |  | Yes | RW Re-Cycled Water Meters | 34471f47-7f5c-4297-b735-729243971eee
checkpoint-no-status |  |  | checkpoint | Water Meter Details:
text | 3a842720-b0d6-447b-815a-7c3714f51389 |  | textbox | Meter No:
text | 9e936261-4077-4692-8f37-55dbf67efe15 |  | textbox | Level:
text | f98875b6-e440-4fdc-b254-3b035d8e4905 |  | textbox | Meter Size:
checkpoint-status |  |  | checkpoint | General visual check for pipe damage/leaks, etc
checkpoint-status |  |  | checkpoint | Meter installed & sized as per current documentation
checkpoint-status |  |  | checkpoint | Meter bracketed
checkpoint-status |  |  | checkpoint | Analogue meter display is facing upright
checkpoint-status |  |  | checkpoint | Confirm I.D. point against the meter register
checkpoint-status |  |  | checkpoint | Pulse rate value is correct
checkpoint-status |  |  | checkpoint | Pulse rate is output is manually proved
checkpoint-status |  |  | checkpoint | BMS wiring connected by mechanical contractor
checkpoint-status |  |  | checkpoint | Flow direction is correct
checkpoint-status |  |  | checkpoint | Pipe I.D. labels are installed & spaced compliant with AS3500
checkpoint-status |  |  | checkpoint | Record installation by photo & time/date
checkpoint-status |  |  | checkpoint | Isolation valves closed after testing (If Required)
checklist-flat |  |  | checklist | MT Cold Water Meters |  |  |  |  | Yes | MT Cold Water Meters | 1567fc4d-ad73-4303-8d8f-75530683ff2f
checkpoint-status |  |  | checkpoint | This installation and following checks are to comply with AS-3500
checkpoint-status |  |  | checkpoint | Water Meter Details:
text | 2b6ff227-c467-4723-b371-f38c65be908e |  | textbox | Meter No:
text | 6d4c22e7-8831-42b1-8524-ea3316fafb4b |  | textbox | Meter Location:
text | 762e9d10-91a6-4891-b7cc-030f54cd427f |  | textbox | Meter Size:
checkpoint-status |  |  | checkpoint | General visual check for pipe damage/leaks, etc
checkpoint-status |  |  | checkpoint | Meter installed & sized as per current documentation
checkpoint-status |  |  | checkpoint | Meter bracketed
checkpoint-status |  |  | checkpoint | Analogue meter display is facing upright
checkpoint-status |  |  | checkpoint | Confirm I.D. point against the meter register
checkpoint-status |  |  | checkpoint | Pulse rate value is correct
checkpoint-status |  |  | checkpoint | Pulse rate is output is manually proved
checkpoint-status |  |  | checkpoint | BMS wiring connected by mechanical contractor
checkpoint-status |  |  | checkpoint | Flow direction is correct
checkpoint-status |  |  | checkpoint | Pipe I.D. labels are installed & spaced compliant with AS3500
checkpoint-status |  |  | checkpoint | Test result to be recorded by photo/time/date. (Provide comment if required)
checkpoint-status |  |  | checkpoint | Isolation valves closed after testing (If Required)
checklist-flat |  |  | checklist | FO Install Cold Water RPZD |  |  |  |  | Yes | FO Install Cold Water RPZD | 0ada9a84-8d95-4844-8a55-7aa3fede5152
checkpoint-status |  |  | checkpoint | Pipe-work installed & sized as per current documentation
checkpoint-status |  |  | checkpoint | General finish & alignment both level & finished height are OK
checkpoint-status |  |  | checkpoint | General visual check for damage, etc
checkpoint-status |  |  | checkpoint | Visual check for water leakage
checkpoint-status |  |  | checkpoint | Mountings fixed & torqued down
checkpoint-status |  |  | checkpoint | Inlet pipework is installed & connected
checkpoint-status |  |  | checkpoint | Outlet pipework is installed & connected
checkpoint-status |  |  | checkpoint | Connection flanges fixed & torqued down to manufacturer specification
checkpoint-status |  |  | checkpoint | RPZD tested & certified buy qualified practitioner
checkpoint-status |  |  | checkpoint | Testing by pressurized Water or Air as per RSG procedure is completed
checkpoint-status |  |  | checkpoint | Test result is compliant with AS3500 (Record test by photo & time/date)
checklist-flat |  |  | checklist | PE Hot Water Generating Packaged Plant |  |  |  |  | Yes | PE Hot Water Generating Packaged Plant | 575b0e3b-7fa7-46a4-8faa-e6b487c24f75
checkpoint-status |  |  | checkpoint | The installer is qualified & trained to carry out the task as assigned
checkpoint-status |  |  | checkpoint | Plant & Equipment installation conforms with current IFC documentation
checkpoint-status |  |  | checkpoint | General finish & alignment both level & finished height are OK
checkpoint-status |  |  | checkpoint | General visual check for damage, etc
checkpoint-status |  |  | checkpoint | Visual check for water leakage
checkpoint-status |  |  | checkpoint | Perform natural gas leak detection procedure
checkpoint-status |  |  | checkpoint | Mountings fixed & torqued down to plinth
checkpoint-status |  |  | checkpoint | Cold water check meter is installed & connected
checkpoint-status |  |  | checkpoint | Natural gas check meter is installed & connected
checkpoint-status |  |  | checkpoint | Cold water inlet pipework is installed & connected
checkpoint-status |  |  | checkpoint | Hot water outlet pipework is installed & connected
checkpoint-status |  |  | checkpoint | Hot water return pipework is installed & connected
checkpoint-status |  |  | checkpoint | Hot water pipework is thermally insulated & correct weight as designed
checkpoint-status |  |  | checkpoint | Exposed hot water pipework is completely sheaved & weather proofed
checkpoint-status |  |  | checkpoint | Natural gas inlet pipework is installed & connected
checkpoint-status |  |  | checkpoint | Connection flanges fixed & torqued down to manufacturer specification
checkpoint-status |  |  | checkpoint | Hot water exhaust pipework discharges over dedicated hot water tolerant drain point
checkpoint-status |  |  | checkpoint | Electrolysis prevention in place if required
checkpoint-status |  |  | checkpoint | Electrical cable is installed
checkpoint-status |  |  | checkpoint | Power flue is installed & terminated as per design
checkpoint-status |  |  | checkpoint | Control panel is installed
checkpoint-status |  |  | checkpoint | Electrical Connections to control panel installed by electrician
checkpoint-status |  |  | checkpoint | Electrical Connections is certified by electrician
checkpoint-status |  |  | checkpoint | Pumps cycles set & test run & certified by pump provider
checkpoint-status |  |  | checkpoint | Pressure gauges installed & running within operating limits
checkpoint-status |  |  | checkpoint | Flow & return temperature gauges installed & running within operating limits
checkpoint-status |  |  | checkpoint | Hot water plant provider has fully commissioned & certified the plant
checkpoint-status |  |  | checkpoint | Test by Pneumatic/Hydrostatic method as per AS3500 & RSG procedure
checkpoint-status |  |  | checkpoint | Test result to be recorded by photo/time/date. (Provide comment if required)
checklist-flat |  |  | checklist | CW Cold Water Tapping to Meter Room |  |  |  |  | Yes | CW Cold Water Tapping to Meter Room | fc21886b-8255-4ea2-aadf-557f10aab7cf
checkpoint-status |  |  | checkpoint | This installation and following checks are to comply with AS-3500
checkpoint-status |  |  | checkpoint | DBYD received & verified before commencement of work
checkpoint-status |  |  | checkpoint | Traffic management plan in place & approved
checkpoint-status |  |  | checkpoint | Authority water applications & start work notices accepted
checkpoint-status |  |  | checkpoint | Municipality asset opening notices placed & accepted
checkpoint-status |  |  | checkpoint | Authority divide valve assembly or tee insertion installed by authority contractor
checkpoint-status |  |  | checkpoint | Sluice valves installed including flanges bolted, torqued & denso protected
checkpoint-status |  |  | checkpoint | General visual check for pipe damage, etc
checkpoint-status |  |  | checkpoint | Pipe-work is designed, installed & sized as per current IFC documentation
checkpoint-status |  |  | checkpoint | Location & levels are correct
checkpoint-status |  |  | checkpoint | Pipe materials are correct for application
checkpoint-status |  |  | checkpoint | Incoming pipework is installed & layed to meter room
checkpoint-status |  |  | checkpoint | Pipe sleeve installed & sealed if required
checkpoint-status |  |  | checkpoint | Connection flanges fixed & torqued down to manufacturer specification
checkpoint-status |  |  | checkpoint | Electrolysis prevention in place if required
checkpoint-status |  |  | checkpoint | Marking tape installed
checkpoint-status |  |  | checkpoint | Backfill is specified materials & compacted to test OK
checkpoint-status |  |  | checkpoint | Spoil is removed
checkpoint-status |  |  | checkpoint | Temporary top-dress of trenches with cold mix etc.
checkpoint-status |  |  | checkpoint | Clips are solidly fixed & of correct size/type as per manufactures instructions.
checkpoint-status |  |  | checkpoint | Clips & Shanks etc. are completely corrosion protected by use of "Denso" type wrapping & sealing
checkpoint-status |  |  | checkpoint | Pipe penetrations are caulked
checkpoint-status |  |  | checkpoint | Above ground pipework fixed & pipe I.D. labelled compliant with AS3500
checkpoint-status |  |  | checkpoint | Main meter inlet valves installed & locked off
checkpoint-status |  |  | checkpoint | Connection flanges fixed & torqued down to manufacturer specification
checkpoint-status |  |  | checkpoint | Authority main meters installed & secured as per authority installation guide
checkpoint-status |  |  | checkpoint | Test by Pneumatic/Hydrostatic method as per AS3500 & RSG procedure
checkpoint-status |  |  | checkpoint | Test result to be recorded by photo/time/date. (Provide comment if required)
checklist-flat |  |  | checklist | SYP Syphonic Downpipes/Overflows (Main Droppers) |  |  |  |  | Yes | SYP Syphonic Downpipes/Overflows (Main Droppers) | 0855a240-18b6-47be-a9d1-46a9c30045b7
checkpoint-status |  |  | checkpoint | This installation and following checks are to comply with AS-3500
checkpoint-status |  |  | checkpoint | General visual check for pipe damage, etc
checkpoint-status |  |  | checkpoint | Pipe materials are correct for application
checkpoint-status |  |  | checkpoint | Downpipes are installed
checkpoint-status |  |  | checkpoint | Overflows are installed
checkpoint-status |  |  | checkpoint | Expansion joints are installed & compliant with AS3500
checkpoint-status |  |  | checkpoint | Ensure expansion joint spacers are removed
checkpoint-status |  |  | checkpoint | Clips are solidly fixed & of correct size/type as per manufactures instructions.
checkpoint-status |  |  | checkpoint | Clips & spacing are installed & compliant with AS3500
checkpoint-status |  |  | checkpoint | Penetrations are installed
checkpoint-status |  |  | checkpoint | Drain penetrations are caulked
checkpoint-status |  |  | checkpoint | Fire collars are installed & registered
checkpoint-status |  |  | checkpoint | Pipe-work is designed, installed & sized as per current IFC documentation
checkpoint-status |  |  | checkpoint | Seal or cap off any open ends if required for security
checkpoint-status |  |  | checkpoint | Acoustic insulation installed & correct weight as designed
checkpoint-status |  |  | checkpoint | Test by Pneumatic/Hydrostatic method as per AS3500 & RSG procedure
checkpoint-status |  |  | checkpoint | Test sticker to be adhered to pipe 1500mm above floor level facing a corridor or accessible wall
checkpoint-status |  |  | checkpoint | Test result to be recorded by photo/time/date. (Provide comment if required)
checkpoint-status |  |  | checkpoint | Pipe I.D. labels are installed & spaced compliant with AS3500
checklist-flat |  |  | checklist | SYP Syphonic Downpipes/Overflows (High Level) |  |  |  |  | Yes | SYP Syphonic Downpipes_Overflows (High Level) | 1fd773f9-24d4-434d-9cf0-038372e0b3e0
checkpoint-status |  |  | checkpoint | This installation and following checks are to comply with AS-3500
checkpoint-status |  |  | checkpoint | General visual check for pipe damage, etc
checkpoint-status |  |  | checkpoint | Pipe materials are correct for application
checkpoint-status |  |  | checkpoint | Downpipes are installed
checkpoint-status |  |  | checkpoint | Overflows are installed
checkpoint-status |  |  | checkpoint | Expansion joints are installed & compliant with AS3500
checkpoint-status |  |  | checkpoint | Ensure expansion joint spacers are removed
checkpoint-status |  |  | checkpoint | Clips are solidly fixed & of correct size/type as per manufactures instructions.
checkpoint-status |  |  | checkpoint | Clips & spacing are installed & compliant with AS3500
checkpoint-status |  |  | checkpoint | Penetrations are installed
checkpoint-status |  |  | checkpoint | Drain penetrations are caulked
checkpoint-status |  |  | checkpoint | Fire collars are installed & registered
checkpoint-status |  |  | checkpoint | Pipe-work is designed, installed & sized as per current IFC documentation
checkpoint-status |  |  | checkpoint | Seal or cap off any open ends if required for security
checkpoint-status |  |  | checkpoint | Acoustic insulation installed & correct weight as designed
checkpoint-status |  |  | checkpoint | Test by Pneumatic/Hydrostatic method as per AS3500 & RSG procedure
checkpoint-status |  |  | checkpoint | Test result to be recorded by photo/time/date. (Provide comment if required)
checkpoint-status |  |  | checkpoint | Pipe I.D. labels are installed & spaced compliant with AS3500
checklist-flat |  |  | checklist | FO Irrigation/Hose Taps |  |  |  |  | Yes | FO Irrigation/Hose Taps | b7d3013d-5790-4d0d-bc0d-1f6879a1fc77
checkpoint-status |  |  | checkpoint | This installation and following checks are to comply with AS-3500
checkpoint-status |  |  | checkpoint | Confirm type supplied & installed as per contract specification
checkpoint-status |  |  | checkpoint | General finish & alignment both level & centre of tapware
checkpoint-status |  |  | checkpoint | Screw-on RPZD fitting installed if required
checkpoint-status |  |  | checkpoint | Solid installation & mounting of tapware
checkpoint-status |  |  | checkpoint | Check cover plates are installed
checkpoint-status |  |  | checkpoint | Look for evidence of behind the wall leakage showing on floor
checkpoint-status |  |  | checkpoint | Valve tag or signage is installed if required.
checkpoint-status |  |  | checkpoint | Seal or cap off any open ends if required for security
checkpoint-status |  |  | checkpoint | Valve is securely turned off (if required)
checklist-flat |  |  | checklist | NG High Level/Corridors |  |  |  |  | Yes | NG High Level/Corridors | f7f35c2d-a4f5-42de-ba89-54a6d00ac032
checkpoint-status |  |  | checkpoint | This installation and following checks are to comply with AS-5601
checkpoint-status |  |  | checkpoint | General visual check for pipe damage/leaks, etc
checkpoint-status |  |  | checkpoint | Pipe materials are correct for application
checkpoint-status |  |  | checkpoint | Pipe-work is designed, installed & sized as per current IFC documentation
checkpoint-status |  |  | checkpoint | Check all valves &/or meter assemblies conform with current documentation
checkpoint-status |  |  | checkpoint | Roll Groove joints are torqued down to manufacturers Instructions
checkpoint-status |  |  | checkpoint | Welded pipe joints are completed
checkpoint-status |  |  | checkpoint | CU pressed pipe joints crimped & witness marked as per manufacturers instructions
checkpoint-status |  |  | checkpoint | XLPE pipe joints are correctly crimped & witness marked as per manufacturers instructions
checkpoint-status |  |  | checkpoint | Meter assemblies correct & bracketed
checkpoint-status |  |  | checkpoint | PR valves are installed. Pressure rate & flow correct
checkpoint-status |  |  | checkpoint | Isolation valves are installed & flow correct
checkpoint-status |  |  | checkpoint | Clips are solidly fixed & of correct size/type as per manufactures instructions.
checkpoint-status |  |  | checkpoint | Clips & spacing are installed & compliant with AS3500
checkpoint-status |  |  | checkpoint | Expansion device or loop is correctly sized & installed conforming with AS3500
checkpoint-status |  |  | checkpoint | Test by Pneumatic/Hydrostatic method as per AS3500 & RSG procedure
checkpoint-status |  |  | checkpoint | Test result to be recorded by photo/time/date. (Provide comment if required)
checkpoint-status |  |  | checkpoint | Pipe I.D. labels are installed & spaced compliant with AS3500
checkpoint-status |  |  | checkpoint | Isolation valves closed after testing (If Required)
checklist-flat |  |  | checklist | SW Downpipes/Overflows (Main Droppers) |  |  |  |  | Yes | SW Downpipes/Overflows (Main Droppers) | 70ea1f65-226b-4113-9607-b62a1d68d8a6
checkpoint-status |  |  | checkpoint | This installation and following checks are to comply with AS-3500
checkpoint-status |  |  | checkpoint | General visual check for pipe damage, etc
checkpoint-status |  |  | checkpoint | Pipe materials are correct for application
checkpoint-status |  |  | checkpoint | Downpipes are installed
checkpoint-status |  |  | checkpoint | Overflows are installed
checkpoint-status |  |  | checkpoint | Expansion joints are installed & compliant with AS3500
checkpoint-status |  |  | checkpoint | Ensure expansion joint spacers are removed
checkpoint-status |  |  | checkpoint | Clips are solidly fixed & of correct size/type as per manufactures instructions.
checkpoint-status |  |  | checkpoint | Clips & spacing are installed & compliant with AS3500
checkpoint-status |  |  | checkpoint | Penetrations are installed
checkpoint-status |  |  | checkpoint | Drain penetrations are caulked
checkpoint-status |  |  | checkpoint | Fire collars are installed & registered
checkpoint-status |  |  | checkpoint | Pipe-work is designed, installed & sized as per current IFC documentation
checkpoint-status |  |  | checkpoint | Roof/overflow outlets installed
checkpoint-status |  |  | checkpoint | Seal or cap off any open ends if required for security
checkpoint-status |  |  | checkpoint | Acoustic insulation installed & correct weight as designed
checkpoint-status |  |  | checkpoint | Test by Pneumatic/Hydrostatic method as per AS3500 & RSG procedure
checkpoint-status |  |  | checkpoint | Test sticker to be adhered to pipe 1500mm above floor level facing a corridor or accessible wall
checkpoint-status |  |  | checkpoint | Test result to be recorded by photo/time/date. (Provide comment if required)
checkpoint-status |  |  | checkpoint | Pipe I.D. labels are installed & spaced compliant with AS3500
checklist-flat |  |  | checklist | PE In-Ground Sewer Pump Station |  |  |  |  | Yes | PE In-Ground Sewer Pump Station | 04ef62b6-efc9-48af-832e-f96db1eff633
checkpoint-status |  |  | checkpoint | The installer is qualified & trained to carry out the task as assigned
checkpoint-status |  |  | checkpoint | Plant & Equipment installation conforms with current IFC documentation
checkpoint-status |  |  | checkpoint | General finish & alignment both level & finished height are OK
checkpoint-status |  |  | checkpoint | General visual check for damage, etc
checkpoint-status |  |  | checkpoint | Finished R.L. are correct & verified
checkpoint-status |  |  | checkpoint | Vents are installed if required
checkpoint-status |  |  | checkpoint | Backfill is specified materials & compacted to test OK
checkpoint-status |  |  | checkpoint | Spoil is removed
checkpoint-status |  |  | checkpoint | Inlet drain is installed & connected
checkpoint-status |  |  | checkpoint | Outlet rising mains installed & connected
checkpoint-status |  |  | checkpoint | Electrical conduit is installed
checkpoint-status |  |  | checkpoint | Electrical cable is installed
checkpoint-status |  |  | checkpoint | Control panel is installed
checkpoint-status |  |  | checkpoint | Electrical Connections to control panel installed by electrician
checkpoint-status |  |  | checkpoint | Electrical Connections is certified by electrician
checkpoint-status |  |  | checkpoint | Pumps cycles set & test run & certified by pump provider
checkpoint-status |  |  | checkpoint | Test by Pneumatic/Hydrostatic method as per AS3500 & RSG procedure
checkpoint-status |  |  | checkpoint | Test result to be recorded by photo/time/date. (Provide comment if required)
checklist-flat |  |  | checklist | FO Flood Stop Valve |  |  |  |  | Yes | FO Flood Stop Valve | 88bee434-7835-44c2-b129-69e31272f646
checkpoint-status |  |  | checkpoint | Pipe-work installed & sized as per current documentation
checkpoint-status |  |  | checkpoint | General finish & alignment both level & finished height are OK
checkpoint-status |  |  | checkpoint | General visual check for damage, etc
checkpoint-status |  |  | checkpoint | Clipped & mounted securely
checkpoint-status |  |  | checkpoint | Inlet pipework is installed & connected
checkpoint-status |  |  | checkpoint | Outlet pipework is installed & connected
checkpoint-status |  |  | checkpoint | Batteries are installed correctly
checkpoint-status |  |  | checkpoint | Control LED lights are all in the Green
checkpoint-status |  |  | checkpoint | Test result is compliant with AS3500 (Record test by photo & time/date)
checklist-flat |  |  | checklist | HW High Level/Corridors |  |  |  |  | Yes | HW High Level/Corridors | 81883985-a11b-4924-8d1b-c813671a67a8
checkpoint-status |  |  | checkpoint | This installation and following checks are to comply with AS-3500
checkpoint-status |  |  | checkpoint | General visual check for pipe damage/leaks, etc
checkpoint-status |  |  | checkpoint | Pipe materials are correct for application
checkpoint-status |  |  | checkpoint | Pipe-work is designed, installed & sized as per current IFC documentation
checkpoint-status |  |  | checkpoint | Check all valves &/or meter assemblies conform with current documentation
checkpoint-status |  |  | checkpoint | Roll Groove joints are torqued down to manufacturers Instructions
checkpoint-status |  |  | checkpoint | Welded pipe joints are completed
checkpoint-status |  |  | checkpoint | CU pressed pipe joints crimped & witness marked as per manufacturers instructions
checkpoint-status |  |  | checkpoint | XLPE pipe joints are correctly crimped & witness marked as per manufacturers instructions
checkpoint-status |  |  | checkpoint | Meter manifolds & frames are firmly bracketed & installed in sizes, quantities & locations as per design
checkpoint-status |  |  | checkpoint | PR valves are installed. Pressure rate & flow correct
checkpoint-status |  |  | checkpoint | Isolation valves are installed & flow correct
checkpoint-status |  |  | checkpoint | Balancing valves are installed & flow correct
checkpoint-status |  |  | checkpoint | Clips are solidly fixed & of correct size/type as per manufactures instructions.
checkpoint-status |  |  | checkpoint | Clips & spacing are installed & compliant with AS3500
checkpoint-status |  |  | checkpoint | Expansion device or loop is correctly sized & installed conforming with AS3500
checkpoint-status |  |  | checkpoint | Heat trace installed if required
checkpoint-status |  |  | checkpoint | Thermal insulation installed & correct weight as designed
checkpoint-status |  |  | checkpoint | Test by Pneumatic/Hydrostatic method as per AS3500 & RSG procedure
checkpoint-status |  |  | checkpoint | Test result to be recorded by photo/time/date. (Provide comment if required)
checkpoint-status |  |  | checkpoint | Pipe I.D. labels are installed & spaced compliant with AS3500
checkpoint-status |  |  | checkpoint | Isolation valves closed after testing (If Required)
checklist-flat |  |  | checklist | TST Testing Potable Water (900 kPa Test 2) |  |  |  |  | Yes | TST Testing Potable Water (900 kPa Test 2) | f21abd9c-9101-4032-bb4f-778fdb69b202
checkpoint-status |  |  | checkpoint | This testing procedure conforms with that as set out in AS-3500.1 (2018) &/or AS-3500.4 (2018)
checkpoint-status |  |  | checkpoint | Ensure all valves dedicated to isolating the test zone are securely shut off & tagged
checkpoint-status |  |  | checkpoint | Nominate an air purging valve point
checkpoint-status |  |  | checkpoint | Nominate a pressure testing valve point (if none at meter manifold)
checkpoint-status |  |  | checkpoint | Ensure isolating valves within the test zone are open as required
checkpoint-status |  |  | checkpoint | Ensure all terminal open ends i.e. lugged elbows, etc are securely capped off
checkpoint-status |  |  | checkpoint | Slowly open a feeder valve & fill the test zone with water until completely purged of any air
checkpoint-status |  |  | checkpoint | Connect pressure testing device to the nominated test point
checkpoint-status |  |  | checkpoint | Shut off the water feeder valve
checkpoint-status |  |  | checkpoint | Commence testing by slowly increasing pressure up to 900 kPa and hold for 30 minutes
checkpoint-status |  |  | checkpoint | [For Couta System] Release pressure down to 500 kpa and hold briefly
checkpoint-status |  |  | checkpoint | [For Couta System] Rapidly increase shock pressure back to 900 kPa and hold for test duration
checkpoint-status |  |  | checkpoint | Testing is deemed successful if the water pressure remains unchanged after 30 minutes
checkpoint-status |  |  | checkpoint | If test is successful, slowly release test pressure and return the system back to neutral conditions
checkpoint-status |  |  | checkpoint | Test sticker in visible location
checkpoint-status |  |  | checkpoint | Test result recorded by photo/time/date
checkpoint-status |  |  | checkpoint | Test route/location attached to this Check Point as PDF plan or snap shot with its unique I.D. number.
checkpoint-status |  |  | checkpoint | Failures are to be immediately reported to management for analysis & repatriation
checklist-flat |  |  | checklist | FO Kitchen Sinks |  |  |  |  | Yes | FO Kitchen Sinks | b8227b12-414c-4efb-b480-dbe5307bcb3f
checkpoint-status |  |  | checkpoint | This installation and following checks are to comply with AS-3500
checkpoint-status |  |  | checkpoint | Confirm type supplied & installed as per contract specification
checkpoint-status |  |  | checkpoint | General finish & alignment both level & centre of fixture/tapware
checkpoint-status |  |  | checkpoint | Solid installation & mounting of sink bowl & mixer
checkpoint-status |  |  | checkpoint | Check operation of plug & washer
checkpoint-status |  |  | checkpoint | Check for evidence of leakage
checkpoint-status |  |  | checkpoint | Check in cupboard for glue, cleaner or pencil marks
checkpoint-status |  |  | checkpoint | Check cover plates are installed
checkpoint-status |  |  | checkpoint | Check mini stops for operation & leaks
checkpoint-status |  |  | checkpoint | Check flexible connections for kinks or twisting
checkpoint-status |  |  | checkpoint | Check double bowl connector & trap is installed & nuts are tight
checkpoint-status |  |  | checkpoint | Check AAV installation (if required)
checkpoint-status |  |  | checkpoint | Operate mixer & half fill bowl then discharge
checkpoint-status |  |  | checkpoint | Check hot water delivery time & temp against contract doc's
checkpoint-status |  |  | checkpoint | Check inside bowl trap for signs of debris etc
checkpoint-status |  |  | checkpoint | Check caulking is correct
checklist-flat |  |  | checklist | SYP Syphonic Downpipes/Overflows (Grated Outlets) |  |  |  |  | Yes | SYP Syphonic Downpipes_Overflows (Grated Outlets) | fe09d158-753e-475a-9158-cae4c31198d6
checkpoint-status |  |  | checkpoint | This installation and following checks are to comply with AS-3500
checkpoint-status |  |  | checkpoint | General visual check for pipe damage, etc
checkpoint-status |  |  | checkpoint | Balcony (BO/OF) grates & bodies are installed in sizes & locations as per design
checkpoint-status |  |  | checkpoint | Trench channels & grates are installed in sizes & locations as per design
checkpoint-status |  |  | checkpoint | Cast-in round/square (RWO/OF) grates & bodies are installed in sizes & locations as per design
checkpoint-status |  |  | checkpoint | Cast-in planter box/tree grates & bodies are installed in sizes & locations as per design
checkpoint-status |  |  | checkpoint | Downpipes are installed
checkpoint-status |  |  | checkpoint | Overflows are installed
checkpoint-status |  |  | checkpoint | Penetrations are installed
checkpoint-status |  |  | checkpoint | Drain penetrations are caulked
checkpoint-status |  |  | checkpoint | Trench channels & grates are installed in sizes & locations as per design
checkpoint-status |  |  | checkpoint | Cast-in round/square grates & bodies are installed in sizes & locations as per design
checkpoint-status |  |  | checkpoint | Cast-in planter box/tree grates & bodies are installed in sizes & locations as per design
checkpoint-status |  |  | checkpoint | Fire collars are installed & registered
checkpoint-status |  |  | checkpoint | Check inside trap for signs of debris etc
checkpoint-status |  |  | checkpoint | Test result to be recorded by photo/time/date. (Provide comment if required)
checklist-flat |  |  | checklist | CW Rough-in (High Level) |  |  |  |  | Yes | CW Rough-in (High Level) | f21c656d-95a9-4b96-a7cd-05c4346bddc0
checkpoint-status |  |  | checkpoint | This installation and following checks are to comply with AS-3500
checkpoint-status |  |  | checkpoint | Check general visual check for pipe damage/leaks, etc
checkpoint-status |  |  | checkpoint | Pipe materials are correct for application
checkpoint-status |  |  | checkpoint | Check silicone applied to studs
checkpoint-status |  |  | checkpoint | Check TCV/TMV correct location & securely clipped
checkpoint-status |  |  | checkpoint | Check all valves &/or meter assemblies conform with current documentation
checkpoint-status |  |  | checkpoint | Check for possible cross connections
checkpoint-status |  |  | checkpoint | Check all crimped joints & witness marks
checkpoint-status |  |  | checkpoint | Check clip spacing are correct at ≤600mm
checkpoint-status |  |  | checkpoint | Test by Pneumatic/Hydrostatic method as per AS3500 & RSG procedure
checkpoint-status |  |  | checkpoint | Test result to be recorded by photo/time/date. (Provide comment if required)
checkpoint-status |  |  | checkpoint | Pipe I.D. labels are installed & spaced compliant with AS3500
checkpoint-status |  |  | checkpoint | Seal or cap off any open ends if required for security
checkpoint-status |  |  | checkpoint | Isolation valves closed after testing (If Required)
checklist-flat |  |  | checklist | FO Tempering Valve (TV's) |  |  |  |  | Yes | FO Tempering Valve (TV's) | 702bc021-b0dc-4ddb-8183-f339b2808542
checkpoint-status |  |  | checkpoint | This installation and following checks are to comply with AS-3500
checkpoint-status |  |  | checkpoint | Confirm type supplied & installed as per contract specification
checkpoint-status |  |  | checkpoint | General finish & alignment both level & centre of tapware
checkpoint-status |  |  | checkpoint | Solid installation & mounting of tapware
checkpoint-status |  |  | checkpoint | Check cover plates are installed
checkpoint-status |  |  | checkpoint | Look for evidence of behind the wall leakage showing on floor
checkpoint-status |  |  | checkpoint | Valve tag or signage is installed if required.
checkpoint-status |  |  | checkpoint | Check hot water delivery time & temp against contract doc's
checkpoint-status |  |  | checkpoint | Temperature test warm water to ≤ 50°C
checkpoint-status |  |  | checkpoint | Test result to be recorded by photo/time/date. (Provide comment if required)
checkpoint-status |  |  | checkpoint | Seal or cap off any open ends if required for security
checkpoint-status |  |  | checkpoint | Valve is securely turned off (if required)
checklist-flat |  |  | checklist | TST Testing Potable Water (1500 kPa) |  |  |  |  | Yes | TST Testing Potable Water (1500 kPa) | 461bfbf2-c191-45a3-9a71-b78e7ee3ce70
checkpoint-status |  |  | checkpoint | This testing procedure conforms with that as set out in AS-3500.1 (2018) &/or AS-3500.4 (2018)
checkpoint-status |  |  | checkpoint | Ensure all valves dedicated to isolating the test zone are securely shut off & tagged
checkpoint-status |  |  | checkpoint | Nominate an air purging valve point
checkpoint-status |  |  | checkpoint | Nominate a pressure testing valve point (if none at meter manifold)
checkpoint-status |  |  | checkpoint | Ensure isolating valves within the test zone are open as required
checkpoint-status |  |  | checkpoint | Ensure all terminal open ends i.e. lugged elbows, etc are securely capped off
checkpoint-status |  |  | checkpoint | Ensure all in-wall mixer assemblies & pressure sensitive meters, etc are isolated/removed from the test zone
checkpoint-status |  |  | checkpoint | Slowly open a feeder valve & fill the test zone with water until completely purged of any air
checkpoint-status |  |  | checkpoint | Connect pressure testing device to the nominated test point
checkpoint-status |  |  | checkpoint | Shut off the water feeder valve
checkpoint-status |  |  | checkpoint | Commence testing by slowly increasing pressure up to 1500 kPa and hold for 30 minutes
checkpoint-status |  |  | checkpoint | Testing is deemed successful if the water pressure remains unchanged after 30 minutes
checkpoint-status |  |  | checkpoint | If test is successful, slowly release test pressure and return the system back to neutral working conditions
checkpoint-status |  |  | checkpoint | Test sticker in visible location
checkpoint-status |  |  | checkpoint | Test result recorded by photo/time/date
checkpoint-status |  |  | checkpoint | Test route/location attached to this Check Point as PDF plan or snap shot with its unique I.D. number.
checkpoint-status |  |  | checkpoint | Failures are to be immediately reported to management for analysis & repatriation
checklist-flat |  |  | checklist | FO Dishwashers |  |  |  |  | Yes | FO Dishwashers | 84dd5ec3-d695-4099-bc25-ecc3d8878378
checkpoint-status |  |  | checkpoint | This installation and following checks are to comply with AS-3500
checkpoint-status |  |  | checkpoint | Confirm type supplied & installed as per contract specification
checkpoint-status |  |  | checkpoint | General finish & alignment both level & centre of fixture/tapware
checkpoint-status |  |  | checkpoint | Check in cupboard for glue, cleaner or pencil marks
checkpoint-status |  |  | checkpoint | Check mini stops for operation & leaks
checkpoint-status |  |  | checkpoint | Check pressure reduction valve if required
checkpoint-status |  |  | checkpoint | Check flexible CW connection for kinks or twisting
checkpoint-status |  |  | checkpoint | Check flexible waste connections for kinks or twisting
checkpoint-status |  |  | checkpoint | Check dishwasher cycle
checkpoint-status |  |  | checkpoint | Check for evidence of leakage
checkpoint-status |  |  | checkpoint | Check flexible waste connection to trap is tight
checklist-flat |  |  | checklist | TST Testing Roof Downpipes (Air Test) |  |  |  |  | Yes | TST Testing Roof Downpipes (Air Test) | 5682aecf-e2d5-4d80-b474-dc2805ff85bf
checkpoint-status |  |  | checkpoint | This testing procedure conforms with that as set out in AS-3500.3 (2018)
checkpoint-status |  |  | checkpoint | Ensure bore is completely free of any blockages, constrictions or debris
checkpoint-status |  |  | checkpoint | Ensure pipe-work is securely fixed to eliminate movement during pressure test
checkpoint-status |  |  | checkpoint | Temporarily plug & seal open ends of pipe-work section to be tested
checkpoint-status |  |  | checkpoint | Provide a temporary valved test point with union fitting
checkpoint-status |  |  | checkpoint | Connect pressure testing device to temporary valve point
checkpoint-status |  |  | checkpoint | Commence choke point testing by slowly increasing pressure up to 30 kPa
checkpoint-status |  |  | checkpoint | Hold test at 30 kPa for 3 minutes
checkpoint-status |  |  | checkpoint | Testing is deemed successful if no pressure drop is recorded up to 3 minutes
checkpoint-status |  |  | checkpoint | If test is successful, slowly release test pressure and return the system back to neutral working conditions
checkpoint-status |  |  | checkpoint | Test sticker on pipe 1500mm high facing a corridor or accessible wall
checkpoint-status |  |  | checkpoint | Test result recorded by photo/time/date
checkpoint-status |  |  | checkpoint | Test route/location attached to this Check Point as PDF plan or snap shot with its unique I.D. number.
checkpoint-status |  |  | checkpoint | Failures are to be immediately reported to management for analysis & repatriation
checklist-flat |  |  | checklist | PE In-Ground On-Site Detention Tank |  |  |  |  | Yes | PE In-Ground On-Site Detention Tank | 0969f975-cbee-4d53-81ec-c1ddc979b827
checkpoint-status |  |  | checkpoint | The installer is qualified & trained to carry out the task as assigned
checkpoint-status |  |  | checkpoint | Plant & Equipment installation conforms with current IFC documentation
checkpoint-status |  |  | checkpoint | General finish & alignment both level & finished height are OK
checkpoint-status |  |  | checkpoint | General visual check for damage, etc
checkpoint-status |  |  | checkpoint | Finished R.L. are correct & verified
checkpoint-status |  |  | checkpoint | Vents are installed if required
checkpoint-status |  |  | checkpoint | Backfill is specified materials & compacted to test OK
checkpoint-status |  |  | checkpoint | Spoil is removed
checkpoint-status |  |  | checkpoint | Inlet drain is installed & connected
checkpoint-status |  |  | checkpoint | Outlet drain is installed & connected
checkpoint-status |  |  | checkpoint | Test by Pneumatic/Hydrostatic method as per AS3500 & RSG procedure
checkpoint-status |  |  | checkpoint | Test result to be recorded by photo/time/date. (Provide comment if required)
checklist-flat |  |  | checklist | HW Risers (Pumped or Mains Pressure Risers) |  |  |  |  | Yes | HW Risers (Pumped or Mains Pressure Risers) | efb25766-486e-4320-b4ba-c25b9003ee32
checkpoint-status |  |  | checkpoint | This installation and following checks are to comply with AS-3500
checkpoint-status |  |  | checkpoint | General visual check for pipe damage/leaks, etc
checkpoint-status |  |  | checkpoint | Penetrations are installed
checkpoint-status |  |  | checkpoint | Pipe materials are correct for application
checkpoint-status |  |  | checkpoint | Pipe-work is designed, installed & sized as per current IFC documentation
checkpoint-status |  |  | checkpoint | Check all valves &/or meter assemblies conform with current documentation
checkpoint-status |  |  | checkpoint | Ensure all risers are installed professionally with no abnormalities
checkpoint-status |  |  | checkpoint | Roll Groove joints are torqued down to manufacturers Instructions
checkpoint-status |  |  | checkpoint | Welded pipe joints are completed
checkpoint-status |  |  | checkpoint | CU pressed pipe joints crimped & witness marked as per manufacturers instructions
checkpoint-status |  |  | checkpoint | XLPE pipe joints are correctly crimped & witness marked as per manufacturers instructions
checkpoint-status |  |  | checkpoint | Pipe penetrations are caulked
checkpoint-status |  |  | checkpoint | Anchors are installed as per manufacturer instructions & compliant with AS3500
checkpoint-status |  |  | checkpoint | Clips are solidly fixed & of correct size/type as per manufactures instructions.
checkpoint-status |  |  | checkpoint | Clips & spacing are installed & compliant with AS3500
checkpoint-status |  |  | checkpoint | Expansion device or loop is correctly sized & installed conforming with AS3500
checkpoint-status |  |  | checkpoint | Isolation valves are installed & flow correct
checkpoint-status |  |  | checkpoint | Heat trace installed if required
checkpoint-status |  |  | checkpoint | Thermal insulation installed & correct weight as designed
checkpoint-status |  |  | checkpoint | Test by Pneumatic/Hydrostatic method as per AS3500 & RSG procedure
checkpoint-status |  |  | checkpoint | Test sticker to be adhered to pipe 1500mm above floor level facing a corridor or accessible wall
checkpoint-status |  |  | checkpoint | Test result to be recorded by photo/time/date. (Provide comment if required)
checkpoint-status |  |  | checkpoint | Pipe I.D. labels are installed & spaced compliant with AS3500
checkpoint-status |  |  | checkpoint | Isolation valves closed after testing (If Required)
checklist-flat |  |  | checklist | SD Wastes & Vents (High Level) |  |  |  |  | Yes | SD Wastes & Vents (High Level) | ba380f9c-c35f-4c30-93bc-8b79046ecf57
checkpoint-status |  |  | checkpoint | This installation and following checks are to comply with AS-3500
checkpoint-status |  |  | checkpoint | General visual check for pipe damage, etc
checkpoint-status |  |  | checkpoint | Pipe materials are correct for application
checkpoint-status |  |  | checkpoint | Expansion joints are installed & compliant with AS3500
checkpoint-status |  |  | checkpoint | Ensure expansion joint spacers are removed
checkpoint-status |  |  | checkpoint | Clips are solidly fixed & of correct size/type as per manufactures instructions.
checkpoint-status |  |  | checkpoint | Clips & spacing are installed & compliant with AS3500
checkpoint-status |  |  | checkpoint | Fixture vent, group vent or AAV is installed as per design
checkpoint-status |  |  | checkpoint | Penetrations are installed
checkpoint-status |  |  | checkpoint | Drain penetrations are caulked
checkpoint-status |  |  | checkpoint | Fire collars are installed & registered
checkpoint-status |  |  | checkpoint | Pipe-work is designed, installed & sized as per current IFC documentation
checkpoint-status |  |  | checkpoint | Seal or cap off any open ends if required for security
checkpoint-status |  |  | checkpoint | Check traps are correct locations, finished heights & clear of debris
checkpoint-status |  |  | checkpoint | Rising mains installed & connected if required
checkpoint-status |  |  | checkpoint | Acoustic insulation installed & correct weight as designed
checkpoint-status |  |  | checkpoint | Test by Pneumatic/Hydrostatic method as per AS3500 & RSG procedure
checkpoint-status |  |  | checkpoint | Test result to be recorded by photo/time/date. (Provide comment if required)
checkpoint-status |  |  | checkpoint | Pipe I.D. labels are installed & spaced compliant with AS3500
checklist-flat |  |  | checklist | SW Downpipes/Overflows (Grated Outlets) |  |  |  |  | Yes | SW Downpipes/Overflows (Grated Outlets) | dfbec851-edd4-437e-9d3e-1079b5930691
checkpoint-status |  |  | checkpoint | This installation and following checks are to comply with AS-3500
checkpoint-status |  |  | checkpoint | General visual check for pipe damage, etc
checkpoint-status |  |  | checkpoint | Balcony (BO/OF) grates & bodies are installed in sizes & locations as per design
checkpoint-status |  |  | checkpoint | Trench channels & grates are installed in sizes & locations as per design
checkpoint-status |  |  | checkpoint | Cast-in round/square (RWO/OF) grates & bodies are installed in sizes & locations as per design
checkpoint-status |  |  | checkpoint | Cast-in planter box/tree grates & bodies are installed in sizes & locations as per design
checkpoint-status |  |  | checkpoint | Downpipes are installed
checkpoint-status |  |  | checkpoint | Overflows are installed
checkpoint-status |  |  | checkpoint | Penetrations are installed
checkpoint-status |  |  | checkpoint | Drain penetrations are caulked
checkpoint-status |  |  | checkpoint | Trench channels & grates are installed in sizes & locations as per design
checkpoint-status |  |  | checkpoint | Cast-in round/square grates & bodies are installed in sizes & locations as per design
checkpoint-status |  |  | checkpoint | Cast-in planter box/tree grates & bodies are installed in sizes & locations as per design
checkpoint-status |  |  | checkpoint | Fire collars are installed & registered
checkpoint-status |  |  | checkpoint | Check inside trap for signs of debris etc
checkpoint-status |  |  | checkpoint | Test result to be recorded by photo/time/date. (Provide comment if required)
checklist-flat |  |  | checklist | FO Drinking Fountain |  |  |  |  | Yes | FO Drinking Fountain | 4f556d9c-a9da-417d-bc6a-bc9777700e84
checkpoint-status |  |  | checkpoint | Confirm type supplied & installed as per contract specification
checkpoint-status |  |  | checkpoint | General finish & alignment both level & center of fixture/tapware
checkpoint-status |  |  | checkpoint | Solid installation & mounting of cabinet, sink bowl & mixer
checkpoint-status |  |  | checkpoint | Check in cupboard for signs of leakage
checkpoint-status |  |  | checkpoint | Look for evidence of behind the wall leakage showing on floor
checkpoint-status |  |  | checkpoint | Check mini stops for operation & leaks
checkpoint-status |  |  | checkpoint | Check pressure reduction valve if required.
checkpoint-status |  |  | checkpoint | Check flexible connections for leaks, kinks or twisting
checkpoint-status |  |  | checkpoint | Check trap is installed & nuts are tight
checkpoint-status |  |  | checkpoint | Adjust & throttle water flow-rate if necessary
checkpoint-status |  |  | checkpoint | Check trap & waste pipe connection for signs of leakage
checkpoint-status |  |  | checkpoint | Check inside bowl trap for signs of debris etc
checklist-flat |  |  | checklist | FO Cleaners Sinks |  |  |  |  | Yes | FO Cleaners Sinks | d390ed81-1d9b-4d58-9a60-31f3070cab12
checkpoint-status |  |  | checkpoint | This installation and following checks are to comply with AS-3500
checkpoint-status |  |  | checkpoint | Confirm type supplied & installed as per contract specification
checkpoint-status |  |  | checkpoint | General finish & alignment both level & centre of fixture/tapware
checkpoint-status |  |  | checkpoint | Solid installation & mounting of sink bowl & mixer
checkpoint-status |  |  | checkpoint | Wall brackets are well fitted & secure
checkpoint-status |  |  | checkpoint | Bucket grate is well fitted & secure
checkpoint-status |  |  | checkpoint | Check operation of plug & washer
checkpoint-status |  |  | checkpoint | Check in cupboard for signs of leakage
checkpoint-status |  |  | checkpoint | Check in cupboard for glue, cleaner or pencil marks
checkpoint-status |  |  | checkpoint | Check cover plates are installed
checkpoint-status |  |  | checkpoint | Look for evidence of behind the wall leakage showing on floor
checkpoint-status |  |  | checkpoint | Check trap is installed & nuts are tight
checkpoint-status |  |  | checkpoint | Check trap & waste pipe connection for signs of leakage
checkpoint-status |  |  | checkpoint | Operate mixer & half fill bowl then discharge
checkpoint-status |  |  | checkpoint | Check hot water delivery time & temp against contract doc's
checkpoint-status |  |  | checkpoint | Check inside bowl trap for signs of debris etc
checkpoint-status |  |  | checkpoint | Check caulking is correct
checklist-flat |  |  | checklist | PE Above-Ground Large Hot Water Circulating Pump Package |  |  |  |  | Yes | PE Above-Ground Large Hot Water Circulating Pump Package | ae12eb1e-5bc9-4a19-a388-7e6657b0dfe4
checkpoint-status |  |  | checkpoint | The installer is qualified & trained to carry out the task as assigned
checkpoint-status |  |  | checkpoint | Plant & Equipment installation conforms with current IFC documentation
checkpoint-status |  |  | checkpoint | General finish & alignment both level & finished height are OK
checkpoint-status |  |  | checkpoint | General visual check for damage, etc
checkpoint-status |  |  | checkpoint | Visual check for water & oil leakage
checkpoint-status |  |  | checkpoint | Mountings fixed & torqued down to plinth
checkpoint-status |  |  | checkpoint | Inlet pipework is installed & connected
checkpoint-status |  |  | checkpoint | Outlet pipework is installed & connected
checkpoint-status |  |  | checkpoint | Connection flanges fixed & torqued down to manufacturer specification
checkpoint-status |  |  | checkpoint | Electrolysis prevention in place if required
checkpoint-status |  |  | checkpoint | Electrical cable is installed
checkpoint-status |  |  | checkpoint | Control panel is installed
checkpoint-status |  |  | checkpoint | Electrical Connections to control panel installed by electrician
checkpoint-status |  |  | checkpoint | Electrical Connections is certified by electrician
checkpoint-status |  |  | checkpoint | Pumps cycles set & test run & certified by pump provider
checkpoint-status |  |  | checkpoint | Pressure gauges installed & running within operating limits
checkpoint-status |  |  | checkpoint | Test by Pneumatic/Hydrostatic method as per AS3500 & RSG procedure
checkpoint-status |  |  | checkpoint | Test result to be recorded by photo/time/date. (Provide comment if required)
checklist-flat |  |  | checklist | SW Downpipes/Overflows (High Level) |  |  |  |  | Yes | SW Downpipes/Overflows (High Level) | f0a3c9e2-7cae-442e-a883-4b048bfb125b
checkpoint-status |  |  | checkpoint | This installation and following checks are to comply with AS-3500
checkpoint-status |  |  | checkpoint | General visual check for pipe damage, etc
checkpoint-status |  |  | checkpoint | Pipe materials are correct for application
checkpoint-status |  |  | checkpoint | Downpipes are installed
checkpoint-status |  |  | checkpoint | Overflows are installed
checkpoint-status |  |  | checkpoint | Expansion joints are installed & compliant with AS3500
checkpoint-status |  |  | checkpoint | Ensure expansion joint spacers are removed
checkpoint-status |  |  | checkpoint | Clips are solidly fixed & of correct size/type as per manufactures instructions.
checkpoint-status |  |  | checkpoint | Clips & spacing are installed & compliant with AS3500
checkpoint-status |  |  | checkpoint | Penetrations are installed
checkpoint-status |  |  | checkpoint | Drain penetrations are caulked
checkpoint-status |  |  | checkpoint | Fire collars are installed & registered
checkpoint-status |  |  | checkpoint | Pipe-work is designed, installed & sized as per current IFC documentation
checkpoint-status |  |  | checkpoint | Roof/overflow outlets installed
checkpoint-status |  |  | checkpoint | Seal or cap off any open ends if required for security
checkpoint-status |  |  | checkpoint | Acoustic insulation installed & correct weight as designed
checkpoint-status |  |  | checkpoint | Test by Pneumatic/Hydrostatic method as per AS3500 & RSG procedure
checkpoint-status |  |  | checkpoint | Test result to be recorded by photo/time/date. (Provide comment if required)
checkpoint-status |  |  | checkpoint | Pipe I.D. labels are installed & spaced compliant with AS3500
checklist-flat |  |  | checklist | PE Above-Ground Potable Cold Water Pump Package |  |  |  |  | Yes | PE Above-Ground Potable Cold Water Pump Package | 9393d75e-0cef-4553-8801-9733da25baeb
checkpoint-status |  |  | checkpoint | The installer is qualified & trained to carry out the task as assigned
checkpoint-status |  |  | checkpoint | Plant & Equipment installation conforms with current IFC documentation
checkpoint-status |  |  | checkpoint | General finish & alignment both level & finished height are OK
checkpoint-status |  |  | checkpoint | General visual check for damage, etc
checkpoint-status |  |  | checkpoint | Visual check for water & oil leakage
checkpoint-status |  |  | checkpoint | Mountings fixed & torqued down to plinth
checkpoint-status |  |  | checkpoint | Inlet pipework is installed & connected
checkpoint-status |  |  | checkpoint | Outlet pipework is installed & connected
checkpoint-status |  |  | checkpoint | Connection flanges fixed & torqued down to manufacturer specification
checkpoint-status |  |  | checkpoint | Electrolysis prevention in place if required
checkpoint-status |  |  | checkpoint | Electrical cable is installed
checkpoint-status |  |  | checkpoint | Control panel is installed
checkpoint-status |  |  | checkpoint | Electrical Connections to control panel installed by electrician
checkpoint-status |  |  | checkpoint | Electrical Connections is certified by electrician
checkpoint-status |  |  | checkpoint | Pumps cycles set & test run & certified by pump provider
checkpoint-status |  |  | checkpoint | Pressure gauges installed & running within operating limits
checkpoint-status |  |  | checkpoint | Test by Pneumatic/Hydrostatic method as per AS3500 & RSG procedure
checkpoint-status |  |  | checkpoint | Test result to be recorded by photo/time/date. (Provide comment if required)
folder-progress |  |  | checklist | checklist |  |  |  |  | Yes | New Template | 7e4205bd-022b-4ff1-a42f-81762061ccd4
checklist-flat |  |  | checklist | FO Toilets |  |  |  |  | Yes | FO Toilets | 89c64c54-5351-4ad5-aa9d-e8f630d6bb7a
checkpoint-status |  |  | checkpoint | This installation and following checks are to comply with AS-3500
checkpoint-status |  |  | checkpoint | Confirm type supplied & installed as per contract specification
checkpoint-status |  |  | checkpoint | General finish & alignment both level & centre of fixture/tapware
checkpoint-status |  |  | checkpoint | Solid installation & mounting of pan, seat, cistern & button plate
checkpoint-status |  |  | checkpoint | Check for evidence of leakage
checkpoint-status |  |  | checkpoint | Operate both full & half flush & check for internal overflow
checkpoint-status |  |  | checkpoint | Check inside bowl trap for signs of debris etc
checkpoint-status |  |  | checkpoint | Check caulking is correct
checklist-flat | 5b9c46ca-0a72-52ed-b78e-d48811fffa2f |  | checklist | 10.6 NG Purging of Consumer Fitting Line |  |  |  |  | Yes | 10.6 NG Purging of Consumer Fitting Line | f01e564c-cbb4-4e6e-bb51-224bd292e741
checkpoint-status | 8af0e13b-90f5-5504-b655-c85f5000fa83 |  | checkpoint | Complies with requirements of either AS3500 and AS5600.1
checkpoint-status | ef8c0f79-2654-51bc-b471-2f31066e5278 |  | checkpoint | Complies with the latest IFC specifications & drawings
checkpoint-status | c9313db2-8453-585e-9d7e-d02448dfbe5c |  | checkpoint | A "Tool Box" meeting to be held on the morning of the meter installation date to define personnel rolls & responsibilities
checkpoint-status | 412a3711-8e09-582a-a470-c598f1d90287 |  | checkpoint | Select the purge areas and ensure no ignition sources are within these areas
checkpoint-status | 4320339f-7f94-5aa9-b60a-49aa23ac802c |  | checkpoint | Prominently display warning signs surrounding the purge areas
checkpoint-status | 7435cc54-6f7a-5e5a-b0a3-e131a1df916c |  | checkpoint | A purge stack or purge bucket must be available and operated by one designated team member
checkpoint-status | 945e2499-7705-5e57-9bca-511de7f2d418 |  | checkpoint | Provide suitable fire-extinguishers within the purge venting areas
checkpoint-status | 8ef25338-1978-5e5d-85c3-6fba8b682827 |  | checkpoint | Nitrogen and connection equipment is available for the purge
checkpoint-status | 77bb0430-7762-5766-a92e-e173f38547d9 |  | checkpoint | Ensure personnel are familiar with operation of the fire-extinguishers
checkpoint-status | 082388c1-9070-557f-b00f-970528f05769 |  | checkpoint | All electronic equipment to be used in the purge area must be rated as "electromagnetically safe"
checkpoint-status | 0c5ce92a-ab79-5543-a3c6-951951270a83 |  | checkpoint | The team leader is to remain in the gas meter room to control & oversee proceedings
checkpoint-status | 419a791d-2500-5fc3-ac5e-68182604dc78 |  | checkpoint | Reliable two-way radio devices are to be issued to all personnel as the means of primary communication
checkpoint-status | d4fc0043-c84a-5f02-a646-f530ad5721f2 |  | checkpoint | Hydraulic Services contractor to purge all air from the consumer line using nitrogen until air is displaced with a nitrogen plug
checkpoint-status | a0dae221-f935-5d34-9416-b3412e3ebdfa |  | checkpoint | ESVs' meter contractor is instructed that all is in readiness for the commencement of his works
checkpoint-status | 449b0b12-c0dc-505b-b9de-85d3148a795e |  | checkpoint | ESVs' meter contractor fits the meter in position and immediately commences the purging & calibration of his meter
checkpoint-status | bbf4d352-e46c-54d3-84e6-9c2b61860be3 |  | checkpoint | At this stage only a minor amount of nitrogen gas will be displaced for venting in the purge areas
checkpoint-status | a4e53f09-7996-5c76-b125-bfecab63a387 |  | checkpoint | Following the successful installation & calibration of the meter, the ESV contractors' engagement is complete
checkpoint-status | 679ebc08-52f3-505c-92a2-4731169b87e7 |  | checkpoint | The Hydraulic Services team now takes over and commences the consumer fitting line primary purge
checkpoint-status | 07831ca8-0e84-5d62-86a4-f69251dee84b |  | checkpoint | Calculate the volume of the main run of pipe before commencing the purge (Re: ESV GIS No: 14 - Table 1 and the example in Appendix 2). Observing the volume passing through the meter will indicate when gas is expected to flow through the purge stack or the purge bucket.
checkpoint-status | 64a8081d-4dbe-54ff-a1dc-a3c82a5a489f |  | checkpoint | Note the gas meter test dial position for indication of the flow rate
checkpoint-status | 2f6204b2-1216-56a1-8545-c3e58c7d6d63 |  | checkpoint | A purge stack or purge bucket has previously been connected to the further most point of the consumer fitting line
checkpoint-status | e39a6b09-25f7-575a-9983-2ba238d854af |  | checkpoint | Carefully open the primary gas control valve & commence the purging process
checkpoint-status | c68c8301-1bcd-5e47-8733-6b206d015e60 |  | checkpoint | Ensure the maximum purge pressure is not exceeded (Pressure is labelled on fitting line)
checkpoint-status | 12e59c8f-5b56-5512-8803-e71af19c76b4 |  | checkpoint | Continue to purge through the purge stack or purge bucket until natural gas is commences being presented
checkpoint-status | 4648b181-529a-55eb-8c69-748f39d7f35e |  | checkpoint | Take a sample from the purge stack or purge bucket sampling point using a suitable gas detector (minimum acceptable reading 95% gas).
checkpoint-status | aeeab83a-7922-52be-bd53-1fcd15f14714 |  | checkpoint | An indication that the purging of natural gas is nearing completion is seen when mass gas aeration evacuates from the purge bucket and proceeds to disperses.
checkpoint-status | a11e8098-4575-508a-b28b-7cefefcc0297 |  | checkpoint | Continue purging & testing until an acceptable reading on the gas detector is obtained
checkpoint-status | 3722a6ad-d65c-5556-ac0d-7520ab8bf874 |  | checkpoint | When the correct test result is obtained, purging of this section will be complete.
checkpoint-status | 96632510-a54d-5574-bbe5-9bbb6c7f8076 |  | checkpoint | Relieve the pressure in the purge hose by opening the purge stack main valve.
checkpoint-status | 711a0f1f-8b2a-51d8-863f-742ddef5e5f9 |  | checkpoint | Disconnect the purge hose and the hose inlet valve from the installation. Cap & seal the fitting line immediately to avoid gas escaping and air re-entering the line.
checkpoint-status | 83c2e693-8169-53c1-a1c7-80d77f756fce |  | checkpoint | Transfer the purge stack or purge bucket and hose to the end of the branch nearest the meter and repeat the procedure.
checkpoint-status | dac4032f-6feb-5f4e-91cd-f2f4fd9deeb1 |  | checkpoint | Continue purging all branches, moving away from the meter, until the whole installation is filled with gas.
checklist-flat |  |  | checklist | NG Risers |  |  |  |  | Yes | NG Risers | 8a04da8b-68ff-4c67-aff3-e470009a0a23
checkpoint-status |  |  | checkpoint | This installation and following checks are to comply with AS-5601
checkpoint-status |  |  | checkpoint | Authority applications are completed for work to commence
checkpoint-status |  |  | checkpoint | General visual check for pipe damage/leaks, etc
checkpoint-status |  |  | checkpoint | Penetrations are installed
checkpoint-status |  |  | checkpoint | Pipe materials are correct for application
checkpoint-status |  |  | checkpoint | Pipe-work is designed, installed & sized as per current IFC documentation
checkpoint-status |  |  | checkpoint | Check all valves &/or meter assemblies conform with current documentation
checkpoint-status |  |  | checkpoint | Ensure all risers are installed professionally with no abnormalities
checkpoint-status |  |  | checkpoint | Roll Groove joints are torqued down to manufacturers Instructions
checkpoint-status |  |  | checkpoint | Welded pipe joints are completed
checkpoint-status |  |  | checkpoint | CU pressed pipe joints crimped & witness marked as per manufacturers instructions
checkpoint-status |  |  | checkpoint | XLPE pipe joints are correctly crimped & witness marked as per manufacturers instructions
checkpoint-status |  |  | checkpoint | Pipe penetrations are caulked
checkpoint-status |  |  | checkpoint | Anchors are installed as per manufacturer instructions & compliant with AS3500
checkpoint-status |  |  | checkpoint | Clips are solidly fixed & of correct size/type as per manufactures instructions.
checkpoint-status |  |  | checkpoint | Clips & spacing are installed & compliant with AS3500
checkpoint-status |  |  | checkpoint | Expansion device or loop is correctly sized & installed conforming with AS3500
checkpoint-status |  |  | checkpoint | Isolation valves are installed & flow correct
checkpoint-status |  |  | checkpoint | Test by Pneumatic/Hydrostatic method as per AS3500 & RSG procedure
checkpoint-status |  |  | checkpoint | Test sticker to be adhered to pipe 1500mm above floor level facing a corridor or accessible wall
checkpoint-status |  |  | checkpoint | Test result to be recorded by photo/time/date. (Provide comment if required)
checkpoint-status |  |  | checkpoint | Pipe I.D. labels are installed & spaced compliant with AS3500
checkpoint-status |  |  | checkpoint | Isolation valves closed after testing (If Required)
checklist-flat |  |  | checklist | HW Rough-in (High Level) |  |  |  |  | Yes | HW Rough-in (High Level) | 3e6050e8-1928-4ce1-b743-8480198faa86
checkpoint-status |  |  | checkpoint | This installation and following checks are to comply with AS-3500
checkpoint-status |  |  | checkpoint | Check general visual check for pipe damage/leaks, etc
checkpoint-status |  |  | checkpoint | Pipe materials are correct for application
checkpoint-status |  |  | checkpoint | Check silicone applied to studs
checkpoint-status |  |  | checkpoint | Check TCV/TMV correct location & securely clipped
checkpoint-status |  |  | checkpoint | Check all valves &/or meter assemblies conform with current documentation
checkpoint-status |  |  | checkpoint | Check for possible cross connections
checkpoint-status |  |  | checkpoint | Check all crimped joints & witness marks
checkpoint-status |  |  | checkpoint | Check clip spacing are correct at ≤600mm
checkpoint-status |  |  | checkpoint | Heat trace installed if required
checkpoint-status |  |  | checkpoint | Thermal insulation installed & correct weight as designed
checkpoint-status |  |  | checkpoint | Test by Pneumatic/Hydrostatic method as per AS3500 & RSG procedure
checkpoint-status |  |  | checkpoint | Test result to be recorded by photo/time/date. (Provide comment if required)
checkpoint-status |  |  | checkpoint | Pipe I.D. labels are installed & spaced compliant with AS3500
checkpoint-status |  |  | checkpoint | Seal or cap off any open ends if required for security
checkpoint-status |  |  | checkpoint | Isolation valves closed after testing (If Required)
checklist-flat |  |  | checklist | WW TMV/TCV Rough-in |  |  |  |  | Yes | WW TMV/TCV Rough-in | d34226ae-cd01-4102-85d7-34831b844a6c
checkpoint-status |  |  | checkpoint | Confirm type supplied & installed as per contract specification
checkpoint-status |  |  | checkpoint | General finish & alignment both level & center of fixture/tapware
checkpoint-status |  |  | checkpoint | Check general visual check for pipe damage/leaks, etc
checkpoint-status |  |  | checkpoint | Check silicone applied to studs
checkpoint-status |  |  | checkpoint | Wall box is installed if required
checkpoint-status |  |  | checkpoint | Check TCV/TMV correct location & securely clipped
checkpoint-status |  |  | checkpoint | Check for possible cross connections
checkpoint-status |  |  | checkpoint | Check all crimped joints & witness marks
checkpoint-status |  |  | checkpoint | Test result is compliant with AS3500 (Record test by photo & time/date)
checkpoint-status |  |  | checkpoint | Pipe I.D. labels are installed & spaced compliant with AS3500
checkpoint-status |  |  | checkpoint | Seal or cap off any open ends if required for security
checklist-flat |  |  | checklist | RW Rough-in (High Level) |  |  |  |  | Yes | RW Rough-in (High Level) | a81c81df-fa1d-4681-8fae-c011c717cf83
checkpoint-status |  |  | checkpoint | This installation and following checks are to comply with AS-3500
checkpoint-status |  |  | checkpoint | Check general visual check for pipe damage/leaks, etc
checkpoint-status |  |  | checkpoint | Pipe materials are correct for application
checkpoint-status |  |  | checkpoint | Check all valves &/or meter assemblies conform with current documentation
checkpoint-status |  |  | checkpoint | Check silicone applied to studs
checkpoint-status |  |  | checkpoint | Check for possible cross connections
checkpoint-status |  |  | checkpoint | Check all crimped joints & witness marks
checkpoint-status |  |  | checkpoint | Check clip spacing are correct at ≤600mm
checkpoint-status |  |  | checkpoint | Test by Pneumatic/Hydrostatic method as per AS3500 & RSG procedure
checkpoint-status |  |  | checkpoint | Test result to be recorded by photo/time/date. (Provide comment if required)
checkpoint-status |  |  | checkpoint | Pipe I.D. labels are installed & spaced compliant with AS3500
checkpoint-status |  |  | checkpoint | Seal or cap off any open ends if required for security
checkpoint-status |  |  | checkpoint | Isolation valves closed after testing (If Required)
checklist-flat |  |  | checklist | RW Risers (Pumped or Mains Pressure Risers) |  |  |  |  | Yes | RW Risers (Pumped or Mains Pressure Risers) | 1c505ed1-5389-4222-b3b5-f6193e330b40
checkpoint-status |  |  | checkpoint | This installation and following checks are to comply with AS-3500
checkpoint-status |  |  | checkpoint | General visual check for pipe damage/leaks, etc
checkpoint-status |  |  | checkpoint | Penetrations are installed
checkpoint-status |  |  | checkpoint | Pipe materials are correct for application
checkpoint-status |  |  | checkpoint | Pipe-work is designed, installed & sized as per current IFC documentation
checkpoint-status |  |  | checkpoint | Check all valves &/or meter assemblies conform with current documentation
checkpoint-status |  |  | checkpoint | Ensure all risers are installed professionally with no abnormalities
checkpoint-status |  |  | checkpoint | Roll Groove joints are torqued down to manufacturers Instructions
checkpoint-status |  |  | checkpoint | Welded pipe joints are completed
checkpoint-status |  |  | checkpoint | CU pressed pipe joints crimped & witness marked as per manufacturers instructions
checkpoint-status |  |  | checkpoint | XLPE pipe joints are correctly crimped & witness marked as per manufacturers instructions
checkpoint-status |  |  | checkpoint | Pipe penetrations are caulked
checkpoint-status |  |  | checkpoint | Anchors are installed as per manufacturer instructions & compliant with AS3500
checkpoint-status |  |  | checkpoint | Clips are solidly fixed & of correct size/type as per manufactures instructions.
checkpoint-status |  |  | checkpoint | Clips & spacing are installed & compliant with AS3500
checkpoint-status |  |  | checkpoint | Expansion device or loop is correctly sized & installed conforming with AS3500
checkpoint-status |  |  | checkpoint | Isolation valves are installed & flow correct
checkpoint-status |  |  | checkpoint | Test by Pneumatic/Hydrostatic method as per AS3500 & RSG procedure
checkpoint-status |  |  | checkpoint | Test sticker to be adhered to pipe 1500mm above floor level facing a corridor or accessible wall
checkpoint-status |  |  | checkpoint | Test result to be recorded by photo/time/date. (Provide comment if required)
checkpoint-status |  |  | checkpoint | Pipe I.D. labels are installed & spaced compliant with AS3500
checkpoint-status |  |  | checkpoint | Isolation valves closed after testing (If Required)
checklist-flat |  |  | checklist | MT Natural Gas Meters |  |  |  |  | Yes | MT Natural Gas Meters | a64b4c3a-6124-42d8-81e7-00793d158931
checkpoint-status |  |  | checkpoint | This installation and following checks are to comply with AS-5601
checkpoint-status |  |  | checkpoint | Natural Gas Meter Details:
text | 6d197827-5659-44b1-980e-e4858a14e405 |  | textbox | Meter No:
text | f9aec612-5858-4fa6-9187-0fbf8e05eb37 |  | textbox | Meter Location:
text | a779d268-7fae-4f66-82da-f5b0320da5c0 |  | textbox | Meter Size:
checkpoint-status |  |  | checkpoint | General visual check for pipe damage/leaks, etc
checkpoint-status |  |  | checkpoint | Meter installed & sized as per current documentation
checkpoint-status |  |  | checkpoint | Meter bracketed
checkpoint-status |  |  | checkpoint | Analogue meter display is facing upright
checkpoint-status |  |  | checkpoint | Confirm I.D. point against the meter register
checkpoint-status |  |  | checkpoint | Pulse rate value is correct
checkpoint-status |  |  | checkpoint | Pulse rate is output is manually proved
checkpoint-status |  |  | checkpoint | BMS wiring connected by mechanical contractor
checkpoint-status |  |  | checkpoint | Flow direction is correct
checkpoint-status |  |  | checkpoint | Pipe I.D. labels are installed & spaced compliant with AS3500
checkpoint-status |  |  | checkpoint | Test result to be recorded by photo/time/date. (Provide comment if required)
checkpoint-status |  |  | checkpoint | Isolation valves closed after testing (If Required)
checklist-flat |  |  | checklist | HW Hot Water Meters |  |  |  |  | Yes | HW Hot Water Meters | 3e9b41c2-230b-4a09-a97c-a6d5bb72d744
checkpoint-no-status |  |  | checkpoint | Water Meter Details:
text | 97816d5b-280d-48a4-bd11-8e753dbec92f |  | textbox | Meter No:
text | cbec50ec-00f9-42bf-8e8f-2f676226b9aa |  | textbox | Level:
text | d4e4b007-6092-4d64-861d-cc81d34d230d |  | textbox | Meter Size:
checkpoint-status |  |  | checkpoint | General visual check for pipe damage/leaks, etc
checkpoint-status |  |  | checkpoint | Meter installed & sized as per current documentation
checkpoint-status |  |  | checkpoint | Meter bracketed
checkpoint-status |  |  | checkpoint | Analogue meter display is facing upright
checkpoint-status |  |  | checkpoint | Confirm I.D. point against the meter register
checkpoint-status |  |  | checkpoint | Pulse rate value is correct
checkpoint-status |  |  | checkpoint | Pulse rate is output is manually proved
checkpoint-status |  |  | checkpoint | BMS wiring connected by mechanical contractor
checkpoint-status |  |  | checkpoint | Flow direction is correct
checkpoint-status |  |  | checkpoint | Pipe I.D. labels are installed & spaced compliant with AS3500
checkpoint-status |  |  | checkpoint | Record installation by photo & time/date
checkpoint-status |  |  | checkpoint | Isolation valves closed after testing (If Required)
checklist-flat |  |  | checklist | PE In-Ground Stormwater Pump Station |  |  |  |  | Yes | PE In-Ground Stormwater Pump Station | 54d86ebc-098a-4441-b4c6-e51108d5bed8
checkpoint-status |  |  | checkpoint | The installer is qualified & trained to carry out the task as assigned
checkpoint-status |  |  | checkpoint | Plant & Equipment installation conforms with current IFC documentation
checkpoint-status |  |  | checkpoint | General finish & alignment both level & finished height are OK
checkpoint-status |  |  | checkpoint | General visual check for damage, etc
checkpoint-status |  |  | checkpoint | Finished R.L. are correct & verified
checkpoint-status |  |  | checkpoint | Vents are installed if required
checkpoint-status |  |  | checkpoint | Backfill is specified materials & compacted to test OK
checkpoint-status |  |  | checkpoint | Spoil is removed
checkpoint-status |  |  | checkpoint | Inlet drain is installed & connected
checkpoint-status |  |  | checkpoint | Outlet rising mains installed & connected
checkpoint-status |  |  | checkpoint | Electrical conduit is installed
checkpoint-status |  |  | checkpoint | Electrical cable is installed
checkpoint-status |  |  | checkpoint | Control panel is installed
checkpoint-status |  |  | checkpoint | Electrical Connections to control panel installed by electrician
checkpoint-status |  |  | checkpoint | Electrical Connections is certified by electrician
checkpoint-status |  |  | checkpoint | Pumps cycles set & test run & certified by pump provider
checkpoint-status |  |  | checkpoint | Test by Pneumatic/Hydrostatic method as per AS3500 & RSG procedure
checkpoint-status |  |  | checkpoint | Test result to be recorded by photo/time/date. (Provide comment if required)
checklist-flat |  |  | checklist | MT Hot Water Meters |  |  |  |  | Yes | MT Hot Water Meters | c7726d65-11d0-471d-b8c4-be4c58922597
checkpoint-status |  |  | checkpoint | This installation and following checks are to comply with AS-3500
checkpoint-status |  |  | checkpoint | Water Meter Details:
text | 3813a42e-01ae-454f-a7d4-e00fba1d0045 |  | textbox | Meter No:
text | c81e2114-fba7-4907-aa62-2b5df83b0f08 |  | textbox | Meter Location:
text | 40f7ac8c-9d51-406d-8ad4-e78393048108 |  | textbox | Meter Size:
checkpoint-status |  |  | checkpoint | General visual check for pipe damage/leaks, etc
checkpoint-status |  |  | checkpoint | Meter installed & sized as per current documentation
checkpoint-status |  |  | checkpoint | Meter bracketed
checkpoint-status |  |  | checkpoint | Analogue meter display is facing upright
checkpoint-status |  |  | checkpoint | Confirm I.D. point against the meter register
checkpoint-status |  |  | checkpoint | Pulse rate value is correct
checkpoint-status |  |  | checkpoint | Pulse rate is output is manually proved
checkpoint-status |  |  | checkpoint | BMS wiring connected by mechanical contractor
checkpoint-status |  |  | checkpoint | Flow direction is correct
checkpoint-status |  |  | checkpoint | Pipe I.D. labels are installed & spaced compliant with AS3500
checkpoint-status |  |  | checkpoint | Test result to be recorded by photo/time/date. (Provide comment if required)
checkpoint-status |  |  | checkpoint | Isolation valves closed after testing (If Required)
checklist-flat |  |  | checklist | TST Testing Natural Gas Service (Nitrogen/Air Test) High Pressure |  |  |  |  | Yes | TST Testing Natural Gas Service (Nitrogen/Air Test) High Pressure | afdb7fd0-bcdf-49d4-b4ce-60724565d498
checkpoint-status |  |  | checkpoint | This testing procedure conforms with that as set out in AS-5601.1 (2013)
checkpoint-status |  |  | checkpoint | Ensure all valves dedicated to isolating the test zone are securely shut off & tagged
checkpoint-status |  |  | checkpoint | Nominate an air purging valve point
checkpoint-status |  |  | checkpoint | Nominate a pressure testing valve point
checkpoint-status |  |  | checkpoint | Ensure isolating valves within the test zone are open as required
checkpoint-status |  |  | checkpoint | Ensure all terminal open ends i.e. lugged elbows, etc are securely capped off
checkpoint-status |  |  | checkpoint | Slowly open test feeder valve & fill the test zone with nitrogen/air until completely purged
checkpoint-status |  |  | checkpoint | Connect pressure testing device to the nominated test point
checkpoint-status |  |  | checkpoint | Shut off the gas feeder valve
checkpoint-status |  |  | checkpoint | Commence testing by slowly increasing pressure up to 1.5 kPa above working pressure
checkpoint-status |  |  | checkpoint | Testing is deemed successful if the pressure remains unchanged for 5 mins of every 30 litres volume of pipe
checkpoint-status |  |  | checkpoint | If test is successful, slowly release test pressure and return the system back to neutral conditions
checkpoint-status |  |  | checkpoint | Test sticker in visible location
checkpoint-status |  |  | checkpoint | Test result recorded by photo/time/date
checkpoint-status |  |  | checkpoint | Test route/location attached to this Check Point as PDF plan or snap shot with its unique I.D. number.
checkpoint-status |  |  | checkpoint | Failures are to be immediately reported to management for analysis & repatriation
checklist-flat |  |  | checklist | RW High Level/Corridors |  |  |  |  | Yes | RW High Level/Corridors | 1f27557f-b6f6-40e3-a796-0c96b1e91ab3
checkpoint-status |  |  | checkpoint | This installation and following checks are to comply with AS-3500
checkpoint-status |  |  | checkpoint | General visual check for pipe damage/leaks, etc
checkpoint-status |  |  | checkpoint | Pipe materials are correct for application
checkpoint-status |  |  | checkpoint | Pipe-work is designed, installed & sized as per current IFC documentation
checkpoint-status |  |  | checkpoint | Check all valves &/or meter assemblies conform with current documentation
checkpoint-status |  |  | checkpoint | Roll Groove joints are torqued down to manufacturers Instructions
checkpoint-status |  |  | checkpoint | Welded pipe joints are completed
checkpoint-status |  |  | checkpoint | CU pressed pipe joints crimped & witness marked as per manufacturers instructions
checkpoint-status |  |  | checkpoint | XLPE pipe joints are correctly crimped & witness marked as per manufacturers instructions
checkpoint-status |  |  | checkpoint | Meter manifolds & frames are firmly bracketed & installed in sizes, quantities & locations as per design
checkpoint-status |  |  | checkpoint | PR valves are installed. Pressure rate & flow correct
checkpoint-status |  |  | checkpoint | Isolation valves are installed & flow correct
checkpoint-status |  |  | checkpoint | Clips are solidly fixed & of correct size/type as per manufactures instructions.
checkpoint-status |  |  | checkpoint | Clips & spacing are installed & compliant with AS3500
checkpoint-status |  |  | checkpoint | Expansion device or loop is correctly sized & installed conforming with AS3500
checkpoint-status |  |  | checkpoint | Test by Pneumatic/Hydrostatic method as per AS3500 & RSG procedure
checkpoint-status |  |  | checkpoint | Test result to be recorded by photo/time/date. (Provide comment if required)
checkpoint-status |  |  | checkpoint | Pipe I.D. labels are installed & spaced compliant with AS3500
checkpoint-status |  |  | checkpoint | Isolation valves closed after testing (If Required)
checklist-flat |  |  | checklist | Incomplete or Delayed Works |  |  |  |  | Yes | Incomplete or Delayed Works | 04bc13f6-0bba-4f00-8547-00f5a7e20d14
checkpoint-no-status |  |  | checkpoint | Incomplete or Delayed Works Details:
text | cdebe66d-42f4-4af7-acc5-d4bed6d0d5ae |  | textbox | Detail:
checklist-flat |  |  | checklist | PE SW Downpipe/Syphonic Diversion Valve |  |  |  |  | Yes | PE SW Downpipe/Syphonic Diversion Valve | e96aa901-83a8-485c-90e9-6211f3d5e981
checkpoint-status |  |  | checkpoint | The installer is qualified & trained to carry out the task as assigned
checkpoint-status |  |  | checkpoint | Plant & Equipment installation conforms with current IFC documentation
checkpoint-status |  |  | checkpoint | General finish & alignment both level & finished height are OK
checkpoint-status |  |  | checkpoint | General visual check for damage, etc
checkpoint-status |  |  | checkpoint | Visual check for water & oil leakage
checkpoint-status |  |  | checkpoint | Mountings fixed & torqued down to plinth
checkpoint-status |  |  | checkpoint | Inlet pipework is installed & connected as per design
checkpoint-status |  |  | checkpoint | Outlet pipework is installed & connected as per design
checkpoint-status |  |  | checkpoint | Diversion pipework is installed & connected as per design
checkpoint-status |  |  | checkpoint | Connection flanges fixed to manufacturer specification
checkpoint-status |  |  | checkpoint | Ensure data wiring is connected between control panels & operating to the manufacturers specification
checkpoint-status |  |  | checkpoint | Ensure electrical connection have been completed & certified by a licenced electrician
checkpoint-status |  |  | checkpoint | Ensure the pnuematic pump is installed & operates to the manufacturers specification
checkpoint-status |  |  | checkpoint | Provider to check the valve actuates correctly & test cycles the valve several times
checkpoint-status |  |  | checkpoint | Test by Pneumatic/Hydrostatic method as per AS3500 & RSG procedure
checkpoint-status |  |  | checkpoint | Test result to be recorded by photo/time/date. (Provide comment if required)
checklist-flat |  |  | checklist | FO Clothes Washing Machine Stops |  |  |  |  | Yes | FO Clothes Washing Machine Stops | 80b5bbdb-0b2b-4033-8f04-fce702403918
checkpoint-status |  |  | checkpoint | This installation and following checks are to comply with AS-3500
checkpoint-status |  |  | checkpoint | Confirm type supplied & installed as per contract specification
checkpoint-status |  |  | checkpoint | General finish & alignment both level & centre of tapware
checkpoint-status |  |  | checkpoint | Check flood stoppers
checkpoint-status |  |  | checkpoint | Solid installation & mounting of tapware
checkpoint-status |  |  | checkpoint | Check cover plates are installed
checkpoint-status |  |  | checkpoint | Look for evidence of behind the wall leakage showing on floor
checkpoint-status |  |  | checkpoint | Seal or cap off any open ends if required for security
checklist-flat |  |  | checklist | PE Above-Ground Rain Water Storage Tank |  |  |  |  | Yes | PE Above-Ground Rain Water Storage Tank | b71d425f-8ca1-4b42-b7a0-97ff95cd8236
checkpoint-status |  |  | checkpoint | The installer is qualified & trained to carry out the task as assigned
checkpoint-status |  |  | checkpoint | Plant & Equipment installation conforms with current IFC documentation
checkpoint-status |  |  | checkpoint | General finish & alignment both level & finished height are OK
checkpoint-status |  |  | checkpoint | General visual check for damage, etc
checkpoint-status |  |  | checkpoint | Finished R.L. are correct & verified
checkpoint-status |  |  | checkpoint | Vents are installed if required
checkpoint-status |  |  | checkpoint | Inlet drain is installed & connected
checkpoint-status |  |  | checkpoint | Outlet drain is installed & connected
checkpoint-status |  |  | checkpoint | Overflow drain is installed to discharge over stormwater pit
checkpoint-status |  |  | checkpoint | Isolation valves are installed (if required)
checkpoint-status |  |  | checkpoint | Suction line installed & connected
checkpoint-status |  |  | checkpoint | Isolation valves are installed (if required)
checkpoint-status |  |  | checkpoint | Electrical cable is installed
checkpoint-status |  |  | checkpoint | Control panel is installed
checkpoint-status |  |  | checkpoint | Electrical Connections to control panel installed by electrician
checkpoint-status |  |  | checkpoint | Electrical Connections is certified by electrician
checkpoint-status |  |  | checkpoint | Tank provider installation certification obtained
checkpoint-status |  |  | checkpoint | Test by Pneumatic/Hydrostatic method as per AS3500 & RSG procedure
checkpoint-status |  |  | checkpoint | Test result to be recorded by photo/time/date. (Provide comment if required)
checkpoint-status |  |  | checkpoint | Pipe I.D. labels are installed & spaced compliant with AS3500
checklist-flat |  |  | checklist | CW Cold Water Meters |  |  |  |  | Yes | CW Cold Water Meters | 97e13576-e2b4-4744-89f1-d188b4806067
checkpoint-no-status |  |  | checkpoint | Water Meter Details:
text | cb3739dc-8d66-42ef-bc29-66b15eb65985 |  | textbox | Meter No:
text | d66d0a69-cd5a-4a57-9999-9ee14fb56837 |  | textbox | Level:
text | 635c0e8c-7b2e-4cca-91dd-e9b5bc1756e3 |  | textbox | Meter Size:
checkpoint-status |  |  | checkpoint | General visual check for pipe damage/leaks, etc
checkpoint-status |  |  | checkpoint | Meter installed & sized as per current documentation
checkpoint-status |  |  | checkpoint | Meter bracketed
checkpoint-status |  |  | checkpoint | Analogue meter display is facing upright
checkpoint-status |  |  | checkpoint | Confirm I.D. point against the meter register
checkpoint-status |  |  | checkpoint | Pulse rate value is correct
checkpoint-status |  |  | checkpoint | Pulse rate is output is manually proved
checkpoint-status |  |  | checkpoint | BMS wiring connected by mechanical contractor
checkpoint-status |  |  | checkpoint | Flow direction is correct
checkpoint-status |  |  | checkpoint | Pipe I.D. labels are installed & spaced compliant with AS3500
checkpoint-status |  |  | checkpoint | Record installation by photo & time/date
checkpoint-status |  |  | checkpoint | Isolation valves closed after testing (If Required)
checklist-flat |  |  | checklist | CW Reduced Pressure Zone Device(RPZD) Rough-in |  |  |  |  | Yes | CW Reduced Pressure Zone Device(RPZD) Rough-in | 6d76655e-95ef-4ac5-a1cb-d343b0fe0322
checkpoint-status |  |  | checkpoint | Confirm type supplied & installed as per contract specification
checkpoint-status |  |  | checkpoint | General finish & alignment both level & center of valve assembly
checkpoint-status |  |  | checkpoint | Check general visual check for pipe damage/leaks, etc
checkpoint-status |  |  | checkpoint | Check silicone applied to studs
checkpoint-status |  |  | checkpoint | Wall box is installed if required
checkpoint-status |  |  | checkpoint | Check RPZD correct location
checkpoint-status |  |  | checkpoint | Check all crimped joints & witness marks
checkpoint-status |  |  | checkpoint | Flow direction is correct
checkpoint-status |  |  | checkpoint | Test result is compliant with AS3500 (Record test by photo & time/date)
checkpoint-status |  |  | checkpoint | Pipe I.D. labels are installed & spaced compliant with AS3500
checkpoint-status |  |  | checkpoint | Isolation valves closed after testing (If Required)
checklist-flat |  |  | checklist | CW High Level/Corridors |  |  |  |  | Yes | CW High Level/Corridors | b6f67c40-b22b-4198-b02a-37e2486bf95a
checkpoint-status |  |  | checkpoint | This installation and following checks are to comply with AS-3500
checkpoint-status |  |  | checkpoint | General visual check for pipe damage/leaks, etc
checkpoint-status |  |  | checkpoint | Pipe materials are correct for application
checkpoint-status |  |  | checkpoint | Pipe-work is designed, installed & sized as per current IFC documentation
checkpoint-status |  |  | checkpoint | Check all valves &/or meter assemblies conform with current documentation
checkpoint-status |  |  | checkpoint | Roll Groove joints are torqued down to manufacturers Instructions
checkpoint-status |  |  | checkpoint | Welded pipe joints are completed
checkpoint-status |  |  | checkpoint | CU pressed pipe joints crimped & witness marked as per manufacturers instructions
checkpoint-status |  |  | checkpoint | XLPE pipe joints are correctly crimped & witness marked as per manufacturers instructions
checkpoint-status |  |  | checkpoint | Meter manifolds & frames are firmly bracketed & installed in sizes, quantities & locations as per design
checkpoint-status |  |  | checkpoint | PR valves are installed. Pressure rate & flow correct
checkpoint-status |  |  | checkpoint | Isolation valves are installed & flow correct
checkpoint-status |  |  | checkpoint | Clips are solidly fixed & of correct size/type as per manufactures instructions.
checkpoint-status |  |  | checkpoint | Clips & spacing are installed & compliant with AS3500
checkpoint-status |  |  | checkpoint | Expansion device or loop is correctly sized & installed conforming with AS3500
checkpoint-status |  |  | checkpoint | Test by Pneumatic/Hydrostatic method as per AS3500 & RSG procedure
checkpoint-status |  |  | checkpoint | Test result to be recorded by photo/time/date. (Provide comment if required)
checkpoint-status |  |  | checkpoint | Pipe I.D. labels are installed & spaced compliant with AS3500
checkpoint-status |  |  | checkpoint | Isolation valves closed after testing (If Required)
checklist-flat |  |  | checklist | FO Gas Appliances |  |  |  |  | Yes | FO Gas Appliances | 02c197c8-8c37-427e-90fb-155981ffabda
checkpoint-status |  |  | checkpoint | This installation and following checks are to comply with AS-5601
checkpoint-status |  |  | checkpoint | Confirm type supplied & installed as per contract specification
checkpoint-status |  |  | checkpoint | General finish & alignment both level & centre of cook top
checkpoint-status |  |  | checkpoint | Ensure wall & surrounding joinery material is fire rated & compliant with AS-5601
checkpoint-status |  |  | checkpoint | Solid installation & mounting of cook top
checkpoint-status |  |  | checkpoint | Check in cupboard for signs of gas leakage
checkpoint-status |  |  | checkpoint | Check in cupboard for glue, cleaner or pencil marks
checkpoint-status |  |  | checkpoint | Check cover plates are installed
checkpoint-status |  |  | checkpoint | Check gas valve for operation & leaks
checkpoint-status |  |  | checkpoint | Check gas regulator for operation & leaks
checkpoint-status |  |  | checkpoint | Check flexible connections for leaks, kinks or twisting
checkpoint-status |  |  | checkpoint | Test operation of all burners from low to full to off
checkpoint-status |  |  | checkpoint | Test flame for complete combustion
checkpoint-status |  |  | checkpoint | Range hood height is compliant with manufacturer recommendation
checkpoint-status |  |  | checkpoint | Test sticker to be adhered to pipe inside cabinet in a visible position
checkpoint-status |  |  | checkpoint | Check caulking is correct
checklist-flat |  |  | checklist | Modular Bathroom (Pod Unit) Connections |  |  |  |  | Yes | Modular Bathroom (Pod Unit) Connections | 72639cd3-d537-483b-8411-7e2525de0354
checkpoint-status |  |  | checkpoint | Confirm Pod Unit supplied & installed as per contract specification
checkpoint-status |  |  | checkpoint | General finish & alignment of Pod unit is level & centred
checkpoint-status |  |  | checkpoint | Check condition of all Pod Unit fixtures/tapware
checkpoint-status |  |  | checkpoint | Check that the Pod Unit sewer drainage is connected to the building system
checkpoint-status |  |  | checkpoint | Check that the sewer pipe-work is acoustically lagged as required
checkpoint-status |  |  | checkpoint | Check that the Pod Unit cold-water pipework is connected to the building system
checkpoint-status |  |  | checkpoint | Check that the Pod Unit hot-water pipework is connected to the building system
checkpoint-status |  |  | checkpoint | Check that the hot-water pipe-work is thermally lagged as required
checkpoint-status |  |  | checkpoint | Check the Pod Unit is provided with an in-built Temp Valve or Thermo Mixing Valve
checkpoint-status |  |  | checkpoint | Check in cupboard for signs of leakage
checkpoint-status |  |  | checkpoint | Look for evidence of behind the wall leakage showing on floor
checkpoint-status |  |  | checkpoint | Check hot water delivery time & temp against contract doc's
checkpoint-status |  |  | checkpoint | Check inside bowl trap for signs of debris etc
checkpoint-status |  |  | checkpoint | Check hot water delivery time & temp against contract doc's
checkpoint-status |  |  | checkpoint | Temperature test warm water to ≤ 50°C
checkpoint-status |  |  | checkpoint | Temperature test warm water to ≤ 43°C if Pod Unit is DDA compliant
checkpoint-status |  |  | checkpoint | Test result is compliant with AS3500 (Record test by photo & time/date)
checkpoint-status |  |  | checkpoint | Valve is securely turned off (if required)
checklist-flat |  |  | checklist | FO Showers |  |  |  |  | Yes | FO Showers | b29fbc4b-9527-4da8-85ef-12ee8959171c
checkpoint-status |  |  | checkpoint | This installation and following checks are to comply with AS-3500
checkpoint-status |  |  | checkpoint | Confirm type supplied & installed as per contract specification
checkpoint-status |  |  | checkpoint | General finish & alignment both level & centre of fixture/tapware
checkpoint-status |  |  | checkpoint | Solid installation of wall mounting plates, levers, wall rails & sprays
checkpoint-status |  |  | checkpoint | Check floor grate or channel for flush fit & alignment
checkpoint-status |  |  | checkpoint | Check for flexible hose leakage
checkpoint-status |  |  | checkpoint | Check hot water delivery time & temp against contract doc's
checkpoint-status |  |  | checkpoint | Check inside floor waste for signs of debris etc
checkpoint-status |  |  | checkpoint | Operate mixer & discharge to floor waste
checklist-flat |  |  | checklist | FO Thermostatic Mixing Valve (TMV's) |  |  |  |  | Yes | FO Thermostatic Mixing Valve (TMV's) | cd9dcf29-f711-4e52-ac4d-11f346305bb4
checkpoint-status |  |  | checkpoint | This installation and following checks are to comply with AS-3500
checkpoint-status |  |  | checkpoint | Confirm type supplied & installed as per contract specification
checkpoint-status |  |  | checkpoint | General finish & alignment both level & centre of tapware
checkpoint-status |  |  | checkpoint | Solid installation & mounting of tapware
checkpoint-status |  |  | checkpoint | Check cover plates are installed
checkpoint-status |  |  | checkpoint | Look for evidence of behind the wall leakage showing on floor
checkpoint-status |  |  | checkpoint | Valve tag or signage is installed if required.
checkpoint-status |  |  | checkpoint | Check hot water delivery time & temp against contract doc's
checkpoint-status |  |  | checkpoint | Temperature test warm water to ≤ 43°C
checkpoint-status |  |  | checkpoint | Test result to be recorded by photo/time/date. (Provide comment if required)
checkpoint-status |  |  | checkpoint | Seal or cap off any open ends if required for security
checkpoint-status |  |  | checkpoint | Test sticker to be adhered to pipe inside wall box or in a visible position
checkpoint-status |  |  | checkpoint | Valve is securely turned off (if required)
checklist-flat |  |  | checklist | FC Floor/Wall Penetrations |  |  |  |  | Yes | FC Floor/Wall Penetrations | 5e440a5d-d7e6-497b-ae5b-030679fe141b
checkpoint-status |  |  | checkpoint | The installer is qualified & trained to carry out the task as assigned
checkpoint-status |  |  | checkpoint | Confirm all penetrations locations are as per current IFC documentation
checkpoint-status |  |  | checkpoint | Check both alignment & height are correct
checkpoint-status |  |  | checkpoint | General visual check for damage, etc
checkpoint-status |  |  | checkpoint | Check (floor) fire collars are rated & sized as per current IFC documentation
checkpoint-status |  |  | checkpoint | Check (wall) fire collars are rated & sized as per current IFC documentation
checkpoint-status |  |  | checkpoint | Check fire wrap is correctly rated & located as per current IFC documentation
checkpoint-status |  |  | checkpoint | Check metal sleeve penetrations are sized & located as per current IFC documentation
checkpoint-status |  |  | checkpoint | Check cast-in roof outlet/overflow bodies are installed in locations & heights as required
checkpoint-status |  |  | checkpoint | Finished R.L. are correct & verified
checkpoint-status |  |  | checkpoint | Seal or cap off any open ends if required for security
checkpoint-status |  |  | checkpoint | Check all fire collars are Logged & Registered
checkpoint-status |  |  | checkpoint | Test result to be recorded by photo/time/date. (Provide comment if required)
checklist-flat |  |  | checklist | FO Laundry Troughs |  |  |  |  | Yes | FO Laundry Troughs | 96e71a4d-f01a-40bc-ae16-1297a69785c4
checkpoint-status |  |  | checkpoint | This installation and following checks are to comply with AS-3500
checkpoint-status |  |  | checkpoint | Confirm type supplied & installed as per contract specification
checkpoint-status |  |  | checkpoint | General finish & alignment both level & centre of fixture/tapware
checkpoint-status |  |  | checkpoint | Solid installation & mounting of trough bowl & mixer
checkpoint-status |  |  | checkpoint | Check operation of plug & washer
checkpoint-status |  |  | checkpoint | Check for evidence of leakage
checkpoint-status |  |  | checkpoint | Check in cupboard for glue, cleaner or pencil marks
checkpoint-status |  |  | checkpoint | Check cover plates are installed
checkpoint-status |  |  | checkpoint | Check mini stops for operation & leaks
checkpoint-status |  |  | checkpoint | Check flexible connections for kinks or twisting
checkpoint-status |  |  | checkpoint | Check trap is installed & nuts are tight
checkpoint-status |  |  | checkpoint | Check AAV installation (if required)
checkpoint-status |  |  | checkpoint | Operate mixer & half fill bowl then discharge
checkpoint-status |  |  | checkpoint | Check hot water delivery time & temp against contract doc's
checkpoint-status |  |  | checkpoint | Check inside bowl trap for signs of debris etc
checkpoint-status |  |  | checkpoint | Check caulking is correct
checklist-flat |  |  | checklist | AU Application for New Service Connection |  |  |  |  | Yes | AU Application for New Service Connection | b381f9cc-afc6-43c0-8de4-a5dae0b9b8fa
checkpoint-status |  |  | checkpoint | Road Opening Permit
checkpoint-status |  |  | checkpoint | Storm Water Drainage
checkpoint-status |  |  | checkpoint | Sewer Drainage
checkpoint-status |  |  | checkpoint | Water Supply
checkpoint-status |  |  | checkpoint | Natural Gas Supply
checklist-flat |  |  | checklist | SD Stacks & Vents (Main Droppers) |  |  |  |  | Yes | SD Stacks & Vents (Main Droppers) | d68f5331-69ef-4eeb-a8d4-af0de63d55ab
checkpoint-status |  |  | checkpoint | This installation and following checks are to comply with AS-3500
checkpoint-status |  |  | checkpoint | General visual check for pipe damage, etc
checkpoint-status |  |  | checkpoint | Pipe materials are correct for application
checkpoint-status |  |  | checkpoint | Sewer stacks are installed
checkpoint-status |  |  | checkpoint | Sewer vents are installed
checkpoint-status |  |  | checkpoint | Cross vents are correct
checkpoint-status |  |  | checkpoint | PAPA vents are installed (if applicable)
checkpoint-status |  |  | checkpoint | Expansion joints are installed & compliant with AS3500
checkpoint-status |  |  | checkpoint | Ensure expansion joint spacers are removed
checkpoint-status |  |  | checkpoint | Stack base I.O. is installed
checkpoint-status |  |  | checkpoint | Stack bases supported correctly
checkpoint-status |  |  | checkpoint | Clips are solidly fixed & of correct size/type as per manufactures instructions.
checkpoint-status |  |  | checkpoint | Clips & spacing are installed & compliant with AS3500
checkpoint-status |  |  | checkpoint | Penetrations are installed
checkpoint-status |  |  | checkpoint | Drain penetrations are caulked
checkpoint-status |  |  | checkpoint | Fire collars are installed & registered
checkpoint-status |  |  | checkpoint | Pipe-work is designed, installed & sized as per current IFC documentation
checkpoint-status |  |  | checkpoint | Seal or cap off any open ends if required for security
checkpoint-status |  |  | checkpoint | Check traps are correct locations, finished heights & clear of debris
checkpoint-status |  |  | checkpoint | Rising mains installed & connected if required
checkpoint-status |  |  | checkpoint | Acoustic insulation installed & correct weight as designed
checkpoint-status |  |  | checkpoint | Test by Pneumatic/Hydrostatic method as per AS3500 & RSG procedure
checkpoint-status |  |  | checkpoint | Test sticker to be adhered to pipe 1500mm above floor level facing a corridor or accessible wall
checkpoint-status |  |  | checkpoint | Test result to be recorded by photo/time/date. (Provide comment if required)
checkpoint-status |  |  | checkpoint | Pipe I.D. labels are installed & spaced compliant with AS3500
checklist-flat |  |  | checklist | TMP Temporary Plumbing Services |  |  |  |  | Yes | TMP Temporary Plumbing Services | 7ae9cc09-211d-49d7-82ba-0fe4b57a83f6
checkpoint-status |  |  | checkpoint | Work Completed (As per below)
label | 1d2b97dc-d82e-4528-bc06-c6653acc7d41 |  | note | Add Comments/Photos below as applicable
button | 804fdd1b-3c15-4939-92e2-0fea73c9b2f2 |  | button | Installer is a Registered Plumber/Apprentice (VIC) | N/A, No,Yes
button | 81875793-f7ba-49a1-862f-8d3368e44492 |  | button | Installer clearly understands the task to be undertaken | N/A, No,Yes
button | 33c91e33-6e83-4836-b633-331fda6e9be3 |  | button | Ensure installation materials are used in accordance with manufacturer instructions | N/A, No,Yes
button | 339d2d76-2d3b-47fd-a08b-31c13286bb4a |  | button | Check for damage or leaks to the installation | N/A, No,Yes
button | 02c2bf6b-6096-413c-853d-2bbb59e43b81 |  | button | Check pressure pipe joints are installed correctly | N/A, No,Yes
button | 187245d0-b9ee-451b-8c10-d01b5a62698f |  | button | Check PVC joints are cleaned & glued (no duct tape) | N/A, No,Yes
button | 6dd1b248-6ad4-4a8e-befa-17780b26df7b |  | button | Ensure all waste/rain water discharges to a live drainage system | N/A, No,Yes
button | 7ab0141b-76f2-4474-b578-097db7b70bb0 |  | button | Ensure all pipe & fittings are not reused | N/A, No,Yes
button | da87f867-67ad-4bc4-9c8b-aac0633c34c1 |  | button | Check cross connections between reused & potable water | N/A, No,Yes
button | e091b966-d60f-4403-ba78-21bcd309eba9 |  | button | Check Jump Form temp connection when jacking | N/A, No,Yes
button | 012bc6b2-bfb7-418e-bbab-3783ddbc8bcd |  | button | Check any open ends are sealed and/or capped | N/A, No,Yes
checkpoint-status |  |  | checkpoint | Final sign off - Pass when Work completed to specifications/drawings (Any issues please comment & Add photo's below)
boolean | bb4fcef1-36d4-41b0-8677-a13134b422d8 |  | tickbox | Area clean
checklist-flat |  |  | checklist | AU Notification to Commence Works in Vicinity |  |  |  |  | Yes | AU Notification to Commence Works in Vicinity | 84d22905-8808-4214-943b-0b40048ae83b
checkpoint-status |  |  | checkpoint | Dial Before You Dig
checkpoint-status |  |  | checkpoint | Council/Municipality
checkpoint-status |  |  | checkpoint | Storm Water Drainage
checkpoint-status |  |  | checkpoint | Sewer Drainage
checkpoint-status |  |  | checkpoint | Water Supply
checkpoint-status |  |  | checkpoint | Natural Gas Supply
checkpoint-status |  |  | checkpoint | Communications & Data
checkpoint-status |  |  | checkpoint | Electrical Power
checkpoint-status |  |  | checkpoint | Metro Rail
checkpoint-status |  |  | checkpoint | Metro Trams
checkpoint-status |  |  | checkpoint | VIC Roads
checklist-flat |  |  | checklist | MT Re-Cycled Water Meters |  |  |  |  | Yes | MT Re-Cycled Water Meters | 5f40783c-ba05-4f99-8ce8-ffec79a5e6cf
checkpoint-status |  |  | checkpoint | This installation and following checks are to comply with AS-3500
checkpoint-status |  |  | checkpoint | Water Meter Details:
text | 07a527bf-6552-48dc-81be-8701e698afd6 |  | textbox | Meter No:
text | f25cc293-2c50-40de-83c2-5a115eed5a82 |  | textbox | Meter Location:
text | e41ce0d9-ee09-47ef-abb9-c64f2c0179bb |  | textbox | Meter Size:
checkpoint-status |  |  | checkpoint | General visual check for pipe damage/leaks, etc
checkpoint-status |  |  | checkpoint | Meter installed & sized as per current documentation
checkpoint-status |  |  | checkpoint | Meter bracketed
checkpoint-status |  |  | checkpoint | Analogue meter display is facing upright
checkpoint-status |  |  | checkpoint | Confirm I.D. point against the meter register
checkpoint-status |  |  | checkpoint | Pulse rate value is correct
checkpoint-status |  |  | checkpoint | Pulse rate is output is manually proved
checkpoint-status |  |  | checkpoint | BMS wiring connected by mechanical contractor
checkpoint-status |  |  | checkpoint | Flow direction is correct
checkpoint-status |  |  | checkpoint | Pipe I.D. labels are installed & spaced compliant with AS3500
checkpoint-status |  |  | checkpoint | Test result to be recorded by photo/time/date. (Provide comment if required)
checkpoint-status |  |  | checkpoint | Isolation valves closed after testing (If Required)
checklist-flat |  |  | checklist | TST Testing Reduced Pressure Zone Device (RPZD) |  |  |  |  | Yes | TST Testing Reduced Pressure Zone Device (RPZD) | 78cf8b4e-67e7-4611-8c5f-463dfac83f77
checkpoint-status |  |  | checkpoint | This testing procedure conforms with that as set out in AS-3500.1 (2018)
checkpoint-status |  |  | checkpoint | The tester is qualified & trained to carry out the testing procedure required
checkpoint-status |  |  | checkpoint | Engage a certified/licenced specialized sub-contractor to perform & document this test
checkpoint-status |  |  | checkpoint | Request & receive a signed certificate of successful test result
checkpoint-status |  |  | checkpoint | If test is successful, slowly release test pressure and return the system back to neutral conditions
checkpoint-status |  |  | checkpoint | Test sticker in visible location
checkpoint-status |  |  | checkpoint | Test result recorded by photo/time/date
checkpoint-status |  |  | checkpoint | Test route/location attached to this Check Point as PDF plan or snap shot with its unique I.D. number.
checkpoint-status |  |  | checkpoint | Failures are to be immediately reported to management for analysis & repatriation
checklist-flat |  |  | checklist | SD Wastes & Vents (Low Level) |  |  |  |  | Yes | SD Wastes & Vents (Low Level) | 544de5f2-c5dc-49a5-8b9b-a6c7bc23d9d3
checkpoint-status |  |  | checkpoint | This installation and following checks are to comply with AS-3500
checkpoint-status |  |  | checkpoint | General visual check for pipe damage, etc
checkpoint-status |  |  | checkpoint | Pipe materials are correct for application
checkpoint-status |  |  | checkpoint | Check in-wall noggings are installed to correct locations
checkpoint-status |  |  | checkpoint | Check waste pipes are installed to correct heights & locations
checkpoint-status |  |  | checkpoint | Check AAV installation (if required)
checkpoint-status |  |  | checkpoint | Clips are solidly fixed & of correct size/type as per manufactures instructions.
checkpoint-status |  |  | checkpoint | Clips & spacing are installed & compliant with AS3500
checkpoint-status |  |  | checkpoint | Penetrations are installed
checkpoint-status |  |  | checkpoint | Drain penetrations are caulked
checkpoint-status |  |  | checkpoint | Fire collars are installed & registered
checkpoint-status |  |  | checkpoint | Pipe-work is designed, installed & sized as per current IFC documentation
checkpoint-status |  |  | checkpoint | Seal or cap off any open ends if required for security
checkpoint-status |  |  | checkpoint | Check traps are correct locations, finished heights & clear of debris
checkpoint-status |  |  | checkpoint | Rising mains installed & connected if required
checkpoint-status |  |  | checkpoint | Acoustic insulation installed & correct weight as designed
checkpoint-status |  |  | checkpoint | Test by Pneumatic/Hydrostatic method as per AS3500 & RSG procedure
checkpoint-status |  |  | checkpoint | Test result to be recorded by photo/time/date. (Provide comment if required)
checkpoint-status |  |  | checkpoint | Pipe I.D. labels are installed & spaced compliant with AS3500
checklist-flat |  |  | checklist | TST Testing Thermostatic Mixing Valve (TMV) |  |  |  |  | Yes | TST Testing Thermostatic Mixing Valve (TMV) | 44d40095-cc7a-465e-9e4a-a87f2c12e589
checkpoint-status |  |  | checkpoint | This testing procedure conforms with that as set out in AS-3500.4 (2018)
checkpoint-status |  |  | checkpoint | The tester is qualified & trained to carry out the testing procedure required
checkpoint-status |  |  | checkpoint | Engage a certified/licenced specialized sub-contractor to perform & document this test
checkpoint-status |  |  | checkpoint | Request & receive a signed certificate of successful test result
checkpoint-status |  |  | checkpoint | If test is successful, slowly release test pressure and return the system back to neutral conditions
checkpoint-status |  |  | checkpoint | Test sticker in visible location
checkpoint-status |  |  | checkpoint | Test result recorded by photo/time/date
checkpoint-status |  |  | checkpoint | Test route/location attached to this Check Point as PDF plan or snap shot with its unique I.D. number.
checkpoint-status |  |  | checkpoint | Failures are to be immediately reported to management for analysis & repatriation
checklist-flat |  |  | checklist | FO Wall Tundishes |  |  |  |  | Yes | FO Wall Tundishes | 08073a04-b995-4904-9460-4e08267a020d
checkpoint-status |  |  | checkpoint | This installation and following checks are to comply with AS-3500
checkpoint-status |  |  | checkpoint | Confirm type supplied & installed as per contract specification
checkpoint-status |  |  | checkpoint | General finish & alignment both level & centre of tundish
checkpoint-status |  |  | checkpoint | Solid installation & mounting of tundish
checkpoint-status |  |  | checkpoint | Look for evidence of behind the wall leakage showing on floor
checklist-flat |  |  | checklist | SW Stormwater Drainage (In-Ground) |  |  |  |  | Yes | SW Stormwater Drainage (In-Ground) | c25f4dbd-2be4-4680-851e-0cde9c4852f7
checkpoint-status |  |  | checkpoint | This installation and following checks are to comply with AS-3500
checkpoint-status |  |  | checkpoint | DBYD received & verified before commencement of work
checkpoint-status |  |  | checkpoint | Authority applications for stormwater drainage & start work notices accepted
checkpoint-status |  |  | checkpoint | Municipality connections installed by Richstone
checkpoint-status |  |  | checkpoint | General visual check for pipe damage, etc
checkpoint-status |  |  | checkpoint | Pipe materials are correct for application
checkpoint-status |  |  | checkpoint | Ensure all grades are correct
checkpoint-status |  |  | checkpoint | Clips are solidly fixed & of correct size/type as per manufactures instructions.
checkpoint-status |  |  | checkpoint | Clips & spacing are installed & compliant with AS3500
checkpoint-status |  |  | checkpoint | Clips & Shanks etc. are completely corrosion protected by use of "Denso" type wrapping & sealing
checkpoint-status |  |  | checkpoint | Backfill is specified materials & compacted to test OK
checkpoint-status |  |  | checkpoint | Spoil is removed
checkpoint-status |  |  | checkpoint | Pipe-work is designed, installed & sized as per current IFC documentation
checkpoint-status |  |  | checkpoint | Seal or cap off any open ends if required for security
checkpoint-status |  |  | checkpoint | Check traps are correct locations, finished heights & clear of debris
checkpoint-status |  |  | checkpoint | Rising mains installed & connected if required
checkpoint-status |  |  | checkpoint | Marker tape installed
checkpoint-status |  |  | checkpoint | Drain penetrations are caulked
checkpoint-status |  |  | checkpoint | Stormwater junxtion & grated pits are installed in sizes & locations as per design
checkpoint-status |  |  | checkpoint | Trench channels & grates are installed in sizes & locations as per design
checkpoint-status |  |  | checkpoint | Cast-in round/square grates & bodies are installed in sizes & locations as per design
checkpoint-status |  |  | checkpoint | Cast-in planter box/tree grates & bodies are installed in sizes & locations as per design
checkpoint-status |  |  | checkpoint | Test by Pneumatic/Hydrostatic method as per AS3500 & RSG procedure
checkpoint-status |  |  | checkpoint | Test result to be recorded by photo/time/date. (Provide comment if required)
checklist-flat |  |  | checklist | CC Concrete Coring & Cutting |  |  |  |  | Yes | CC Concrete Coring & Cutting | a4e5e1c7-a550-4ff4-9d94-a443b356048b
checkpoint-status |  |  | checkpoint | Structural Engineer has been consulted & certified the proposed cutting
checkpoint-status |  |  | checkpoint | Post tensioning design has been overlayed
checkpoint-status |  |  | checkpoint | Electronic/Sonic survey has been completed & certified
checkpoint-status |  |  | checkpoint | Safety procedures have been certified & work area is in compliance
checkpoint-status |  |  | checkpoint | Installed & sized as per current documentation
checkpoint-status |  |  | checkpoint | Covers installed if required for security
checkpoint-status |  |  | checkpoint | Record installation by photo & time/date
checkpoint-status |  |  | checkpoint | Check cast-in roof outlet/overflow bodies installed in locations & heights as required
checkpoint-status |  |  | checkpoint | Finished R.L. are correct & verified
checkpoint-status |  |  | checkpoint | Seal or cap off any open ends if required for security
checkpoint-status |  |  | checkpoint | Record installation by photo & time/date
checklist-flat |  |  | checklist | COM Commission Fixture Groups |  |  |  |  | Yes | COM Commission Fixture Groups | 6bcf020a-8b3b-4ff2-b2bc-4be2539b650e
checkpoint-status |  |  | checkpoint | Confirm the installer is qualified & trained to carry out the task as assigned
checkpoint-status |  |  | checkpoint | Ensure all sewer drainage pressure tests have been successfully carried out & recorded previously
checkpoint-status |  |  | checkpoint | Ensure all down-pipe drainage pressure tests have been successfully carried out & recorded previously
checkpoint-status |  |  | checkpoint | Ensure all water pressure tests have been successfully carried out & recorded previously
checkpoint-status |  |  | checkpoint | Ensure all natural gas pressure tests have been successfully carried out & recorded previously
checkpoint-status |  |  | checkpoint | Confirm the fixtures/tapware/appliances installed conform with the contract & specification docs
checkpoint-status |  |  | checkpoint | Ensure the fixtures/tapware/appliances installed are un-blemished & fit for hand over
checkpoint-status |  |  | checkpoint | Ensure the fixtures/tapware/appliances are installed level, square & centre of position
checkpoint-status |  |  | checkpoint | Ensure the fixtures/tapware/appliances are neatly & firmly fitted
checkpoint-status |  |  | checkpoint | Ensure the wall/splash-back materials & clearances conform with AS-5601
checkpoint-status |  |  | checkpoint | Ensure the range-hood height clearance conforms with AS-5601 & manufacturer tolerances
checkpoint-status |  |  | checkpoint | Check gas appliance burner operation for functionality & complete combustion
checkpoint-status |  |  | checkpoint | Check installation of correct pressure reduction valves on dish washers, fridges, etc.
checkpoint-status |  |  | checkpoint | Check all valves, unions & regulators are fit for purpose & not leaking
checkpoint-status |  |  | checkpoint | Check for installation debris, glue, cleaner & set-out marks. (remove if necessary)
checkpoint-status |  |  | checkpoint | General visual check for signs of water leakage
checkpoint-status |  |  | checkpoint | Check cover plates have been installed
checkpoint-status |  |  | checkpoint | Check mini stops have been installed
checkpoint-status |  |  | checkpoint | Check flexible water/gas connections are fit for purpose with no twisting or kinks
checkpoint-status |  |  | checkpoint | Check dishwasher hose for connection with no twists or kinks
checkpoint-status |  |  | checkpoint | Check waste trap & associated connectors are installed with nuts firmly tightened
checkpoint-status |  |  | checkpoint | Check all fixture & floor waste traps are clear of debris & free flowing
checkpoint-status |  |  | checkpoint | Check all balcony rain water outlets & overflows are clear of debris & free flowing
checkpoint-status |  |  | checkpoint | AAV location & height is code compliant
checkpoint-status |  |  | checkpoint | Operate each fixture/tapware/appliance through its operation & functionality sequence
checkpoint-status |  |  | checkpoint | Check hot water delivery time & temperature against contract specification requirements
checkpoint-status |  |  | checkpoint | Visually check inside traps & floor wastes for possible debris & ensure free flow of waste water
checkpoint-status |  |  | checkpoint | Check hot water thermostatic control valves (TMV) for correct function & delivery temps ≤ 43°C
checkpoint-status |  |  | checkpoint | Check hot water temperature control valves (TCV) for correct function & delivery temps ≤ 50°C
checkpoint-status |  |  | checkpoint | Check location & functionality of any balancing or straining valves
checkpoint-status |  |  | checkpoint | Check correct operation & connections to all tundishes
checkpoint-status |  |  | checkpoint | Check RPZD fitting is installed on balcony tap if required
checkpoint-status |  |  | checkpoint | Check quality & application of caulking is fit for purpose
checkpoint-status |  |  | checkpoint | Check flood stoppers if in use on CWM stops
checkpoint-status |  |  | checkpoint | Seal or cap off any open ends if required i.e. CWM stops
checkpoint-status |  |  | checkpoint | Check valve tag numbers match their allocated location.
checkpoint-status |  |  | checkpoint | Check flow meter numbers match their allocated location.
checkpoint-status |  |  | checkpoint | Test sticker in visible location
checkpoint-status |  |  | checkpoint | Test result recorded by photo/time/date
checkpoint-status |  |  | checkpoint | Test route/location attached to this Check Point as PDF plan or snap shot with its unique I.D. number.
checklist-flat |  |  | checklist | FO Wash Basins |  |  |  |  | Yes | FO Wash Basins | 35ac35ae-d90e-4932-9e29-763f9b40a033
checkpoint-status |  |  | checkpoint | This installation and following checks are to comply with AS-3500
checkpoint-status |  |  | checkpoint | Confirm type supplied & installed as per contract specification
checkpoint-status |  |  | checkpoint | General finish & alignment both level & centre of fixture/tapware
checkpoint-status |  |  | checkpoint | Solid installation & mounting of basin bowl & mixer
checkpoint-status |  |  | checkpoint | Check operation of plug & washer
checkpoint-status |  |  | checkpoint | Check for evidence of leakage
checkpoint-status |  |  | checkpoint | Check in cupboard for glue, cleaner or pencil marks
checkpoint-status |  |  | checkpoint | Check cover plates are installed
checkpoint-status |  |  | checkpoint | Check mini stops for operation & leaks
checkpoint-status |  |  | checkpoint | Check flexible connections for kinks or twisting
checkpoint-status |  |  | checkpoint | Check trap is installed & nuts are tight
checkpoint-status |  |  | checkpoint | Check AAV installation (if required)
checkpoint-status |  |  | checkpoint | Operate mixer & half fill bowl then discharge
checkpoint-status |  |  | checkpoint | Check hot water delivery time & temp against contract doc's
checkpoint-status |  |  | checkpoint | Check inside bowl trap for signs of debris etc
checkpoint-status |  |  | checkpoint | Check caulking is correct
checklist-flat |  |  | checklist | New Task: |  |  |  |  | Yes | Add New Task | c5099ee7-1aea-4421-8179-48ef4fc5e602
checkpoint-status |  |  | checkpoint | Task completed
checklist-flat |  |  | checklist | TST Testing Roof Downpipes (Water Test) |  |  |  |  | Yes | TST Testing Roof Downpipes (Water Test) | 8f7d9669-cd40-446a-9001-87827240c0ba
checkpoint-status |  |  | checkpoint | This testing procedure conforms with that as set out in AS-3500.3 (2018)
checkpoint-status |  |  | checkpoint | Ensure bore is completely free of any blockages, constrictions or debris
checkpoint-status |  |  | checkpoint | Ensure pipe-work is securely fixed to eliminate movement during pressure test
checkpoint-status |  |  | checkpoint | Temporarily plug & seal any open ends below the test point
checkpoint-status |  |  | checkpoint | Choke test to a head of 10 metres or if the downpipe if shorter, fill to its limit
checkpoint-status |  |  | checkpoint | Slowly fill the test riser with water until full and hold for 30 minutes
checkpoint-status |  |  | checkpoint | Testing is deemed successful if the water level remains unchanged after 30 minutes
checkpoint-status |  |  | checkpoint | If test is successful, slowly release test pressure and return the system back to neutral working conditions
checkpoint-status |  |  | checkpoint | Test sticker on pipe 1500mm high facing a corridor or accessible wall
checkpoint-status |  |  | checkpoint | Test result recorded by photo/time/date
checkpoint-status |  |  | checkpoint | Test route/location attached to this Check Point as PDF plan or snap shot with its unique I.D. number.
checkpoint-status |  |  | checkpoint | Failures are to be immediately reported to management for analysis & repatriation
checklist-flat |  |  | checklist | NG Natural Gas Meters |  |  |  |  | Yes | NG Natural Gas Meters | 4becfd7b-e66b-41cd-b62e-e7e574aabaaf
checkpoint-no-status |  |  | checkpoint | Water Meter Details:
text | 6111b881-06f6-4bf4-a8d5-9d1f4be8567d |  | textbox | Meter No:
text | b9fbb427-370b-44f1-981c-368aa43218c2 |  | textbox | Level:
text | f017d1d4-5c48-476e-9115-ce4274167dbb |  | textbox | Meter Size:
checkpoint-status |  |  | checkpoint | General visual check for pipe damage/leaks, etc
checkpoint-status |  |  | checkpoint | Meter installed & sized as per current documentation
checkpoint-status |  |  | checkpoint | Meter bracketed
checkpoint-status |  |  | checkpoint | Analogue meter display is facing upright
checkpoint-status |  |  | checkpoint | Confirm I.D. point against the meter register
checkpoint-status |  |  | checkpoint | Pulse rate value is correct
checkpoint-status |  |  | checkpoint | Pulse rate is output is manually proved
checkpoint-status |  |  | checkpoint | BMS wiring connected by mechanical contractor
checkpoint-status |  |  | checkpoint | Flow direction is correct
checkpoint-status |  |  | checkpoint | Pipe I.D. labels are installed & spaced compliant with AS3500
checkpoint-status |  |  | checkpoint | Record installation by photo & time/date
checkpoint-status |  |  | checkpoint | Isolation valves closed after testing (If Required)
checklist-flat |  |  | checklist | SD Sewer Drainage (In-Ground) |  |  |  |  | Yes | SD Sewer Drainage (In-Ground) | faa93398-51d3-4c7f-be64-543427531e95
checkpoint-status |  |  | checkpoint | This installation and following checks are to comply with AS-3500
checkpoint-status |  |  | checkpoint | DBYD received & verified before commencement of work
checkpoint-status |  |  | checkpoint | Authority sewer drainage applications & start work notices accepted
checkpoint-status |  |  | checkpoint | Authority connections installed by certified contractors
checkpoint-status |  |  | checkpoint | General visual check for pipe damage, etc
checkpoint-status |  |  | checkpoint | Sewer instection chambers are installed in sizes & locations as per design
checkpoint-status |  |  | checkpoint | Sewer Boundary Traps are installed in sizes & locations as per design
checkpoint-status |  |  | checkpoint | Sewer reflux valves are installed in sixes & locations as per design
checkpoint-status |  |  | checkpoint | Pipe materials are correct for application
checkpoint-status |  |  | checkpoint | Ensure all grades are correct
checkpoint-status |  |  | checkpoint | Ensure all invert levels are correct
checkpoint-status |  |  | checkpoint | Sewer vents are installed
checkpoint-status |  |  | checkpoint | Clips are solidly fixed & of correct size/type as per manufactures instructions.
checkpoint-status |  |  | checkpoint | Clips & Shanks etc. are completely corrosion protected by use of "Denso" type wrapping & sealing
checkpoint-status |  |  | checkpoint | Clips & spacing are installed & compliant with AS3500
checkpoint-status |  |  | checkpoint | Backfill is specified materials & compacted to test OK
checkpoint-status |  |  | checkpoint | Spoil is removed
checkpoint-status |  |  | checkpoint | Vents are installed compliant with AS3500
checkpoint-status |  |  | checkpoint | Pipe-work is designed, installed & sized as per current IFC documentation
checkpoint-status |  |  | checkpoint | Seal or cap off any open ends if required for security
checkpoint-status |  |  | checkpoint | Check traps are correct locations & clear of debris
checkpoint-status |  |  | checkpoint | Check trap grates are at correct finished heights
checkpoint-status |  |  | checkpoint | Rising mains installed & connected if required
checkpoint-status |  |  | checkpoint | Marking tape installed
checkpoint-status |  |  | checkpoint | Drain penetrations are caulked
checkpoint-status |  |  | checkpoint | Test by Pneumatic/Hydrostatic method as per AS3500 & RSG procedure
checkpoint-status |  |  | checkpoint | Test result to be recorded by photo/time/date. (Provide comment if required)
checklist-flat |  |  | checklist | NG Rough-in (High Level) |  |  |  |  | Yes | NG Rough-in (High Level) | 62a2812b-47f0-46bc-8b2a-e1b548285be8
checkpoint-status |  |  | checkpoint | container
checklist-flat |  |  | checklist | TST Testing Natural Gas Service (Nitrogen/Air Test) Low Pressure |  |  |  |  | Yes | TST Testing Natural Gas Service (Nitrogen/Air Test) Low Pressure | 6a479fa7-e348-482d-979d-b4cc187027ac
checkpoint-status |  |  | checkpoint | This testing procedure conforms with that as set out in AS-5601.1 (2013)
checkpoint-status |  |  | checkpoint | Ensure all valves dedicated to isolating the test zone are securely shut off & tagged
checkpoint-status |  |  | checkpoint | Nominate an air purging valve point
checkpoint-status |  |  | checkpoint | Nominate a pressure testing valve point
checkpoint-status |  |  | checkpoint | Ensure isolating valves within the test zone are open as required
checkpoint-status |  |  | checkpoint | Ensure all terminal open ends i.e. lugged elbows, etc are securely capped off
checkpoint-status |  |  | checkpoint | Slowly open test feeder valve & fill the test zone with nitrogen/air until completely purged
checkpoint-status |  |  | checkpoint | Connect pressure testing device to the nominated test point
checkpoint-status |  |  | checkpoint | Shut off the gas feeder valve
checkpoint-status |  |  | checkpoint | Commence testing by slowly increasing pressure up to 1.5 kPa above working pressure
checkpoint-status |  |  | checkpoint | Testing is deemed successful if the pressure remains unchanged for 5 mins of every 30 litres volume of pipe
checkpoint-status |  |  | checkpoint | If test is successful, slowly release test pressure and return the system back to neutral conditions
checkpoint-status |  |  | checkpoint | Test sticker in visible location
checkpoint-status |  |  | checkpoint | Test result recorded by photo/time/date
checkpoint-status |  |  | checkpoint | Test route/location attached to this Check Point as PDF plan or snap shot with its unique I.D. number.
checkpoint-status |  |  | checkpoint | Failures are to be immediately reported to management for analysis & repatriation