## QA Folder Structure
QA Folder Structure |  |  | Checklists
OHS |  |  | SWMS TBC
Site QA
Level 4
|  | Fix 1 | Fix 1 ITP
|  | Fix 2 | Fix 2 ITP
Level 16
|  | Fix 1 | Fix 1 ITP
|  | Fix 2 | Fix 2 ITP
Level 18
|  | Fix 1 | Fix 1 ITP
|  | Fix 2 | Fix 2 ITP

## ITPChecklists
type | name | values | prefix | postfix | usage count | user addable
checklist-flat | Fix 1 ITP
checkpoint | Working to an approved drawing
checkpoint | Setout is correct as per current approved drawings
text | Drawing no. & Revision
checkpoint | No cross-connection on all water lines
checkpoint | Support and fixings checked (water hammer/silicone) and in order
checkpoint | All lines new and existing capped for testing
checkpoint | Pressure tested waterlines 1500kpa for 30 mins with start photo attached below
checkpoint | Pressure tested waterlines 1500kpa for 30 mins with finish photo attached below
checkpoint | Fixture waste points heights and centres doubled checked before wall sign off
checkpoint | All suspended drainage has been supported as per AS3500 Requirements
checkpoint | All suspended drainage been flow tested and has no leaks
checkpoint | Please supply photos of all water and waste completetd installations
checkpoint | Area clean & works signed off below
checklist-flat | Fix 2 ITP
checkpoint | Only approved fixtures installed
checkpoint | Products checked and have no imperfections
checkpoint | Fixtures installed as per approved drawing locations
checkpoint | No cross-connection on all water lines
checkpoint | Hot water correct temperature & Hot water tempering valve set to 50c +/-5c)
checkpoint | DDA Hot water correct temperature & Hot water tmv set to 42c +/-2c)
checkpoint | Water pressure acceptable 350kpa - 500kpa
checkpoint | Checked all drainage is working correctly wth no leaks
checkpoint | Cleaned out all strainers
checkpoint | Commissioned all fixtures
checkpoint | Final check for any leaks
checkpoint | Area clean - sign off and photos attached below
checklist-flat | SWMS Checklist
checkpoint | SWMS doc uploaded and details enterred below
text | Name
text | Date

## Sheet3
| Matt | Jacob | Nick
Jan
1
2
3
4
Feb