## ITPs Checklists
type | name | values | prefix | postfix | usage count | user addable
checklist-flat | Fix 1 ITP
checkpoint | Working to an approved drawing
checkpoint | Setout is correct as per current approved drawings
text | Drawing no. & Revision
checkpoint | No cross-connection on all water lines
checkpoint | Support and fixings checked (water hammer/silicone) and in order
checkpoint | All lines new and existing capped for testing
checkpoint | Pressure tested waterlines 1500kpa for 30 mins with start photo attached below
checkpoint | Pressure tested waterlines 1500kpa for 30 mins with finish photo attached below
checkpoint | Fixture waste points heights and centres doubled checked before wall sign off
checkpoint | All suspended drainage has been supported as per AS3500 Requirements
checkpoint | All suspended drainage been flow tested and has no leaks
checkpoint | Please supply photos of all water and waste completetd installations
checkpoint | Area clean & works signed off below
checklist-flat | Fix 2 ITP
checkpoint | Only approved fixtures installed
checkpoint | Products checked and have no imperfections
checkpoint | Fixtures installed as per approved drawing locations
checkpoint | No cross-connection on all water lines
checkpoint | Hot water correct temperature & Hot water tempering valve set to 50c +/-5c)
checkpoint | DDA Hot water correct temperature & Hot water tmv set to 42c +/-2c)
checkpoint | Water pressure acceptable 350kpa - 500kpa
checkpoint | Checked all drainage is working correctly wth no leaks
checkpoint | Cleaned out all strainers
checkpoint | Commissioned all fixtures
checkpoint | Final check for any leaks
checkpoint | Area clean - sign off and photos attached below
checklist-flat | SWMS Checklist
checkpoint | SWMS doc uploaded and details entered below
text | Name
text | Date
checklist-flat | Take 5 Checklist
checkpoint | Task details entered below
text | Task
checkpoint-no-status | If any of the below are 'Fail' (no) - make yourself aquainted with site requirements before starting work
checkpoint | Have you completed a site induction?
checkpoint | Do you know the site’s health and safety rules?
checkpoint | Are you familiar with security arrangements and the system for reporting incidents, near misses and hazards?
checkpoint | Are you familiar with the emergency facilities and evacuation procedure/route for the site?
checkpoint | Do you have access to appropriate emergency and first aid equipment?
checkpoint | Have you asked the person in charge about all relevant hazards?
checkpoint-no-status | If any of the below are 'Fail' (no) - follow up with person in charge to ensure your safety | [5 empty] | task:
checkpoint | If the work involves a high risk task (such as work at heights, hot-work, confined spaces), has a safe work method statement or job safety analysis been completed?
checkpoint | Do you have the correct procedures, equipment and PPE to do the work safely?
checkpoint | Has equipment that requires a lock/tag-out and/or power that requires isolation/containment been completed?
checkpoint | Is there appropriate separation of vehicles and people during the proposed work?
checkpoint | Is all required electrical/mechanical equipment in a safe condition?
checkpoint | Are all hazardous and/or dangerous goods/substances used and stored according to their material safety data sheets?
checkpoint | Have you consulted with all fellow workers about the task to be completed and the safe way to do it?
checkpoint | Have you got a safe way of getting in and out of your work area?
checkpoint | Have any manual handling risks been identified and assessed?
checkpoint-no-status | Any additional site specifc hazards or requirements commented below
checklist-flat | Events QA ITP
checkpoint | Kitchen layout is correct as per current drawings issued by client
checkpoint | Kitchen layout is correct as per current drawings issued by client
checkpoint | Do all gas appliances have the minimum 500mm clearance from combustible surfaces?
checkpoint | Do all gas appliances have an isolation valve installed and is valve in good condition?
checkpoint | Have all gas appliances been fixed in position?
checkpoint | Are gas flexible hoses installed off the floor?
checkpoint | Have all gas flexible hoses been installed with slack for expansion?
checkpoint | Are the gas LPG bottles installed with the minimum 1500mm clearance from an ignition source and secured to the base plate with chain?
checkpoint | Have all gas appliance been commissioned? Are they working as intended?
checkpoint | Has all tiger tail been installed neatly free of deformation in hoses?
checkpoint | Are all sinks,basins and appliance waste points connected?
checkpoint | Are all sinks, basin and appliance water points connected?
checkpoint | Is hot water unit connected and working as required?
checkpoint | Is macerator unit connected and working as required?
checkpoint | Are sullage tanks and sewer connections in place and connected as required?
checkpoint | All water points have been checked for cross connections
checkpoint | All water pipe has been installed neatly
checkpoint | All water and waste has been checked for leaks and repaired as required
checkpoint | Have all excess plumbing materials been removed from kitchen ready for handover?
checklist-flat | Transplumb Roofing ITP
checkpoint | Working to an approved drawing
checkpoint | Only approved materials installed
checkpoint | All fixings correctly installed as per AS 3500
checkpoint | Boxgutters/sump/downpipes installed and clipped correctly as per AS 3500
checkpoint | Flashings installed correctly and siliconed
checkpoint | Testing carried out where possible
checkpoint | Area clean & works signed off below
checklist-flat | Transplumb Variations
checkpoint | Variation details entered below
text | Variation Name
text | Variation Description
checkpoint | Materials & Labour Breakdown - Names, Hours & Materials Quantities entered in comments below
checkpoint | Final signoff - any supporting docs and client signature attached below
holdpoint | Request Signoff
checklist-flat | Transplumb General Works ITP
checkpoint | Client notified of works to be carried out
button | Do any of the works require pressure testing on completion | Yes,No
checkpoint | All requested works completed
checkpoint | Area clean & works signed off below
checklist-flat | Transplumb Drainage BG ITP
checkpoint | Working to an approved drawing
checkpoint | Setout is correct as per current approved drawings
checkpoint | Pipe bedding materials comply (as per AS 3500)
checkpoint | Grades, fittings & joints installed to standards
checkpoint | Inspection & Testing carried out prior to backfill
checkpoint | Sealed any open ends
checkpoint | Backfill & compact trenches to code requirements
checkpoint | CCTV on completion
checkpoint | Area clean & works signed off below
checklist-flat | Hydraulic Pressure Test Record Checklist
checkpoint | Details entered below
text | Description of system being tested
text | Nominal Working Pressure (KPA)
text | Max Test Pressure (KPA)
text | Test Type (Hydro/Air)
text | Gauges Calibration
text | Time at test
text | Time at test completion
text | Pressure at completion
text | Duration of Pressure Test
checkpoint | Transplumb and witness signoff attached below
holdpoint | Request signoff