## QA Folder Structure
QA Folder Structure |  |  |  |  | Checklists
Site QA |  | B5-B1, G, L1-L29
Wet Fire
Sleeves
|  |  | L1-L29 |  | Sleeves ITP
|  |  | Expand out below |  | Repeat until L29
Hydrants
|  |  | Low Rise |  | Hydrant Mains Risers ITP
|  |  | Mid Rise |  | Hydrant Mains Risers ITP
|  |  | High Rise |  | Hydrant Mains Risers ITP
Sprinkler Systems
First Fix
|  |  |  | G-L29 | Sprinkler System First Fix
Second Fix
|  |  |  | G-L29 | Sprinkler System Second Fix
|  |  | Expand out below |  | Repeat until L29
|  | Hose Reels |  |  | Hose Reels ITP
|  | Fire Water Tanks |  |  | Fire Water Tanks ITP
|  | Fire Pumps |  |  | Fire Pumps ITP
|  | Booster Assembly |  |  | Booster Installation ITP
|  | Fire Extinguishers |  |  | Fire Extinguishers ITP
Dry Fire
Fire Alarms
First Fix
|  |  |  | L1-L29 | Fire Alarms First Fix
Second Fix
L1-L29
Fire Alarms Second Fix
|  |  | Expand out below |  | Repeat until L29
EWIS
|  |  | L1-L29 |  | EWIS ITP
|  |  | Expand out below |  | Repeat until L29
|  | MASDS |  |  | Needs ITP - just leave as a folder for now

## Pirie ITPs
type | name | values | prefix | postfix
checklist-flat | Booster Installation ITP
checkpoint | Booster pipework cleaned & capped for transport to site
checkpoint | Booster pipework installed in accordance with applicable standards & specification utilising approved seismic fixings & bracing, approved fire penetration sealing
label | Boosters located in accordance with approved drawing & in accordance with AS2419
checkpoint | SAMFs approved hydrant values, hard suction & dual booster connectors fitted including pressure gauges
checkpoint | All above ground pipework securely fixed & plugged off & isolating valves closed & SAMFs required signage & block plans installed
checkpoint | Booster enclosure to be in accordance with SAMFs
checkpoint | Door hold open devices fitted & budget locks fitted as specified
checkpoint | Arrange for SAMFs to inspect fire booster assembly
checklist-flat | Fire Extinguishers ITP
checkpoint | Fire extinguishers & signs installed in accordance with AS 2444 & applicable approved drawing
checkpoint | Arranged SAMFS to carry out inspection and verify quantity and location of extinguishers are acceptable
checklist-flat | Fire Pumps ITP
checkpoint | Pumps & associated pipework installed in accordance with the approved drawings & AS2118. Pump room secure & lockable
checkpoint | Pump wiring installed in accordance with AS3000 & phase 3 & neutral power supply available
checkpoint | Fire water storage tank water supply available (suction) & all piping (discharge) & drains complete, pressure tested ready for use
checkpoint | Diesel engine filled with oil, fuel, batteries connected & diesel muffler & exhaust fitted to vent exhaust gases to atmosphere
checkoints | Pump testing completed - detail any non-conformances below
checklist-flat | Sprinkler System First Fix
checkpoint | Pipework installed in accordance with applicable TFP approved drawings
checkpoint | First fix sprinkler pipework, hangers, seismic fixings, guards, air bleed vents, drain valves fitted in accordance with AS2118
checkpoint | First Fix Pressure Test
checklist | Sprinkler System Second Fix
section | Installation
checkpoint | Second fix sprinkler pipework, hangers, seismic fixings, guards, air bleed vents, drain valves fitted in accordance with AS2118 | Yes, No, N/A
checkpoint | Second Fix Pressure Test
checkpoint | Sprinkler seismic hanging systems to be installed to AS1170.4 & include engineers sign off & supporting documentation | Yes, No, N/A
checkpoint | Fire penetrations to be sealed in accordance with manufacturers tested system with the location indicated on as builts with labels - Please attach photos
checkpoint | Sprinkler head spacings & temperature ratings checked to comply with AS2118
section | Test Procedures
checkpoint | Connect air compressor to above ground pipework to be tested. Fill pipework with compressed air to 100kpa
label | Inspect above ground pipework for obvious leakage. Re-check pressure gauge and if no major pressure loss, pump up to 200kpa. Hold at 200kpa for 10 minutes. If no obvious air leakage from pipework being tested, release air pressure via control valve on compressor, and fill pipework with water to towns main pressure and set up TFP pressure test pump
checkpoint | Notify builders supervisor that fire services pipework is to be pressure tested
checkpoint | If no obvious loss of pressure pump switch on TFP pressure test pump and pump to 1600kpa and hold at this test pressure for at least two hours as specified
section | Sign-Off
checkpoint | Works completed to specification/drawings - Attach photos of work below
checklist | Hydrant Mains Risers ITP
section | Installation
checkpoint | Pipework installed in accordance with appliance standards, seismic fixings & specifications
checkpoint | Hydrant & hose reel pipework cleaned & capped for transport to site
label | Hydrant & hose reels located in accordance with AS2419
checkpoint | First fix hydrant pipework, hangers, seismic fixings, drain valves fitted in accordance with AS2419
label | Hydrant seismic hanging systems to be installed to AS1170.4 & include engineers sign off & supporting documentation
checkpoint | Hydrants installed in accordance with AS2419 and SA water requirements
checkpoint | Hydrant caps and chains fitted
checkpoint | Hydrant valve wheels or oval spindles fitted as specified
checkpoint | Hydrant hose connection checked for SAMFs approved thread
checkpoint | Inspection carried out by Engineer - Attached/Any relevant comments added below | Yes, No, N/A
label | Sign-off attached below as applicable
checkpoint | Fire penetrations to be sealed in accordance with manufacturers tested system to the locations as indicated on as built drawings complete with labels - Please attach photos
button | Inspection carried out by Engineer - Attached/Any relevant comments added below | Yes, No, N/A
label | Sign-off attached below as applicable
checkpoint | Acoustic penetrations to be sealed in accordance with approved sample wall & manufacturers tested system to the locations as indicated on as builts
button | Inspection carried out by Engineer - Attached/Any relevant comments added below | Yes, No, N/A
label | Sign-off attached below as applicable
checkpoint | Hose reels located in accordance with approved drawing and in accordance with AS2441
checkpoint | All above ground pipework securely fixed and plugged off and isolating valves closed
checkpoint | Inspection carried out - Detail any corrective action for non-conformance Inspections
section | Test Procedures
checkpoint | Review inspection details above to verify that all inspections are satisfactory and test procedures can now follows
checkpoint | Connect air compressor to above ground pipework to be tested. Fill pipework with compressed air to 100kpa. Inspect above ground pipework for obvious leakage. Re-check pressure gauge and if no major pressure loss, pump up to 200kpa
label | Hold at 200kpa for 10 minutes. If no obvious air leakage from pipework being tested, release air pressure via control valve on compressor, and fill pipework with water to towns main pressure
checkpoint | Connect pressure test pump to water filled section of pipework being tested. Pump to 1000kpa and hold pressure for 5 minutes
label | If no obvious loss of pressure, pump to 1500kpa. if no obvious loss of pressure pump to 1700kpa and hold at this test pressure for at least two hours
section | Sign-Off
checkpoint | Works completed to specification/drawings - Attach photos of work below
checklist | Hose Reels ITP
section | Installation
checkpoint | Fire hose reels and signs installed in accordance with AS2441
checkpoint | Fire hose reels and sign installed in accordance with applicable approved drawing
checkpoint | Hose guides and rollers installed where applicable
checkpoint | Packing tapes removed, hose vented, water flow checked at minimum flow rate of 20 litres per minute
checkpoint | Fire hose reel turns freely with no excessive force
section | Test Procedures
checkpoint | Confirm hose reel pipework has been inspected and pressure tested as per ITP for hose reel pipework
checkpoint | With water supply valve to hose reels open, run out hose reels to full length and flow hose reels at full flow
label | Check hose reel assembly for leaks and secure fixings. Shut off water supply valve and rewind hoses
checkpoint | Arrange for SAMFs to carry out inspection and flow test on each hose reel
checkpoint | Arrange for client to witness SAMFs tests
section | Sign-Off
checkpoint | Works completed to specification/drawings - Attach photos of work below
checklist | Fire Water Tanks ITP
section | Installation
checkpoint | Tank roof and walls assembled in accordance with approved jsa's, shop drawings and approved construction drawings
checkpoint | Tank liner Installed in accordance with manufacturers data sheets and instructions
checkpoint | Ensure all tank panels, roof sheets, anchor bolts for tank internal braces are tight and no debris is left inside tank
checkpoint | Ensure all external tank connection fittings, access ladders, manhole covers, tank contents level indicators and external wind braces (if fitted) are correctly installed, tight and operational
checkpoint | Vacuum out any debris from inside tank and check all fixings/bolts for tightness. re-fit external manhole cover to form confined space
checkpoint | Tank leak test complete
section | Test Procedures
checkpoint | Make a detailed inspection of external walls of tank to check for any sign of a leak
checkpoint | Check ladders and manhole covers to ensure easy access is possible
checkpoint | Check tank contents gauge and signage for correct operation
checkpoint | Check tank roof and flashings to ensure no sharp edges and roof flashings are vermin proof
section | Sign-Off
checkpoint | Works completed to specification/drawings - Attach photos of work below
checklist-flat | Fire Alarms First Fix
checkpoint | Wiring installed in accordance with AS3000, ETSA regulations, Telstra and Austel regulations
checkpoint | Continuity and polarity checks carried out on all cables
checklist-flat | Fire Alarms Second Fix
section | Installation
checkpoint | Detectors, bells, break glass alarms, automatic magnetic door holders, visual alarms, mimic panels, main FIP, data gathering panels all installed in accordance with applicable approved drawings and AS1668, AS2036, as1670,AS1603 and SAMFs requirements
section | Test Procedures
checkpoint | Ensure client and builders site representative are aware that fire alarm system is to be tested, resulting in audible alarms
label | Audible and visual alarms can be disconnected or isolated during test once they have been proved to be operational
checkpoint | Conducted SAMFs signalling device test procedures
label | Ensure all mechanical plant interface circuits are isolated or disconnected (smoke spill fans, gas solenoid, etc)
checkpoint | Arrange formal SAMFs inspection and system testing
section | Sign-Off
checkpoint | Works completed to specification/drawings - Attach photos of work below
holdpoint | Request Builder Sign Off
checklist | EWIS ITP
section | Installation
checkpoint | Wiring installed in accordance with AS3000, SAPN, Telstra and Austel regulations
checkpoint | Fire penetrations to be sealed in accordance with manufacturers tested system to the locations as indicated on as built drawings complete with labels - Please attach photos
checkpoint | Acoustic penetrations to be sealed in accordance with approved sample wall & manufacturers tested system to the locations as indicated on as builts
checkpoint | Continuity and polarity checks carried out on all cables
checkpoint | EWIS panel loudspeakers and WPIs installed in accordance with applicable approved drawings and AS1668, AS2036, AS1670, AS1603 and SAMFs requirements
section | Test Procedures
checkpoint | Ensure Client and Builders representative are aware that EWIS system is to be tested. Resulting in audible alarms
checkpoint | Conducted SAMFs signalling device test procedures
checkpoint | Arrange formal SAMFs inspection and system testing
section | Sign-Off
checkpoint | Works completed to specification/drawings - Attach photos of work below
holdpoint | Request Builder Sign Off
checklist-flat | Sleeves ITP
checkpoint | Penetration sleeves installed in accordance with applicable, TFP/Combined approved drawings
checkpoint | Cast in pipework/sleeves as per approved engineer detail
label | Comment Notes relevant to inspection below